## BoQ1
Government eProcurement System Created By: RAGHU RAMA REDDY DODDA Created Date/Time: 19-Jul-2023 12:58 PM Tender Title: 1 Replacement of Feeder Pillars at Operational area at Chennai Airport 2 Replacement of Electrical LT Panels at Admin Building, other ancillary buildings and allied works at Chennai Airport Tender ID: 2023_AAI_156567_1
Tender Inviting Authority: AGM (E-E)-I, AAI Chennai Airport.
Name of Work: 1. REPLACEMENT OF FEEDER PILLARS AT OPERATIONAL AREA AT CHENNAI AIRPORT. 2. REPLACEMENT OF ELECTRICAL LT PANELS AT ADMIN BUILDING, OTHER ANCILLARY BUILDINGS AND ALLIED WORKS AT CHENNAI AIRPORT
E - Bid No: 2023_AAI_156567_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Arkensolutions Pvt Ltd.,(GSTN-29AAICA0624R1Z9) |  | SHANTI ENTERPRISES ELECTRICALS PRIVATE LIMITED(GSTN-33AABCS2732HIZP) |  | SHRI VAARI ELECTRICALS PVT LTD(GSTN-33AAJCS5545E1ZE) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | SARASWAT ENGINEERING SERVICES(GSTN-27AAZFS6239C1ZO) |  | R.K.M. ELECTRICALS(GSTN-33ACAPM4207B2ZE) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | BHARATH TRADERS(GSTN-NA) |  | JyotiElectrosystemspvtltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location: Bay No. 30 ,Bay No. ( 101-104),Bay (43-45) & Bay No. (51-57)
1.01 | Two Nos. of 200 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
1.02 | Five Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
1.03 | Three Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having (0-32) Amp Digital Energy Meter and ON/OFF/TRIP Indication Lamps as required.
1.04 | One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
1.05 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
1.06 | All as above1.01 to 1.05 | 4.00 | Jobs |  | 348050.00 | 1392200.00 | 273363.04 | 1093452.16 | 386651.00 | 1546604.00 | 296999.00 | 1187996.00 | 295741.00 | 1182964.00 | 450000.00 | 1800000.00 | 329565.00 | 1318260.00 | 483575.00 | 1934300.00 | 260000.00 | 1040000.00 | 1040000.00 | JyotiElectrosystemspvtltd
2.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location : For Bays (81-92) and Bays (93-99)
2.01 | Two Nos. of 400 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
2.02 | Seven Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
2.03 | Three Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having (0-32) Amp Digital Energy Meter and ON/OFF/TRIP Indication Lamps as required.
2.04 | One Set of 600 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
2.05 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
2.06 | All as above 2.01 to 2.05 | 2.00 | Jobs |  | 479750.00 | 959500.00 | 342138.16 | 684276.32 | 451269.00 | 902538.00 | 370919.00 | 741838.00 | 421573.00 | 843146.00 | 580000.00 | 1160000.00 | 412622.00 | 825244.00 | 648600.00 | 1297200.00 | 284000.00 | 568000.00 | 568000.00 | JyotiElectrosystemspvtltd
3.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location : Bay 80
3.01 | Two Nos. of 400 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
3.02 | Two Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoings with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps as required.
3.03 | Two Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having (0-32) Amp Digital Energy Meter and ON/OFF/TRIP Indication Lamps as required.
3.04 | Two Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoing with ON/OFF/TRIP Indication Lamps as required.
3.05 | One Set of 600 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
3.06 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
3.07 | All as above 3.01 to 3.06 | 1.00 | Job |  | 430250.00 | 430250.00 | 340944.07 | 340944.07 | 445300.00 | 445300.00 | 370499.00 | 370499.00 | 373326.00 | 373326.00 | 550000.00 | 550000.00 | 411181.00 | 411181.00 | 571550.00 | 571550.00 | 320000.00 | 320000.00 | 320000.00 | JyotiElectrosystemspvtltd
4.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location : Bays (46-50)
4.01 | Two Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
4.02 | Four Nos. of 200 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoing with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
4.03 | Four Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
4.04 | Two Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having (0-32) Amp Digital Energy Meter and ON/OFF/TRIP Indication Lamps as required.
4.05 | One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
4.06 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
4.07 | All as above 4.01 to 4.06 | 1.00 | Job |  | 622450.00 | 622450.00 | 457884.49 | 457884.49 | 568709.00 | 568709.00 | 494999.00 | 494999.00 | 536020.00 | 536020.00 | 700000.00 | 700000.00 | 552406.00 | 552406.00 | 784530.00 | 784530.00 | 396000.00 | 396000.00 | 396000.00 | JyotiElectrosystemspvtltd
5.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location : Bays(61-68) -2 Panels
5.01 | Two Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
5.02 | Five Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
5.03 | Two Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having (0-32) Amp Digital Energy Meter and ON/OFF/TRIP Indication Lamps as required.
5.04 | One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
5.05 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
5.06 | All as above 5.01 to 5.05 | 2.00 | Jobs |  | 387650.00 | 775300.00 | 254645.88 | 509291.76 | 357081.00 | 714162.00 | 276999.00 | 553998.00 | 283080.00 | 566160.00 | 415000.00 | 830000.00 | 302061.00 | 604122.00 | 436885.00 | 873770.00 | 236000.00 | 472000.00 | 472000.00 | JyotiElectrosystemspvtltd
6.00 | Fabrication, SITC of TTA MV Switch Board Essential Panel/Non-Essential made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, floor/wall mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, etc., as required and comprising of the following: (Inside Mandapam Under Staircase)
6.01 | One No. of 200 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with Resin Cast CT operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
6.02 | Three Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
6.03 | Six Nos. of 63 A, 10 KA, 4P MCB as Outgoing as required.
6.04 | One Set of 400 Amps Al. Bus Bars with at Par Neutral BUS BARS as required.
6.05 | All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
6.06 | All as above 6.01 to 6.05 | 1.00 | Job |  | 190400.00 | 190400.00 | 165947.39 | 165947.39 | 153930.00 | 153930.00 | 187999.00 | 187999.00 | 184662.00 | 184662.00 | 330000.00 | 330000.00 | 211933.00 | 211933.00 | 344655.00 | 344655.00 | 140000.00 | 140000.00 | 140000.00 | JyotiElectrosystemspvtltd
7.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: (Outside Near Main LT Panel-Gate Side)
7.01 | Two Nos. of 400 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
7.02 | Three Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoing with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
7.03 | One No. of 100 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
7.04 | One Set of 600 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
7.05 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
7.06 | All as above 7.01 to 7.05 | 1.00 | Job |  | 442350.00 | 442350.00 | 350018.07 | 350018.07 | 426192.00 | 426192.00 | 379999.00 | 379999.00 | 380059.00 | 380059.00 | 440000.00 | 440000.00 | 422139.00 | 422139.00 | 545675.00 | 545675.00 | 320000.00 | 320000.00 | 320000.00 | JyotiElectrosystemspvtltd
8.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 300 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: (Way to Kitchen-Outside Panel Clubbed with Other Panel nearby)
8.01 | Two Nos. of 200 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
8.02 | One No. of 200 A, 50 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
8.03 | Three Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
8.04 | Four Nos. of 63 A, 10 KA, 4P MCB as Outgoings as required.
8.05 | One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
8.06 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
8.07 | All as above 8.01 to 8.06 | 1.00 | Job |  | 305150.00 | 305150.00 | 234761.99 | 234761.99 | 314744.00 | 314744.00 | 254999.00 | 254999.00 | 261762.00 | 261762.00 | 330000.00 | 330000.00 | 282947.00 | 282947.00 | 414230.00 | 414230.00 | 224000.00 | 224000.00 | 224000.00 | JyotiElectrosystemspvtltd
9.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 300 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: (Near Transit Accomodation & Cargo Pump House)
9.01 | One No. of 250 A, 36 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps as required.
9.02 | Six Nos. of 100 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
9.03 | One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
9.04 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
9.05 | All as above 9.01 to 9.04 | 2.00 | Jobs |  | 250350.00 | 500700.00 | 174532.74 | 349065.48 | 257914.00 | 515828.00 | 189999.00 | 379998.00 | 215760.00 | 431520.00 | 300000.00 | 600000.00 | 210209.00 | 420418.00 | 306130.00 | 612260.00 | 143200.00 | 286400.00 | 286400.00 | JyotiElectrosystemspvtltd
10.00 | Fabrication, SITC of TTA MV Switch Board Essential Panel/Non-Essential made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, floor mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, etc., as required and comprising of the following: (GF LHS AND RHS - NESS and ESS PANELS)
10.01 | Two Nos. of 400 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with Resin Cast CT operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, Mechanical Interlocking Facility with Incomers as required.
10.02 | Four Nos. of 125 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, with ON/OFF/TRIP Indication Lamps as required.
10.03 | Six Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, with ON/OFF/TRIP Indication Lamps as required.
10.04 | Two Nos. of 63 A, 10 KA, 4P MCB as Outgoing as required.
10.05 | One Set of 600 Amps Al. Bus Bars with at Par Neutral BUS BARS as required.
10.06 | All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
10.07 | All as above 10.01 to 10.06 | 4.00 | Jobs |  | 522100.00 | 2088400.00 | 408267.83 | 1633071.32 | 321218.00 | 1284872.00 | 449999.00 | 1799996.00 | 436160.00 | 1744640.00 | 450000.00 | 1800000.00 | 505319.00 | 2021276.00 | 647335.00 | 2589340.00 | 292800.00 | 1171200.00 | 1171200.00 | JyotiElectrosystemspvtltd
11.00 | Fabrication, SITC of TTA MV Switch Board Essential Panel/Non-Essential made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, floor/wall mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, etc., as required and comprising of the following: (FF/SF/TF-LHS AND RHS-NESS and ESS)
11.01 | One No. of 125 A, 36 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with Resin Cast CT operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
11.02 | Two Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, with ON/OFF/TRIP Indication Lamps as required.
11.03 | Four Nos. of 63 A, 10 KA, 4P MCB as Outgoing as required.
11.04 | One Set of 200 Amps Al. Bus Bars with at Par Neutral BUS BARS as required.
11.05 | All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
11.06 | All as above 11.01 to 11.05 | 12.00 | Jobs |  | 178300.00 | 2139600.00 | 148330.43 | 1779965.16 | 121564.00 | 1458768.00 | 171999.00 | 2063988.00 | 142344.00 | 1708128.00 | 210000.00 | 2520000.00 | 188390.00 | 2260680.00 | 320045.00 | 3840540.00 | 108320.00 | 1299840.00 | 1299840.00 | JyotiElectrosystemspvtltd
12.00 | Fabrication, SITC of TTA MV Switch Board Essential Panel/Non-Essential made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, floor/wall mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, etc., as required and comprising of the following: (INSIDE FS-CORRIDOR PANEL)
12.01 | One No. of 125 A, 36 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with Resin Cast CT operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
12.02 | Twelve Nos. of 63 A, 10 KA, 4P MCB as Outgoing as required.
12.03 | One Set of 200 Amps Al. Bus Bars with at Par Neutral BUS BARS as required.
12.04 | All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
12.05 | All as above 12.01 to 12.04 | 1.00 | Job |  | 176100.00 | 176100.00 | 144089.59 | 144089.59 | 92336.00 | 92336.00 | 171799.00 | 171799.00 | 142025.00 | 142025.00 | 312500.00 | 312500.00 | 183942.00 | 183942.00 | 329360.00 | 329360.00 | 101360.00 | 101360.00 | 92336.00 | SHRI VAARI ELECTRICALS PVT LTD
13.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: (Outside-FS-Near Compound Wall)
13.01 | Two Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps and Mechanical Castle Interlock (2 Lock + 1 Key) as required.
13.02 | One No. of 125 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoing with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
13.03 | Two Nos. of 63 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps as required.
13.04 | Four Nos. of 63 A, 10 KA, 4P MCB as Outgoing as required.
13.05 | One Set of 300 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
13.06 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
13.07 | All as above 13.01 to 13.06 | 1.00 | Job |  | 306250.00 | 306250.00 | 247467.59 | 247467.59 | 317724.00 | 317724.00 | 267999.00 | 267999.00 | 260640.00 | 260640.00 | 287500.00 | 287500.00 | 308072.00 | 308072.00 | 404685.00 | 404685.00 | 212800.00 | 212800.00 | 212800.00 | JyotiElectrosystemspvtltd
14.00 | Supply, Installation, Testing and Commissioning of MV Switch Board Outdoor Type Main/Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 250 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel of 100 mm ISMC and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal up to 900 mm (450 mm BGL and 450 mm AGL), fixing of panel etc., complete as required and comprising of the following: Location: Near to Admin Compound wall
14.01 | One No. of 100 A, 36 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required.
14.02 | 03 Nos. of 20 A, 10 KA, DP MCB along with contactors,timers as Outgoings as required.
14.03 | 02 Nos. of 40 A, 10 KVA 4P MCB as Outgoing as requireed.
14.04 | One Set of 160 Amps Al. Bus Bars with at Par Neutral Bus Bars as required.
14.05 | All accessories such as fuses, auxillary contactors, auxillary switches, MCBs etc., as required.
14.06 | All as above 14.01 to 14.05 | 1.00 | Job |  | 162300.00 | 162300.00 | 75335.77 | 75335.77 | 63226.00 | 63226.00 | 94999.00 | 94999.00 | 143148.00 | 143148.00 | 115000.00 | 115000.00 | 99117.00 | 99117.00 | 94185.00 | 94185.00 | 78400.00 | 78400.00 | 63226.00 | SHRI VAARI ELECTRICALS PVT LTD
15.00 | Dismantling of Existing Panel from Site and transporting the same to Store of Engineer-In-Charge including disconnection and dismantling of Cables from Panel, Dismantling of Foundation including disposal of the debris, Levelling etc., as required. | 16.00 | Jobs |  | 8500.00 | 136000.00 | 8351.00 | 133616.00 | 20000.00 | 320000.00 | 14999.00 | 239984.00 | 15847.00 | 253552.00 | 4000.00 | 64000.00 | 4900.00 | 78400.00 | 8000.00 | 128000.00 | 12000.00 | 192000.00 | 64000.00 | R.K.M. ELECTRICALS
16.00 | Dismantling of Existing Panel from Site and transporting the same to Store of Engineer-In-Charge including disconnection and dismantling of Cables from Panel, etc., as required. | 19.00 | Jobs |  | 4500.00 | 85500.00 | 5567.00 | 105773.00 | 6000.00 | 114000.00 | 9999.00 | 189981.00 | 10971.00 | 208449.00 | 3500.00 | 66500.00 | 4900.00 | 93100.00 | 8000.00 | 152000.00 | 12000.00 | 228000.00 | 66500.00 | R.K.M. ELECTRICALS
17.00 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required.
17.01 | 4C X 16 Sq.mm | 200.00 | Mtrs |  | 116.00 | 23200.00 | 128.98 | 25796.00 | 160.00 | 32000.00 | 128.00 | 25600.00 | 122.00 | 24400.00 | 160.00 | 32000.00 | 132.00 | 26400.00 | 140.00 | 28000.00 | 148.80 | 29760.00 | 23200.00 | Arkensolutions Pvt Ltd.,
17.02 | 4C X 25 Sq.mm | 2000.00 | Mtrs |  | 159.00 | 318000.00 | 152.74 | 305480.00 | 181.00 | 362000.00 | 156.00 | 312000.00 | 145.00 | 290000.00 | 180.00 | 360000.00 | 162.00 | 324000.00 | 170.00 | 340000.00 | 182.40 | 364800.00 | 290000.00 | SARASWAT ENGINEERING SERVICES
17.03 | 3.5 C X 120 Sq.mm | 2800.00 | Mtrs |  | 516.00 | 1444800.00 | 495.57 | 1387596.00 | 583.00 | 1632400.00 | 506.00 | 1416800.00 | 469.00 | 1313200.00 | 650.00 | 1820000.00 | 586.00 | 1640800.00 | 525.00 | 1470000.00 | 589.20 | 1649760.00 | 1313200.00 | SARASWAT ENGINEERING SERVICES
18.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
18.01 | Upto 35 sq. mm | 1700.00 | Mtrs |  | 30.00 | 51000.00 | 56.00 | 95200.00 | 70.00 | 119000.00 | 19.00 | 32300.00 | 35.00 | 59500.00 | 30.00 | 51000.00 | 44.00 | 74800.00 | 35.00 | 59500.00 | 20.00 | 34000.00 | 32300.00 | CHENNAI ENGINEERING SERVICES
18.02 | Above 35 sq. mm and upto 95 sq. mm | 200.00 | Mtrs |  | 50.00 | 10000.00 | 89.00 | 17800.00 | 80.00 | 16000.00 | 29.00 | 5800.00 | 64.00 | 12800.00 | 60.00 | 12000.00 | 64.00 | 12800.00 | 40.00 | 8000.00 | 40.00 | 8000.00 | 5800.00 | CHENNAI ENGINEERING SERVICES
18.03 | Above 95 sq. mm and upto 185 sq. mm | 2450.00 | Mtrs |  | 70.00 | 171500.00 | 111.00 | 271950.00 | 130.00 | 318500.00 | 59.00 | 144550.00 | 87.00 | 213150.00 | 100.00 | 245000.00 | 74.00 | 181300.00 | 60.00 | 147000.00 | 80.00 | 196000.00 | 144550.00 | CHENNAI ENGINEERING SERVICES
18.04 | Above 185 sq. mm and upto 400 sq. mm | 3150.00 | Mtrs |  | 100.00 | 315000.00 | 134.00 | 422100.00 | 260.00 | 819000.00 | 119.00 | 374850.00 | 117.00 | 368550.00 | 180.00 | 567000.00 | 108.00 | 340200.00 | 100.00 | 315000.00 | 120.00 | 378000.00 | 315000.00 | Arkensolutions Pvt Ltd.,, BHARATH TRADERS
19.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
19.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 200.00 | Mtrs |  | 50.00 | 10000.00 | 78.00 | 15600.00 | 70.00 | 14000.00 | 39.00 | 7800.00 | 47.00 | 9400.00 | 50.00 | 10000.00 | 54.00 | 10800.00 | 50.00 | 10000.00 | 28.00 | 5600.00 | 5600.00 | JyotiElectrosystemspvtltd
19.02 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25x3mm MS flat clamp) | 200.00 | Mtrs |  | 100.00 | 20000.00 | 167.00 | 33400.00 | 130.00 | 26000.00 | 69.00 | 13800.00 | 105.00 | 21000.00 | 180.00 | 36000.00 | 84.00 | 16800.00 | 100.00 | 20000.00 | 48.00 | 9600.00 | 9600.00 | JyotiElectrosystemspvtltd
20.00 | Laying of 110 mm dia OD HDPE Pipe along with all accessoreis like sockets, bends, coupler etc, complete with fitting cutting,jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. (HDPE pipe will be supplied by AAI) | 2500.00 | Mtrs |  | 224.00 | 560000.00 | 278.00 | 695000.00 | 280.00 | 700000.00 | 229.00 | 572500.00 | 146.00 | 365000.00 | 200.00 | 500000.00 | 225.00 | 562500.00 | 150.00 | 375000.00 | 400.00 | 1000000.00 | 365000.00 | SARASWAT ENGINEERING SERVICES
21.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed /XLPE aluminium conductor cable of 1.1 KV grade as required.
21.01 | 4X16 Sq.mm | 20.00 | Set |  | 1080.00 | 21600.00 | 2920.82 | 58416.40 | 2200.00 | 44000.00 | 3499.00 | 69980.00 | 3580.00 | 71600.00 | 600.00 | 12000.00 | 1274.00 | 25480.00 | 1500.00 | 30000.00 | 4800.00 | 96000.00 | 12000.00 | R.K.M. ELECTRICALS
21.02 | 4x25 Sq.mm | 5.00 | Set |  | 1390.00 | 6950.00 | 3247.82 | 16239.10 | 3000.00 | 15000.00 | 3499.00 | 17495.00 | 3820.00 | 19100.00 | 800.00 | 4000.00 | 2744.00 | 13720.00 | 1800.00 | 9000.00 | 4800.00 | 24000.00 | 4000.00 | R.K.M. ELECTRICALS
21.03 | 3½ X 95 Sq. mm | 5.00 | Set |  | 2730.00 | 13650.00 | 4357.73 | 21788.65 | 4750.00 | 23750.00 | 4499.00 | 22495.00 | 4886.00 | 24430.00 | 1500.00 | 7500.00 | 2744.00 | 13720.00 | 2400.00 | 12000.00 | 4800.00 | 24000.00 | 7500.00 | R.K.M. ELECTRICALS
21.04 | 3½ X 120 Sq. mm | 10.00 | Set |  | 2940.00 | 29400.00 | 5906.63 | 59066.30 | 4750.00 | 47500.00 | 5999.00 | 59990.00 | 5495.00 | 54950.00 | 2300.00 | 23000.00 | 2940.00 | 29400.00 | 4370.00 | 43700.00 | 4800.00 | 48000.00 | 23000.00 | R.K.M. ELECTRICALS
21.05 | 3½ X 300 Sq. mm | 10.00 | Set |  | 3320.00 | 33200.00 | 7144.54 | 71445.40 | 8000.00 | 80000.00 | 6499.00 | 64990.00 | 6781.00 | 67810.00 | 3500.00 | 35000.00 | 4704.00 | 47040.00 | 4500.00 | 45000.00 | 4800.00 | 48000.00 | 33200.00 | Arkensolutions Pvt Ltd.,
21.06 | 3½ X 400 Sq. mm | 5.00 | Set |  | 4370.00 | 21850.00 | 9231.36 | 46156.80 | 9000.00 | 45000.00 | 6499.00 | 32495.00 | 7886.00 | 39430.00 | 5000.00 | 25000.00 | 6468.00 | 32340.00 | 6000.00 | 30000.00 | 5600.00 | 28000.00 | 21850.00 | Arkensolutions Pvt Ltd.,
22.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
22.01 | 3½ X 400 sq. mm (82mm) | 10.00 | Set |  | 2660.00 | 26600.00 | 2018.04 | 20180.40 | 2800.00 | 28000.00 | 1499.00 | 14990.00 | 5537.00 | 55370.00 | 1200.00 | 12000.00 | 1764.00 | 17640.00 | 2100.00 | 21000.00 | 1600.00 | 16000.00 | 12000.00 | R.K.M. ELECTRICALS
22.02 | 3½ X 300 sq. mm (70 mm) | 15.00 | Set |  | 2180.00 | 32700.00 | 1504.42 | 22566.30 | 2400.00 | 36000.00 | 1199.00 | 17985.00 | 4318.00 | 64770.00 | 1000.00 | 15000.00 | 1568.00 | 23520.00 | 1900.00 | 28500.00 | 1200.00 | 18000.00 | 15000.00 | R.K.M. ELECTRICALS
22.03 | 3½ X 150 sq. mm (50mm) | 1.00 | Set |  | 1330.00 | 1330.00 | 841.79 | 841.79 | 2200.00 | 2200.00 | 999.00 | 999.00 | 2187.00 | 2187.00 | 800.00 | 800.00 | 1274.00 | 1274.00 | 800.00 | 800.00 | 800.00 | 800.00 | 800.00 | JyotiElectrosystemspvtltd, R.K.M. ELECTRICALS, BHARATH TRADERS
22.04 | 3½ X 120 sq. mm (45mm) | 25.00 | Set |  | 1130.00 | 28250.00 | 760.40 | 19010.00 | 2000.00 | 50000.00 | 799.00 | 19975.00 | 1683.00 | 42075.00 | 700.00 | 17500.00 | 1176.00 | 29400.00 | 750.00 | 18750.00 | 800.00 | 20000.00 | 17500.00 | R.K.M. ELECTRICALS
22.05 | 3½ X 95 sq. mm (45mm) | 30.00 | Set |  | 890.00 | 26700.00 | 619.14 | 18574.20 | 1600.00 | 48000.00 | 749.00 | 22470.00 | 1534.00 | 46020.00 | 700.00 | 21000.00 | 980.00 | 29400.00 | 650.00 | 19500.00 | 640.00 | 19200.00 | 18574.20 | SHANTI ENTERPRISES ELECTRICALS PRIVATE LIMITED
22.06 | 3½ X 70 sq. mm (38mm) | 10.00 | Set |  | 720.00 | 7200.00 | 527.67 | 5276.70 | 1400.00 | 14000.00 | 699.00 | 6990.00 | 1271.00 | 12710.00 | 500.00 | 5000.00 | 735.00 | 7350.00 | 550.00 | 5500.00 | 640.00 | 6400.00 | 5000.00 | R.K.M. ELECTRICALS
22.07 | 3½ X 50 sq. mm (35mm) | 25.00 | Set |  | 610.00 | 15250.00 | 504.59 | 12614.75 | 1000.00 | 25000.00 | 699.00 | 17475.00 | 1062.00 | 26550.00 | 500.00 | 12500.00 | 637.00 | 15925.00 | 500.00 | 12500.00 | 480.00 | 12000.00 | 12000.00 | JyotiElectrosystemspvtltd
22.08 | 3½ X 35 sq. mm (32mm) | 40.00 | Set |  | 500.00 | 20000.00 | 363.19 | 14527.60 | 800.00 | 32000.00 | 649.00 | 25960.00 | 833.00 | 33320.00 | 300.00 | 12000.00 | 343.00 | 13720.00 | 400.00 | 16000.00 | 480.00 | 19200.00 | 12000.00 | R.K.M. ELECTRICALS
22.09 | 3½ X 25 sq. mm (28mm) | 130.00 | Set |  | 400.00 | 52000.00 | 356.27 | 46315.10 | 600.00 | 78000.00 | 649.00 | 84370.00 | 667.00 | 86710.00 | 300.00 | 39000.00 | 245.00 | 31850.00 | 350.00 | 45500.00 | 400.00 | 52000.00 | 31850.00 | vk sam engineering
22.10 | 4 X 16 sq. mm (28mm) | 115.00 | Set |  | 340.00 | 39100.00 | 303.34 | 34884.10 | 500.00 | 57500.00 | 499.00 | 57385.00 | 664.00 | 76360.00 | 200.00 | 23000.00 | 196.00 | 22540.00 | 300.00 | 34500.00 | 400.00 | 46000.00 | 22540.00 | vk sam engineering
22.11 | 4 X 10 sq. mm (25mm) | 15.00 | Set |  | 260.00 | 3900.00 | 300.57 | 4508.55 | 450.00 | 6750.00 | 449.00 | 6735.00 | 552.00 | 8280.00 | 190.00 | 2850.00 | 147.00 | 2205.00 | 275.00 | 4125.00 | 400.00 | 6000.00 | 2205.00 | vk sam engineering
23.00 | Supply and Laying of 100 mm dia size C class GI pipe for taxiway/runway/Road crossing at a depth of 150 mm i/c cutting the Apron/ PQC /bituminous surface, re-filling with cement concrete mixture of ratio 1:2:4 and making good the surface matching with original finish etc., as required and as per the instruction of Engineer-in-charge. | 1800.00 | Mtrs |  | 1850.00 | 3330000.00 | 1507.07 | 2712726.00 | 1750.00 | 3150000.00 | 1499.00 | 2698200.00 | 2321.00 | 4177800.00 | 1300.00 | 2340000.00 | 2045.00 | 3681000.00 | 1625.00 | 2925000.00 | 800.00 | 1440000.00 | 1440000.00 | JyotiElectrosystemspvtltd
24.00 | Supply and Laying of 100 mm dia size C class GI pipe on surface and providing 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) concrete of thickness 150mm above and all around the pipe required as per the instruction of Engineer-in-charge. | 300.00 | Mtrs |  | 2170.00 | 651000.00 | 1396.07 | 418821.00 | 1750.00 | 525000.00 | 1199.00 | 359700.00 | 1955.00 | 586500.00 | 1300.00 | 390000.00 | 2450.00 | 735000.00 | 1520.00 | 456000.00 | 5200.00 | 1560000.00 | 359700.00 | CHENNAI ENGINEERING SERVICES
25.00 | Supply and Laying of 50 mm dia size C class GI pipe for apron/taxiway/runway/Road crossing at a depth of 150 mm i/c cutting the Apron/ PQC /bituminous surface, re-filling with cement concrete mixture of ratio 1:2:4 and making good the surface matching with original finish etc., as required and as per the instruction of Engineer-in-charge. | 500.00 | Mtrs |  | 1400.00 | 700000.00 | 771.18 | 385590.00 | 875.00 | 437500.00 | 999.00 | 499500.00 | 1295.00 | 647500.00 | 675.00 | 337500.00 | 1367.00 | 683500.00 | 850.00 | 425000.00 | 4000.00 | 2000000.00 | 337500.00 | R.K.M. ELECTRICALS
26.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 32.00 | Each |  | 14900.00 | 476800.00 | 13028.32 | 416906.24 | 8250.00 | 264000.00 | 4999.00 | 159968.00 | 12036.00 | 385152.00 | 9000.00 | 288000.00 | 4900.00 | 156800.00 | 30000.00 | 960000.00 | 4000.00 | 128000.00 | 128000.00 | JyotiElectrosystemspvtltd
27.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 8.00 | Each |  | 14400.00 | 115200.00 | 17006.43 | 136051.44 | 11500.00 | 92000.00 | 11999.00 | 95992.00 | 11095.00 | 88760.00 | 7500.00 | 60000.00 | 7350.00 | 58800.00 | 20000.00 | 160000.00 | 6400.00 | 51200.00 | 51200.00 | JyotiElectrosystemspvtltd
28.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 100.00 | Mtrs |  | 330.00 | 33000.00 | 301.34 | 30134.00 | 270.00 | 27000.00 | 99.00 | 9900.00 | 289.00 | 28900.00 | 250.00 | 25000.00 | 318.00 | 31800.00 | 180.00 | 18000.00 | 200.00 | 20000.00 | 9900.00 | CHENNAI ENGINEERING SERVICES
29.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 220.00 | Mtrs |  | 880.00 | 193600.00 | 795.96 | 175111.20 | 350.00 | 77000.00 | 399.00 | 87780.00 | 908.00 | 199760.00 | 200.00 | 44000.00 | 637.00 | 140140.00 | 200.00 | 44000.00 | 200.00 | 44000.00 | 44000.00 | JyotiElectrosystemspvtltd, R.K.M. ELECTRICALS, BHARATH TRADERS
30.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 300.00 | Mtrs |  | 172.00 | 51600.00 | 223.34 | 67002.00 | 210.00 | 63000.00 | 109.00 | 32700.00 | 210.00 | 63000.00 | 200.00 | 60000.00 | 253.00 | 75900.00 | 145.00 | 43500.00 | 158.40 | 47520.00 | 32700.00 | CHENNAI ENGINEERING SERVICES
31.00 | Supply& fixing of nominal 2.0 mm thick (Width 1 Mtr) PVC synthetic, electric insulated mats conforming to IS 15652-2006 having Dielectric strength of 30 KV, no adverse effect of mineral oil, high insulation resistance (Minimum 1,00,000 M Ω on wet condition with 5 KV meggar) etc., as required. | 180.00 | Sq.Mtrs |  | 980.00 | 176400.00 | 918.84 | 165391.20 | 2500.00 | 450000.00 | 999.00 | 179820.00 | 753.00 | 135540.00 | 1500.00 | 270000.00 | 931.00 | 167580.00 | 600.00 | 108000.00 | 5600.00 | 1008000.00 | 108000.00 | BHARATH TRADERS
32.00 | Providing Civil Works as required as detailed below:
32.01 | Cement concrete in 1:2:4 (1 cement: 3 coarse sand: 6 graded stone aggregate 20mm nominal size) | 10.00 | Cum |  | 9350.00 | 93500.00 | 10578.00 | 105780.00 | 10500.00 | 105000.00 | 3499.00 | 34990.00 | 9143.00 | 91430.00 | 7000.00 | 70000.00 | 8330.00 | 83300.00 | 7000.00 | 70000.00 | 4400.00 | 44000.00 | 34990.00 | CHENNAI ENGINEERING SERVICES
32.02 | Brick work with bricks of class designation 60 in foundation and plinth in 1:6 (1 cement: 6 coarse sand) | 10.00 | Cum |  | 9020.00 | 90200.00 | 8351.00 | 83510.00 | 13000.00 | 130000.00 | 3999.00 | 39990.00 | 9996.00 | 99960.00 | 5500.00 | 55000.00 | 9310.00 | 93100.00 | 7500.00 | 75000.00 | 6400.00 | 64000.00 | 39990.00 | CHENNAI ENGINEERING SERVICES
32.03 | Cement plaster 12mm thick of mixture 1:6 | 10.00 | Sq.Mtrs |  | 590.00 | 5900.00 | 1113.00 | 11130.00 | 950.00 | 9500.00 | 499.00 | 4990.00 | 914.00 | 9140.00 | 250.00 | 2500.00 | 588.00 | 5880.00 | 350.00 | 3500.00 | 144.00 | 1440.00 | 1440.00 | JyotiElectrosystemspvtltd
33.00 | Fabrication & Supply of MS Rectangular Transformer Housing Box of size 750x330x300 mm, made out of 8mm thick MS sheet on four sides and bottom, 10mm thick MS sheet for top cover with 8 Nos. M-10 size threaded hole, 1 No. 25mm dia drain hole at the bottom and suitable holes to enable entry of 40/50/63/90mm dia GI/HDPE pipe and secondary leads, (2 Nos. partition plates of 200mm high inside the box made of 8mm thick MS Sheet) with rubber gaskets for top cover, two nos. cadmium plated earthing bolts with nuts etc. including painting with one coat of red oxide paint and two coats of black enamel paint finish etc. as required. | 10.00 | Nos |  | 87450.00 | 874500.00 | 16971.44 | 169714.40 | 32500.00 | 325000.00 | 9999.00 | 99990.00 | 11893.00 | 118930.00 | 40000.00 | 400000.00 | 14700.00 | 147000.00 | 19000.00 | 190000.00 | 24000.00 | 240000.00 | 99990.00 | CHENNAI ENGINEERING SERVICES
34.00 | Installation of MS Transformer housing box of size not less than 750mm X 330 mm X 300 mm in runway/taxiway shoulder by cutting of bitumen/concrete area including providing 75mm thick cement concrete 1:2:4 all around and bottom of the transformer housing box with required slope to level of runway/taxiway all around the housing box with the bitumen surface and plastering of exposed surface with cement mortar 1:4 of thickness 12 mm over the concrete surface including painting top of MS box and lettering & numbering in a base of suitable colour with one coat of zinc chromate primer and two coats of poly urethane paint etc. after installation complete as required. | 10.00 | Nos |  | 5200.00 | 52000.00 | 5567.00 | 55670.00 | 12500.00 | 125000.00 | 2999.00 | 29990.00 | 2194.00 | 21940.00 | 15000.00 | 150000.00 | 6860.00 | 68600.00 | 5000.00 | 50000.00 | 32000.00 | 320000.00 | 21940.00 | SARASWAT ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 20859330.00 |  | 16980831.78 |  | 19690533.00 |  | 17163360.00 |  | 19283185.00 |  | 20297650.00 |  | 19768561.00 |  | 23593155.00 |  | 18177280.00
Lowest Amount Quoted BY: SHANTI ENTERPRISES ELECTRICALS PRIVATE LIMITED(16980831.78)

## BOQ Summary
BOQ Summary Details Tender Title: 1 Replacement of Feeder Pillars at Operational area at Chennai Airport 2 Replacement of Electrical LT Panels at Admin Building, other ancillary buildings and allied works at Chennai Airport Tender ID: 2023_AAI_156567_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHANTI ENTERPRISES ELECTRICALS PRIVATE LIMITED | 16980831.78 | L1
| 2 | CHENNAI ENGINEERING SERVICES | 17163360.00 | L2
| 3 | JyotiElectrosystemspvtltd | 18177280.00 | L3
| 4 | SARASWAT ENGINEERING SERVICES | 19283185.00 | L4
| 5 | SHRI VAARI ELECTRICALS PVT LTD | 19690533.00 | L5
| 6 | vk sam engineering | 19768561.00 | L6
| 7 | R.K.M. ELECTRICALS | 20297650.00 | L7
| 8 | Arkensolutions Pvt Ltd., | 20859330.00 | L8
| 9 | BHARATH TRADERS | 23593155.00 | L9