## BoQ1
Government eProcurement System Created By: VIVEK KUMAR SINGH Created Date/Time: 12-Jul-2023 04:48 PM Tender Title: Provision of New Automatic Weather Observation System (AWOS) at JPNI Airport Patna SH Electrical Works Tender ID: 2023_AAI_157500_1
Tender Inviting Authority: Airport Authority of India, JPNI Airport Patna
Name of Work: Provision of New Automatic Weather Observation System (AWOS) at JPNI Airport, Patna. SH:Electrical Works.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Ruhi Electronics(GSTN-10ABYPJ8411H1ZM) |  | ANIL KUMAR(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply,Installation,Testing and Commissioning of indoor type LT cubical Panel, double door,weather and vermin proof, powder coated paiting,duly fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, degree of protection of Enclossure shall be minimum IP~43.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system.Entire panel shall have a common GI earth bar of size 40mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable.Suitable MS angle base support to the panel. The cubical panel shall consist of following switch gears, Bus Bar and other acessories complete as required (a)INCOMMER: (i)100 A FP, 35 KA,adjustable Microprocessor release based MCCB (Ics=Icu= 100%) with O/C , S/C & E/F protection with Extended Rotary Handle- 2 Nos. (ii) LED Digital Multifunction Meter-2 Nos. (iii)RYB LED indications for each (b) AUTOMATIC CHANGEOVER: (i) 100 Amp 4 Pole, On load automaic change over switch with settable overvoltage & undervoltage protection,protection against single phasing with LED Indicating lamps- 1 no. (ii) Suitable range 3 Phase Energy Meter connected to outgoing side of automatic changeover -01 No. (c)BUSBARS: 1 Set of 100 Amp TPN busbars of high conductivity copper with 100% neutral size with Heat shrinkable colour coded insulation sleeves i.c SMC bus bar supports etc -1set. . (d)OUTGOING: (i)63 A FP, 35 KA,adjustable Microprocessor release based MCCB (Ics=Icu= 100%) with O/C & S & E/F protection with Extended Rotary Handle- 6 Nos INSTRUMENTS AND OTHER ACCESSORTIES (i)06 Nos. 0 to 500 V digital voltmeter for 3 phase, 4 wire operation with seletor switches alongwith MCBs. for each Outgoing (ii)06 Nos. digital ammeter of suitable range (measure 0 to 200 AMP) for 3 phaes, 4 wire operation with selector switch and suitable range CT's. for each outgoings (iii)06 Sets of phase (RYB) indicating lamps, LED type | 1.00 | Each |  | 461494.00 | 461494.00 | 501110.00 | 501110.00 | 461494.00 | Ruhi Electronics
2.00 | Supply,Installation,Testing and Commissioning of outdoor type LT cubical Panel, totaly enclosed,canopy type, double door,free standing, floor mounting, dust and vermin proof, powder coated paiting,duly fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, degree of Protection of enclossure shall be minimum IP~54.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system.Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control wiring should be done by FRLS PVC insulated solid copper conductor cable..Suitable MS angle base support & grouting leg to the panel. The feeder pillar shall consist of following swich gears, Bus Bar and other accessories and suitable MS mounting frame etc complete as required: (a)INCOMMER: (i) 63 A FP, 35 KA,adjustable Microprocessor release based MCCB (Ics=Icu= 100%) with O/C, S/C & E/F protection with Extended Rotary Handle- 2 Nos. (iii) LED Digital Multifunction Meter-2 Nos. (iv)RYB lED indications for each incomer. (b)AUTOMATIC CHANGEOVER: (i) 63 Amp 4 Pole, On load automaic change over switch with settable overvoltage & undervoltage protection,protection against single phasing with LED Indicating lamps- 1 no. (c)BUSBARS: 1 Set of 63 Amp TPN busbars of high conductivity copper with 100% neutral size with Heat shrinkable colour coded insulation sleeves i.c SMC bus bar supports etc -1 set. (d)OUTGOING: (i)63 A, FP, 35 KA,adjustable Microprocessor release based MCCB (Ics=Icu= 100%) with O/C & S & E/F protection with Extended Rotary Handle- 2 Nos. (ii)UPS Outgoing:(a)Suitable seperate compartmental space for provision of 2 KVA online Single phase UPS and battery with free airflow arrangement & insect trap mesh( UPS Space(WxDXH) 250mm x 500mm x 400mm and SMF Batteries space in separate compartment (WxDXH) 250mm x 500mm x 250mm ) (b)20 A, 2P,10 KA, MCB - 2 Nos. for incomming Power to UPS (c)(b)20 A, 2P,10 KA, MCB - 2 Nos. for outgoing Power to UPS INSTRUMENTS AND OTHER ACCESSORTIES (i)02 Nos. 0 to 500 V digital voltmeter for 3 phase, 4 wire operation with seletor switches alongwith MCBs. for each Outgoing | 2.00 | Each |  | 394639.00 | 789278.00 | 470555.00 | 941110.00 | 789278.00 | Ruhi Electronics
3.00 | Supply,Installation,Testing and Commissioning of suitable size pole mounted weather proof heavy duty hard PVC cable box in polycarbonate suitable for LV switchgeras with IP 67,mechanical impacts IK10,high temperature resistive,UV rediation proof,halogen free,electrical insulated,polyamide screw for fixing opening cover or inbuilt hinges that keep lid and base together after opening i/c Supply & fixing of weather proof 3" dia.,1.2M length hard PVC Pole with suitable mouting GI/SS Clamp/Channel and other required accessories for mounting the cable box.The Cable box shall consist of following swich gears and accessories shall be fixed on suitable size din rail including internal wiring with suitable size FRLS PVC cu conductor cable etc complete as required excluding CC works. Incoming:i)20 A, 2P,10 KA, MCB - 2 Nos. Outgoing:ii) 6 - 32 Amp,10KA,SP MCB- 05 Nos. iii)Power Distribution PVC Board with modular cover plate having 6 Amps modular Switch & Socket - 5 Nos. iv) Air tight hard PVC cable glands for incoming and outgoing flexible power cables | 2.00 | Each |  | 13134.00 | 26268.00 | 26000.00 | 52000.00 | 26268.00 | Ruhi Electronics
4.00 | SITC of 2 KVA Online UPS with 20 minute battery back up suitable to work on single phase, 230 V, 50 Hz, having single phase output with pure sine wave , along with required nos. of SMF batteries, battery stand & required accessories etc as per tender specifications complete as required. | 2.00 | Each |  | 51060.00 | 102120.00 | 50000.00 | 100000.00 | 100000.00 | ANIL KUMAR
5.00 | Supply of 12 Core, Single Mode, OS2, armoured optical Fibre cable, external rodent resistant with as per standard specification as required. | 4500.00 | Mtrs |  | 80.00 | 360000.00 | 60.00 | 270000.00 | 270000.00 | ANIL KUMAR
6.00 | Laying of one no. optical fiber cable upto 12core in existing HDPE/GI pipe/open masnory duct/tray/open surface/trench/false ceiling/ wall surface with suitable metal saddle etc complete as required. | 4500.00 | Mtrs |  | 10.00 | 45000.00 | 9.00 | 40500.00 | 40500.00 | ANIL KUMAR
7.00 | Supply,installation,testing & commissioning of following connectivity accessories for optical fiber cable etc complete as required:
7.01 | 24 Port LIU fully loaded with splicing of 24 Nos.SC pigital and coupler | 11.00 | Each |  | 26250.00 | 288750.00 | 20000.00 | 220000.00 | 220000.00 | ANIL KUMAR
7.02 | 12 Port LIU fully loaded with splicing of 12 Nos. SC pigital and coupler | 8.00 | Each |  | 20400.00 | 163200.00 | 16000.00 | 128000.00 | 128000.00 | ANIL KUMAR
7.03 | SC-SC single mode fiber optic patch cord, 2 mtr | 29.00 | Each |  | 2000.00 | 58000.00 | 1800.00 | 52200.00 | 52200.00 | ANIL KUMAR
7.04 | SC-SC single mode fiber optic patch cord, 10 mtr | 10.00 | Each |  | 5500.00 | 55000.00 | 6300.00 | 63000.00 | 55000.00 | Ruhi Electronics
7.05 | Floor mounted 18U Network rack with 5/15 amp PDU, fan and handware etc | 1.00 | Each |  | 52000.00 | 52000.00 | 40000.00 | 40000.00 | 40000.00 | ANIL KUMAR
7.06 | Wall mounted indoor type 6U Network rack with 5/15 amp PDU, fan and handware etc | 8.00 | Each |  | 10000.00 | 80000.00 | 10000.00 | 80000.00 | 80000.00 | ANIL KUMAR, Ruhi Electronics
7.07 | Pole mounted outdoor type 6U Network rack with 5/15 amp PDU, fan and handware etc i/c Supply & fixing of weather proof 3" dia.,1.2M height hard PVC Pole with suitable mouting GI/SS Clamp and other required accessories for mounting the Network rack and cxcluding CC work. | 3.00 | Each |  | 51000.00 | 153000.00 | 41000.00 | 123000.00 | 123000.00 | ANIL KUMAR
7.08 | Media converter 10/100 SC to SC for OFC single mode: Simplex | 13.00 | Each |  | 3500.00 | 45500.00 | 3100.00 | 40300.00 | 40300.00 | ANIL KUMAR
7.09 | Media converter chassis, 14 slot | 1.00 | Each |  | 45000.00 | 45000.00 | 41000.00 | 41000.00 | 41000.00 | ANIL KUMAR
7.10 | OTDR test per core of OFC with submission of report etc as required. | 72.00 | Each |  | 160.00 | 11520.00 | 340.00 | 24480.00 | 11520.00 | Ruhi Electronics
8.00 | Supply and making outdoor type joint with suitable kit enclosure including splicing, all accessories for Single Mode,12 core armoured optical Fibre cable etc. complete as required. | 3.00 | Job |  | 5000.00 | 15000.00 | 5250.00 | 15750.00 | 15000.00 | Ruhi Electronics
9.00 | Supply of following sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS:7098 (Part I),1988 amended upto date etc complete as required.
9.01 | 3.5C x 50 sqmm | 100.00 | Mtrs |  | 290.00 | 29000.00 | 455.00 | 45500.00 | 29000.00 | Ruhi Electronics
9.02 | 3.5C x 35 sqmm | 3700.00 | Mtrs |  | 201.00 | 743700.00 | 305.00 | 1128500.00 | 743700.00 | Ruhi Electronics
10.00 | Supply of power cable of 1.1KV grade of following sizes copper conductor PVC insulated PVC sheathed un-armoured power cable confirming to IS:694 with upto date ammendments etc complete as required.
10.01 | 3C x 6 sqmm | 200.00 | Mtrs |  | 202.00 | 40400.00 | 200.00 | 40000.00 | 40000.00 | ANIL KUMAR
11.00 | Supply of following size outer dia. HDPE pipe as per IS:4984:1995,Material Grade:PE 100, PN10 and as per specified in particular specification.
11.01 | 32 mm | 3500.00 | Mtrs |  | 40.00 | 140000.00 | 30.00 | 105000.00 | 105000.00 | ANIL KUMAR
11.02 | 50 mm | 3200.00 | Mtrs |  | 100.00 | 320000.00 | 80.00 | 256000.00 | 256000.00 | ANIL KUMAR
12.00 | Supply of DWC HDPE Pipe of ID:38mm & OD:50mm as per confirming to IS:16205 amended upto date etc complete as required. | 100.00 | Mtrs |  | 50.00 | 5000.00 | 45.00 | 4500.00 | 4500.00 | ANIL KUMAR
13.00 | Laying of following sizes outer dia. HDPE/DWC HDPE pipe in the existing trench/open duct/closed duct including coupling, splicing of pipe etc complete as required.
13.01 | 32 mm | 1000.00 | Mtrs |  | 14.00 | 14000.00 | 11.00 | 11000.00 | 11000.00 | ANIL KUMAR
13.02 | 50mm | 400.00 | Mtrs |  | 20.00 | 8000.00 | 22.00 | 8800.00 | 8000.00 | Ruhi Electronics
14.00 | Laying of following sizes outer dia. HDPE pipe with HDD trenchless method direct in ground at minimum depth of 3.0 meter (i/c under Runway/Taxiway/Road) in all type soil including coupling, splicing of pipe,rope etc complete as required in all respect as per specification.
14.01 | 32 mm | 2500.00 | Mtrs |  | 236.00 | 590000.00 | 350.00 | 875000.00 | 590000.00 | Ruhi Electronics
14.02 | 50mm | 2900.00 | Mtrs |  | 236.00 | 684400.00 | 350.00 | 1015000.00 | 684400.00 | Ruhi Electronics
15.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power/RC cable of 1.1 kV grade of following size in the existing RCC/GI/HUME/METAL/HDPE pipe etc. as required.
15.01 | Upto 35 sq. mm | 3400.00 | Mtrs |  | 30.00 | 102000.00 | 28.00 | 95200.00 | 95200.00 | ANIL KUMAR
15.02 | Above 35 sq. mm and upto 95 sq. mm | 40.00 | Mtrs |  | 50.00 | 2000.00 | 45.00 | 1800.00 | 1800.00 | ANIL KUMAR
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power/RC cable of 1.1 KV grade of following size in the existing masonry open duct as required.
16.01 | Upto 35 sq. mm | 300.00 | Mtrs |  | 20.00 | 6000.00 | 20.00 | 6000.00 | 6000.00 | ANIL KUMAR, Ruhi Electronics
16.02 | Above 35 sq. mm and upto 95 sq. mm | 60.00 | Mtrs |  | 30.00 | 1800.00 | 40.00 | 2400.00 | 1800.00 | Ruhi Electronics
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
17.01 | 3.5C x 50 sqmm (35mm) | 4.00 | Set |  | 500.00 | 2000.00 | 500.00 | 2000.00 | 2000.00 | ANIL KUMAR, Ruhi Electronics
17.02 | 3.5C x 35 sqmm (32mm) | 13.00 | set |  | 400.00 | 5200.00 | 450.00 | 5850.00 | 5200.00 | Ruhi Electronics
18.00 | Supply and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
18.01 | 3.5C x 35 sqmm | 4.00 | Job |  | 2200.00 | 8800.00 | 2800.00 | 11200.00 | 8800.00 | Ruhi Electronics
19.00 | Laying of following size one number cu conductor power cable of 1.1 KV grade in existing HDPE/GI pipe/open masnory duct/open surface etc including proper termination etc complete as required.
19.01 | 3C x 2.5 sqmm | 200.00 | Mtrs |  | 10.00 | 2000.00 | 12.00 | 2400.00 | 2000.00 | Ruhi Electronics
20.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 6/10 amps modular socket outlet and 6/10 amps modular switch, connection etc. as required. | 10.00 | Each |  | 500.00 | 5000.00 | 550.00 | 5500.00 | 5000.00 | Ruhi Electronics
21.00 | Supply and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required | 5.00 | Each |  | 700.00 | 3500.00 | 700.00 | 3500.00 | 3500.00 | ANIL KUMAR, Ruhi Electronics
22.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/ recessed 20mm dia meduim class PVC conduit / Casing Caping as required.
22.01 | 2x4.0 Sq.mm + 1x4.0 Sq.mm earth wire. | 100.00 | Mtrs |  | 300.00 | 30000.00 | 300.00 | 30000.00 | 30000.00 | ANIL KUMAR, Ruhi Electronics
23.00 | Earthing with GI earth plate 600 mm X 600 mm X6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 3.00 | Set |  | 6500.00 | 19500.00 | 7200.00 | 21600.00 | 19500.00 | Ruhi Electronics
24.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 18.00 | Mtrs |  | 800.00 | 14400.00 | 700.00 | 12600.00 | 12600.00 | ANIL KUMAR
25.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 30.00 | Mtrs |  | 150.00 | 4500.00 | 200.00 | 6000.00 | 4500.00 | Ruhi Electronics
26.00 | Excavation for cable/pipe trenching/foundation etc as per site requirement of depth upto 1.2 m in soft soil including refilling,dressing of sides and ramming of bottoms,getting out the excavated soil and disposal of surplus excavated soil as directed within a lead of 50 metres. | 68.00 | Cum |  | 350.00 | 23800.00 | 300.00 | 20400.00 | 20400.00 | ANIL KUMAR
27.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in trenching/foundation for cable/pipe laying etc including form work etc as required. | 3.00 | Cum |  | 8000.00 | 24000.00 | 7500.00 | 22500.00 | 22500.00 | ANIL KUMAR
28.00 | Constructing brick masonry chamber of size 1200mmx1200mmx1000mm of inner clearnce with wall width 225mm in cement mortar 1:4 (1 cement :4 coarse sand ) inside cement plaster 12 mm thick with cement mortar 1:3 (1 cement: 3 Coarse sand) finished with floating coat of neat cement foundation concrete 1:3:6( 1 cement: 3 coarse sand:6 graded stone aggregate 40 mm nominal size) all complete as per standard design with cover of 100 mm thickness made by RCC in cement mortar 1:2:4( 1 cement: 2 coarse sand:4 graded stone aggregate 40 mm nominal size) in two piece with 12 mm rod handle in order to easy handling. | 20.00 | Job |  | 20000.00 | 400000.00 | 17000.00 | 340000.00 | 340000.00 | ANIL KUMAR
29.00 | Excavation of hard rock for cable trench depth upto 1.2 m including refilling by soft soil,getting out and disposal of excavated soil as directed within a lead of 50 metres. | 1.00 | Cum |  | 2200.00 | 2200.00 | 1000.00 | 1000.00 | 1000.00 | ANIL KUMAR
30.00 | Cutting cement concrete/road bitumins by manually/ mechanical including disposal of material within 50 metres lead as directed. | 1.00 | Cum |  | 2500.00 | 2500.00 | 1000.00 | 1000.00 | 1000.00 | ANIL KUMAR
31.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 10.00 | Each |  | 900.00 | 9000.00 | 450.00 | 4500.00 | 4500.00 | ANIL KUMAR
| Total in Figures |  |  |  |  | 5993830.00 |  | 6817200.00
Lowest Amount Quoted BY: Ruhi Electronics(5993830.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of New Automatic Weather Observation System (AWOS) at JPNI Airport Patna SH Electrical Works Tender ID: 2023_AAI_157500_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ruhi Electronics | 5993830.00 | L1
| 2 | ANIL KUMAR | 6817200.00 | L2