## BoQ1
Government eProcurement System Created By: SUDHAKARA NAIK Created Date/Time: 31-Jul-2023 12:57 PM Tender Title: Provision of Power Supply for Lighting the Premises of Quarters Including Lighting etc. at Belagavi Airport Tender ID: 2023_AAI_159204_1
Tender Inviting Authority: AGM (Engg-E), AAI, Belagavi Airport
Name of Work: PROVISION OF POWER SUPPLY FOR LIGHTING THE PREMISES OF QUARTERS INCLUDING LIGHTING ETC AT BELAGAVI AIRPORT.
Contract No: AAI/BGM/Engg-E/2023-24/ Date: 05/07/2023
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | ANU ELECTRICALS(GSTN-29AKWPM5631P1Z2) |  | DEEPAKELECTRICALS(GSTN-33ALUPD3531C1ZI) |  | Manish Electricals(GSTN-23ABLPM9012E1ZW)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying of following size cables as per technical specification etc. complete as required.
1.01 | 3.5C X 50 Sq.mm, Aluminium conductor, XLPE insulated and FRLS outer Sheethed Armored of 1.1KV grade as per IS.7098 | 220.00 | Mtr | 100.00 | 260.00 | 57200.00 | 250.00 | 55000.00 | 340.00 | 74800.00 | 300.00 | 66000.00 | 55000.00 | ANU ELECTRICALS
1.02 | 3.5C X 70 Sq.mm, Aluminium conductor, XLPE insulated and FRLS outer Sheethed Armored of 1.1KV grade as per IS.7098 | 770.00 | Mtr | 10.00 | 360.00 | 277200.00 | 400.00 | 308000.00 | 410.00 | 315700.00 | 415.00 | 319550.00 | 277200.00 | Shantha ELectricals and Engineers Pvt Ltd
2.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 75 mm dia (OD-75 mm & ID-63 mm nominal) | 670.00 | Mtr | 10.00 | 260.00 | 174200.00 | 300.00 | 201000.00 | 210.00 | 140700.00 | 300.00 | 201000.00 | 140700.00 | DEEPAKELECTRICALS
3.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 35 sq. mm and upto 95 sq. mm | 900.00 | Mtr | 10.00 | 40.00 | 36000.00 | 100.00 | 90000.00 | 33.00 | 29700.00 | 30.00 | 27000.00 | 27000.00 | Manish Electricals
4.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size on wall surface as required. Upto 35 sq.mm (clamped with 1mm thick saddle) | 11.50 | Mtr | 10.00 | 50.00 | 575.00 | 12.00 | 138.00 | 40.00 | 460.00 | 120.00 | 1380.00 | 138.00 | ANU ELECTRICALS
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 75.00 | Mtr | 10.00 | 70.00 | 5250.00 | 28.00 | 2100.00 | 22.00 | 1650.00 | 30.00 | 2250.00 | 1650.00 | DEEPAKELECTRICALS
6.00 | Supplying and making end termination with double compression brass gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade (Weather proof for feeder pillar & Flame proof for In-door Panel) as required.
6.01 | 3½ X 50 sq. mm (35mm). | 2.00 | Set | 10.00 | 1600.00 | 3200.00 | 300.00 | 600.00 | 300.00 | 600.00 | 700.00 | 1400.00 | 600.00 | ANU ELECTRICALS, DEEPAKELECTRICALS
6.02 | 3½ X 70 sq. mm (38mm). | 10.00 | Set | 10.00 | 1800.00 | 18000.00 | 500.00 | 5000.00 | 350.00 | 3500.00 | 700.00 | 7000.00 | 3500.00 | DEEPAKELECTRICALS
6.03 | 3½ X 120 sq. mm (45mm). | 1.00 | Set | 10.00 | 2100.00 | 2100.00 | 600.00 | 600.00 | 400.00 | 400.00 | 1000.00 | 1000.00 | 400.00 | DEEPAKELECTRICALS
7.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 30.00 | Each | 10.00 | 3000.00 | 90000.00 | 500.00 | 15000.00 | 400.00 | 12000.00 | 500.00 | 15000.00 | 12000.00 | DEEPAKELECTRICALS
8.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement: 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 3.00 | Each | 10.00 | 19800.00 | 59400.00 | 20000.00 | 60000.00 | 18000.00 | 54000.00 | 14000.00 | 42000.00 | 42000.00 | Manish Electricals
9.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement: 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 100x90 cm and 50 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 3.00 | Each | 10.00 | 15500.00 | 46500.00 | 19900.00 | 59700.00 | 26000.00 | 78000.00 | 14000.00 | 42000.00 | 42000.00 | Manish Electricals
10.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 40 mm nominal size) in feeder pillar base pedestals, including form work, CC Bed of 0.3 Width X 0.750 Long X 0.750 (2 Nos per Each Panel) Depth with protusion of 200mm above ground including excavation and refilling etc complete as required. | 4.00 | Job | 10.00 | 5500.00 | 22000.00 | 20000.00 | 80000.00 | 2700.00 | 10800.00 | 3000.00 | 12000.00 | 10800.00 | DEEPAKELECTRICALS
11.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 40 mm nominal size) in feeder pillar base pedestals, including form work, CC Bed of 0.20 Width X 0.550 Long X 0.550 Mtr (2 Nos per Each Panel) Depth with protusion of 200mm above ground including excavation and refilling etc complete as required. | 2.00 | Job | 10.00 | 4200.00 | 8400.00 | 20000.00 | 40000.00 | 2000.00 | 4000.00 | 8500.00 | 17000.00 | 4000.00 | DEEPAKELECTRICALS
12.00 | OUT DOOR FEEDER PILLARS ESSENTIAL SUPPLY-FEEDER PANEL Supply, installation, testing and commisioning of outdoor feeder pillar Double door LT Panel, Compartmentalised cubicle type, fabricated from CRCA sheet steel of 2 mm thick for frame work and covers, Cable entry through bottom cable gland Plate-3 mm, hinged door, totally enclosed-dust & vermin proof (min IP-66),Gasket lined, PCC Pedestal support free mounting with spacing of atleast 300mm between ground level and panel, Uppermost Handle Height shall be at 1.7 mtr limit, Panel design shall conform to IS 8623 / IEC 60439 & of Form-3b construction with sufficient space for heat dissipation, Curved canopy to ensure immediate drain of Rain water, Lifting Hooks, Base channel MS channel Base of 75 mm x 5mm I beam, construction and Aluminium Plate Tags, Affixed danger board- size 200 mm x 150 mm, Three languages (Local, Hindi, English), coated with approved shade of powder coat Detailed Circuit diagram with a laminate Coat/Aluminium Plate on inside of Panel, Cubicle Metal tags identifying Circuit i.e feeder Number and designation, Iron angle/Channel frame work with necessary cable alley, heat shrink sleeved bus bar and bus bar chamber, Cable termination Shrouding with transparent hylam / mica sheet of not less than 10mm, interconnection using suitable size copper leads/solid aluminium strips, cable terminals blocks, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos. earth studs on either side with cut-ots cloase with Bush, Earth wire frompnael frame & cuble doors should be tapped to earth Bar , suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system interconnections with suitable size of copper leads/solid aluminium strips. The panel shall be fabricated from a firm having CPRI certification with test certificates for similar panel (required for short circuit rating, temperature rise and IP classification) as per drawing & Technical specification.
12.01 | Essential Feeder Pillar #1: Main (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 353000.00 | 353000.00 | 100000.00 | 100000.00 | 210000.00 | 210000.00 | 275000.00 | 275000.00 | 100000.00 | ANU ELECTRICALS
12.02 | Essential Feeder Pillar #2: Stand-by (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 365000.00 | 365000.00 | 100000.00 | 100000.00 | 235000.00 | 235000.00 | 105000.00 | 105000.00 | 100000.00 | ANU ELECTRICALS
12.03 | Essential Feeder Pillar #3: Junction feeder panel (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 310000.00 | 310000.00 | 120000.00 | 120000.00 | 255000.00 | 255000.00 | 115000.00 | 115000.00 | 115000.00 | Manish Electricals
12.04 | Essential Feeder Pillar #4: STP feeder panel (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 493000.00 | 493000.00 | 120000.00 | 120000.00 | 275000.00 | 275000.00 | 105000.00 | 105000.00 | 105000.00 | Manish Electricals
12.05 | Essential Sub-Feeder Pillar #5: Quarters:2 (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 258000.00 | 258000.00 | 150000.00 | 150000.00 | 170000.00 | 170000.00 | 95000.00 | 95000.00 | 95000.00 | Manish Electricals
12.06 | Essential Sub-Feeder Pillar #6: Guest House-IV (Refer Technical Specifications in Tender Document for all details of Cubicles with components, Incomer, Outgoing etc.) | 1.00 | Each | 10.00 | 273000.00 | 273000.00 | 150000.00 | 150000.00 | 200000.00 | 200000.00 | 75000.00 | 75000.00 | 75000.00 | Manish Electricals
13.00 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. Cement concrete filling with 1:2:4 of entire excavated trench and disposing of surplus excavated soil as directed, within a lead of 50 m : All kinds of soil-(Bitumen Road). Pipes including collar exceeding 80 mm dia. but not exceeding 300 mm dia (0.60 width) | 10.00 | Mtr | 10.00 | 3000.00 | 30000.00 | 800.00 | 8000.00 | 900.00 | 9000.00 | 1200.00 | 12000.00 | 8000.00 | ANU ELECTRICALS
14.00 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.0 m, including getting out the excavated soil, Providing and laying non-pressure B- class GI pipes-100mm Dia with collars jointed with GI couplers, Cement concrete filling with 1:2:4 of entire excavated trench and disposing of surplus excavated soil as directed, within a lead of 50 m : All kinds of soil-Bitumen Road. GI Pipe-B class- 100mm including coupler (0.30 width) | 12.00 | Mtr | 10.00 | 2700.00 | 32400.00 | 1000.00 | 12000.00 | 1900.00 | 22800.00 | 1600.00 | 19200.00 | 12000.00 | ANU ELECTRICALS
15.00 | Supply & laying of 1.5 Mtr GI 'B' class pipe-100mm across existing drain including Making chases up to 15x15 cm in drain wall for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), including finishing complete so as to make it leak proof etc complete as required. | 2.00 | Job | 10.00 | 18000.00 | 36000.00 | 999.00 | 1998.00 | 3200.00 | 6400.00 | 1200.00 | 2400.00 | 1998.00 | ANU ELECTRICALS
16.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Set | 10.00 | 9500.00 | 95000.00 | 5000.00 | 50000.00 | 6500.00 | 65000.00 | 7500.00 | 75000.00 | 50000.00 | ANU ELECTRICALS
17.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 46.00 | Mtr | 10.00 | 1100.00 | 50600.00 | 100.00 | 4600.00 | 220.00 | 10120.00 | 700.00 | 32200.00 | 4600.00 | ANU ELECTRICALS
18.00 | Providing and laying of 6 SWG GI wire inside excavated cable trench/humepipe for loop earthing etc complete as required. | 990.00 | Mtr | 10.00 | 45.00 | 44550.00 | 50.00 | 49500.00 | 35.00 | 34650.00 | 30.00 | 29700.00 | 29700.00 | Manish Electricals
19.00 | Supplying and fixing of following size HDPE pipe-PN6, 63mm Dia. ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. etc., complete as required. HDPE Pipe-63mm Dia, PN6 clamped with 25x3mm MS flat clamp | 80.00 | Mtr | 10.00 | 290.00 | 23200.00 | 200.00 | 16000.00 | 150.00 | 12000.00 | 400.00 | 32000.00 | 12000.00 | DEEPAKELECTRICALS
20.00 | Supply of LED street light (06 Mtr height) Luminaire/fitting with epoxy powder coated pressure die cast aluminium housing, having system lumen output not less than 4800 lumens and system efficacy of not less than 120 lumens per watt, CCT 5700K, Complete with electronic driver and accessories etc, encapsulated and suitable for outdoor pole arm mounting application with IP66 or above & IK 07 or above complete with integrated street Light optics and as per technical specifications etc complete as required. (Similar to Philips-CAT No. BRP331 LED48 CW R5N PC PSU S1 or equivalent). | 31.00 | EA | 10.00 | 2800.00 | 86800.00 | 9900.00 | 306900.00 | 4000.00 | 124000.00 | 5000.00 | 155000.00 | 86800.00 | Shantha ELectricals and Engineers Pvt Ltd
21.00 | Supply of LED flood light/Area Light Luminaire for High Mast (12 Mtr height) with high pressure die cast Aluminium / standard alloy housing and LEDs of approved make pasted on diecast housing and high efficiency PMMA diffuser, Driver installed on cast aluminium housing and prewired upto the terminal block. It has a system lumen output not less than 16200 lumens with luminaire efficacy of not less than 135lm/W, CCT 5700, suitable for outdoor applications with IP66 or above & IK 07 and as per technical specifications etc complete as required. (Similar to Philips- CAT No: BVP192 LED165 CW NB FG A1 PSU GR or equivalent) | 18.00 | EA | 10.00 | 8200.00 | 147600.00 | 15000.00 | 270000.00 | 12800.00 | 230400.00 | 25000.00 | 450000.00 | 147600.00 | Shantha ELectricals and Engineers Pvt Ltd
| Total in Figures |  |  |  |  | 3398175.00 |  | 2376136.00 |  | 2585680.00 |  | 2332080.00
Lowest Amount Quoted BY: Manish Electricals(2332080.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Power Supply for Lighting the Premises of Quarters Including Lighting etc. at Belagavi Airport Tender ID: 2023_AAI_159204_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 2332080.00 | L1
| 2 | ANU ELECTRICALS | 2376136.00 | L2
| 3 | DEEPAKELECTRICALS | 2585680.00 | L3
| 4 | Shantha ELectricals and Engineers Pvt Ltd | 3398175.00 | L4