## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 02-Aug-2023 06:21 PM Tender Title: Modification and upgradation of existing Departure BHS into Inline X Ray Baggage Handling System at Amritsar Airport. SH Provision of Air conditioning for CT EDS machine and associated equipment of ILBHS at Amritsar airport. Tender ID: 2023_AAI_159982_1
Tender Inviting Authority: <Asstt. GM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Modification and upgradation of existing Departure BHS into Inline X-Ray Baggage Handling System at Amritsar Airport. SH: Provision of Air-conditioning for CT EDS machine and associated equipment of ILBHS at Amritsar airport..>
Tender ID: <2023_AAI_159982_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Blue Star Limited(GSTN-04AAACB4487D1Z0) |  | PRINCE AIRCON(GSTN-03AAVFP8627R1Z6) |  | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | PROJENIX PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
0.00 | SH-A (Hi side)
1.00 | Supply of modular type Variable Refrigerant Flow / Variable Refrigerant Volume air-cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), microprocessor-based Controller, top discharge type condensing unit(s), with R410A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 415V +/- 10%, 3 Phase, 50 Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP shall be 3.7 at 100% load and 7.5 at 50% load at AHRI conditions.
1.10 | 32 HP (COOLING ODU UNIT) | 2.00 | Nos |  | 470000.00 | 940000.00 | 435180.00 | 870360.00 | 670000.00 | 1340000.00 | 613216.00 | 1226432.00 | 870360.00 | PRINCE AIRCON
2.00 | Supply of following minimum capacity VRV/VRF High wall type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, Corded/cordless remote control, drain water lift-up mechanism, necessary accessories, etc., suitable for operation on 230V±10%, 50Hz, single-phase AC supply, complete as required. The unit shall have automatic force shutdown provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be as per site conditions.
2.10 | 1.60 TR or equivalent | 10.00 | Nos |  | 19950.00 | 199500.00 | 20706.00 | 207060.00 | 24000.00 | 240000.00 | 21491.00 | 214910.00 | 199500.00 | Blue Star Limited
2.20 | 2.00 TR or equivalent | 4.00 | Nos |  | 20200.00 | 80800.00 | 21288.00 | 85152.00 | 26000.00 | 104000.00 | 21838.00 | 87352.00 | 80800.00 | Blue Star Limited
3.00 | Supply of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports, etc., suitable for operation on single-phase AC supply 230V±10%, 50Hz, complete as required. The unit shall have automatic force shutdown provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be as per site conditions.
3.10 | 3.3TR or Equivalent | 8.00 | Nos |  | 34500.00 | 276000.00 | 39646.00 | 317168.00 | 40000.00 | 320000.00 | 36930.00 | 295440.00 | 276000.00 | Blue Star Limited
3.20 | Sh-B (Installation)
4.00 | ITC of Outdoor Units address setting & capacity as mentioned below. Multispeed motor, coil section with DX coil, outer cabinet, drain pan, drain water lift-up mechanism, insulation, pipe connections etc. of various capacities as per specifications & drawings.
4.10 | 32 HP (COOLING ODU UNIT) | 2.00 | Nos |  | 25980.00 | 51960.00 | 96000.00 | 192000.00 | 20000.00 | 40000.00 | 48488.00 | 96976.00 | 40000.00 | VOLKS ENERGIE PVT LTD
5.00 | Installation, testing and commissioning of Indoor Unit capacity as mentioned below including supply and installation of suitable Refnet, Mounting assembly, all necessary accessories etc. required for successful operations as per site conditions
5.10 | Ceiling mounted ductable Indoor unit (3.3TR)+ REFNET | 8.00 | Nos |  | 5200.00 | 41600.00 | 8000.00 | 64000.00 | 1000.00 | 8000.00 | 209.00 | 1672.00 | 1672.00 | PROJENIX PRIVATE LIMITED
5.20 | Hi-Wall (1.60TR) + REFNET | 10.00 | Nos |  | 4550.00 | 45500.00 | 6500.00 | 65000.00 | 1000.00 | 10000.00 | 523.00 | 5230.00 | 5230.00 | PROJENIX PRIVATE LIMITED
5.30 | Hi-Wall (2.00TR) + REFNET | 4.00 | Nos |  | 4550.00 | 18200.00 | 6500.00 | 26000.00 | 1000.00 | 4000.00 | 836.00 | 3344.00 | 3344.00 | PROJENIX PRIVATE LIMITED
6.00 | Supply, Installation, testing and commissioning including vacuumization and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring-type hanger supports, jointing/brazing including accessories, including necessary wall crossing by making suitable hole and refilling with suitable sealant & insulated with XPLE Class-O tubular insulation/with Class-O closed-cell elastomeric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications, etc. as required:
6.10 | 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2mm with 19mm thick insulation | 100.00 | RMT |  | 1580.00 | 158000.00 | 1624.00 | 162400.00 | 1176.00 | 117600.00 | 894.00 | 89400.00 | 89400.00 | PROJENIX PRIVATE LIMITED
6.20 | 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 20.00 | RMT |  | 100.00 | 2000.00 | 1600.00 | 32000.00 | 917.00 | 18340.00 | 686.00 | 13720.00 | 2000.00 | Blue Star Limited
6.30 | 19 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 150.00 | RMT |  | 100.00 | 15000.00 | 1099.00 | 164850.00 | 800.00 | 120000.00 | 582.00 | 87300.00 | 15000.00 | Blue Star Limited
6.40 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 60.00 | RMT |  | 960.00 | 57600.00 | 1100.00 | 66000.00 | 674.00 | 40440.00 | 493.00 | 29580.00 | 29580.00 | PROJENIX PRIVATE LIMITED
6.50 | 12.7 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19mm thick insulation | 130.00 | RMT |  | 710.00 | 92300.00 | 800.00 | 104000.00 | 500.00 | 65000.00 | 346.00 | 44980.00 | 44980.00 | PROJENIX PRIVATE LIMITED
6.60 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 200.00 | RMT |  | 550.00 | 110000.00 | 667.00 | 133400.00 | 445.00 | 89000.00 | 263.00 | 52600.00 | 52600.00 | PROJENIX PRIVATE LIMITED
6.70 | 6.4 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 50.00 | RMT |  | 50.00 | 2500.00 | 650.00 | 32500.00 | 335.00 | 16750.00 | 187.00 | 9350.00 | 2500.00 | Blue Star Limited
7.00 | Providing and fixing of PVC drain water piping complete with fittings, support including necessary wall crossing by making suitable hole and refilling with suitable sealant as per specification. | 180.00 | RMT |  | 35.00 | 6300.00 | 210.00 | 37800.00 | 100.00 | 18000.00 | 84.00 | 15120.00 | 6300.00 | Blue Star Limited
8.00 | Supply and laying, testing & commissioning of following sizes of Copper control cables with PVC conduit, including fixing clamps & effecting proper connections to equipment, etc. complete as required.
8.10 | 3C X2.5 Sqmm | 200.00 | RMT |  | 215.00 | 43000.00 | 240.00 | 48000.00 | 100.00 | 20000.00 | 172.00 | 34400.00 | 20000.00 | VOLKS ENERGIE PVT LTD
8.20 | 2C x 1.5 Sqmm | 200.00 | RMT |  | 140.00 | 28000.00 | 190.00 | 38000.00 | 100.00 | 20000.00 | 84.00 | 16800.00 | 16800.00 | PROJENIX PRIVATE LIMITED
9.00 | SITC of suitable size MS stand required for ODU as per specification. | 4.00 | Nos |  | 3250.00 | 13000.00 | 6500.00 | 26000.00 | 8000.00 | 32000.00 | 3135.00 | 12540.00 | 12540.00 | PROJENIX PRIVATE LIMITED
10.00 | SITC of GSS Sheet metal confirming to relevant IS standard and with suitable supports using MS angles,channels,rods,anchor bolts etc. without insulation as per site condition and specification.
10.10 | 22G galvanized sheet steel | 25.00 | Sq. Mtr |  | 100.00 | 2500.00 | 1290.00 | 32250.00 | 1000.00 | 25000.00 | 836.00 | 20900.00 | 2500.00 | Blue Star Limited
10.20 | 24G galvanized sheet steel | 25.00 | Sq. Mtr |  | 100.00 | 2500.00 | 1290.00 | 32250.00 | 900.00 | 22500.00 | 679.00 | 16975.00 | 2500.00 | Blue Star Limited
11.00 | Supply, laying , testing & commissioning of 1100V XLPE insulated PVC Sheathed armoured Al. conductor cable including supply and fixing clamps etc as required as per IS 7098 part I of following size:
11.10 | 3.5 X 50 Sqmm | 200.00 | RMT |  | 600.00 | 120000.00 | 240.00 | 48000.00 | 400.00 | 80000.00 | 314.00 | 62800.00 | 48000.00 | PRINCE AIRCON
11.20 | 3.5C X 25 Sqmm | 200.00 | RMT |  | 375.00 | 75000.00 | 180.00 | 36000.00 | 240.00 | 48000.00 | 251.00 | 50200.00 | 36000.00 | PRINCE AIRCON
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required.
12.10 | 3.5 X 50 Sqmm | 6.00 | Nos |  | 2600.00 | 15600.00 | 30.00 | 180.00 | 1000.00 | 6000.00 | 125.00 | 750.00 | 180.00 | PRINCE AIRCON
12.20 | 3.5C X 25 Sqmm | 6.00 | Nos |  | 1950.00 | 11700.00 | 30.00 | 180.00 | 1000.00 | 6000.00 | 52.00 | 312.00 | 180.00 | PRINCE AIRCON
13.00 | Supplying, Installation, Testing and commissioning of surface/ recess mounted, 415 V, FP, Panel with IP 42 protection, fabricated with 2mm thick CRCA Sheet complete with detachable gland plate suitable entry for cables and front hinged door locking arrangement duly powder coated, required MCB/MCCB/Suitable capacity Busbar as require rating, accessories including connection, inter connection, wiring with minimum 2.5 sqmm flexible copper wire & provision for earth connection etc complete as required including following: 1) 01 Incomer- 100 Amp, FP ,MCCB 2) 02 nos. Outgoing - 63 Amp FP RCCB, AC Type. 3) 03 Nos. Outgoing- 40Amp FP RCCB, AC Type. | 2.00 | Nos |  | 50000.00 | 100000.00 | 40000.00 | 80000.00 | 100000.00 | 200000.00 | 60088.00 | 120176.00 | 80000.00 | PRINCE AIRCON
14.00 | Supplying, Installation, Testing and commissioning of surface/ recess mounted, 415 V, FP, Panel with IP 54 protection, fabricated with 2mm thick CRCA Sheet complete with detachable gland plate suitable entry for cables and front hinged door locking arrangement duly powder coated, required MCB/MCCB/Suitable capacity Busbar as require rating, accessories including connection, inter connection, wiring with minimum 2.5 sqmm flexible copper wire & provision for earth connection etc complete as required including following: 1) 01 Incomer- 63 Amp, FP, RCCB, AC Type. 2) 03 nos. Outgoing -40 Amp, FP, RCCB, AC Type. | 2.00 | Nos |  | 41000.00 | 82000.00 | 25000.00 | 50000.00 | 70000.00 | 140000.00 | 49638.00 | 99276.00 | 50000.00 | PRINCE AIRCON
15.00 | Supplying and fixing of surface/ recess mounting, 230 V, FP Distribution board made of sheet steel, dust protected, duly powder painted, hinged door, Suitable cable entry, earth bar etc. complete as required including following: 1) 01 Incomer- 40 Amp FP RCCB, AC Type. 2) 10 Nos. Outgoing - 6/16 Amp SP MCB, "C" Curve. | 4.00 | Nos |  | 24000.00 | 96000.00 | 15000.00 | 60000.00 | 50000.00 | 200000.00 | 28215.00 | 112860.00 | 60000.00 | PRINCE AIRCON
16.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required. A) 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 300.00 | RMT |  | 300.00 | 90000.00 | 100.00 | 30000.00 | 170.00 | 51000.00 | 251.00 | 75300.00 | 30000.00 | PRINCE AIRCON
17.00 | Supplying and fixing suitable size/ modules, GI box alongwith modular base & cover plate for modular switches in recess/surface etc. i/c Supplying and fixing 01 no. modular switch 15/16 A and 01 no. 6 pin 15/16 A socket outlet socket including connections etc. | 25.00 | Job |  | 460.00 | 11500.00 | 700.00 | 17500.00 | 500.00 | 12500.00 | 784.00 | 19600.00 | 11500.00 | Blue Star Limited
18.00 | Supply and filling of R410A Referigerant gas as per site requirement | 45.00 | Kg |  | 1050.00 | 47250.00 | 100.00 | 4500.00 | 600.00 | 27000.00 | 637.00 | 28665.00 | 4500.00 | PRINCE AIRCON
19.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays bends with perforation not more than 17.5%, joined with connectors,suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 120.00 | Mtr |  | 470.00 | 56400.00 | 450.00 | 54000.00 | 450.00 | 54000.00 | 418.00 | 50160.00 | 50160.00 | PROJENIX PRIVATE LIMITED
20.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm | 150.00 | Mtr |  | 80.00 | 12000.00 | 75.00 | 11250.00 | 225.00 | 33750.00 | 31.00 | 4650.00 | 4650.00 | PROJENIX PRIVATE LIMITED
21.00 | Supplying and fixing piano type 5A switch (01 No) and 5A 3 Pin socket (04 Nos) including supply and fixing of switch box and cover including connections etc. as required. | 15.00 | Nos |  | 450.00 | 6750.00 | 300.00 | 4500.00 | 800.00 | 12000.00 | 627.00 | 9405.00 | 4500.00 | PRINCE AIRCON
21.10 | SH-C (Operation and maintenance)
22.00 | Operation and routine maintenance of VRV System involving attending to complaints/fault/break downs and taking rectification action, ensuring serviceability/satisfactory working condition of the system, maintenance of records/documentation etc. as specified by providing 01 no. of skilled manpower in each shift on all days throughout contract period.
22.10 | 1st Year | 12.00 | Months |  | 98500.00 | 1115099.00 | 85000.00 | 962268.00 | 75208.00 | 851415.00 | 80950.00 | 916419.00 | 851415.00 | VOLKS ENERGIE PVT LTD
22.20 | 2nd Year | 12.00 | Months |  | 100000.00 | 1068000.00 | 86000.00 | 918480.00 | 80000.00 | 854400.00 | 87426.00 | 933710.00 | 854400.00 | VOLKS ENERGIE PVT LTD
22.30 | 3rd Year | 12.00 | Months |  | 102000.00 | 1027670.00 | 88000.00 | 886618.00 | 85000.00 | 856392.00 | 94420.00 | 951300.00 | 856392.00 | VOLKS ENERGIE PVT LTD
23.00 | All inclusive comprehensive maintenance (After DLP of 01 year) of complete VRV system including all consumable and manpower cost required for troubleshooting, preventive maintenance and breakdown maintenance etc. as required of complete system (including outdoor units, Indoor units, gas refilling, leakage repair, PLC repair/replacement, compressors repair/replacement etc. complete in all respects) as per good engineering practice, recommendation of manufacturer and instructions of engineer-in-charge for maintaining the system in acceptable functional, operational and serviceable state.
23.10 | 2nd Year | 12.00 | Months |  | 9600.00 | 102528.00 | 13000.00 | 138840.00 | 4000.00 | 42720.00 | 11147.00 | 119050.00 | 42720.00 | VOLKS ENERGIE PVT LTD
23.20 | 3rd Year | 12.00 | Months |  | 9990.00 | 100651.00 | 14000.00 | 141053.00 | 5000.00 | 50376.00 | 11425.00 | 115109.00 | 50376.00 | VOLKS ENERGIE PVT LTD
24.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 6324408.00 |  | 6179559.00 |  | 6196183.00 |  | 6044763.00
Lowest Amount Quoted BY: PROJENIX PRIVATE LIMITED(6044763.00)

## BOQ Summary
BOQ Summary Details Tender Title: Modification and upgradation of existing Departure BHS into Inline X Ray Baggage Handling System at Amritsar Airport. SH Provision of Air conditioning for CT EDS machine and associated equipment of ILBHS at Amritsar airport. Tender ID: 2023_AAI_159982_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PROJENIX PRIVATE LIMITED | 6044763.00 | L1
| 2 | PRINCE AIRCON | 6179559.00 | L2
| 3 | VOLKS ENERGIE PVT LTD | 6196183.00 | L3
| 4 | Blue Star Limited | 6324408.00 | L4