## BoQ1
Government eProcurement System Created By: Bidyut Roy Created Date/Time: 11-Aug-2023 11:59 AM Tender Title: Provision of theme-based facia Illumination system at New Terminal building Tender ID: 2023_AAI_160693_1
Tender Inviting Authority: Asst. GENERAL MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, KOLHAPUR AIRPORT, KOLHAPUR.
Name of Work: Provision of theme-based facia Illumination system at New Terminal building of Kolhapur Airport
Contract No: 2023_AAI_160693_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PAVAN QUICK SERVICE(GSTN-NA) |  | LAD AND ASSOCIATE(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply,Installation,Testing and Commissioning of 200-400mm long LED RGBW Linear Wall Washer luminaire for Facade lighting with aluminium extruded housing, of following wattage. Luminaire shall be capable of producing dynamic color changing light for with 16 million colors by DMX/Ethernet based control. The beam angle of the fittings shall be narrow, medium, wide or asymmetric as per the requirement. Luminaire shall be complete with driver and capable of operating at line voltage without any separate power supply from 100-270VAC , 50Hz with powerfactor>0.9. Fixture shall be suitable to operate at an ambient temperature range of -10°Cto+50°and shall be IP65 and IK06 rated. Lifetime shall be at least L70:50000 burning hours at 50°C . Luminaire shall be conforming to BIS(IS10322)and shall be complete with all necessary accessories required for proper working of fixture including weatherproof connection cables ,waterproof connectors with fixing etc. as required. 25 W | 27.00 | each |  | 15661.00 | 422847.00 | 16392.00 | 442584.00 | 422847.00 | PAVAN QUICK SERVICE
2.00 | Supply,Installation,Testing and Commissioning of LED RGBW Linear Wall Washer luminaire of length 1Meter atleast for Facade lighting with aluminium extruded housing, of following wattage. Luminaire shall be capable of producing dynamic color changing light for with 16 million colors by DMX/Ethernet based control. The beam angle of the fittings shall be narrow, medium, wide or asymmetric as per the requirement. Luminaire shall be complete with driver and capable of operating at line voltage without any separate power supply from 100-270VAC , 50Hz with powerfactor>0.9. Fixture shall be suitable to operate at an ambient temperature range of-10°Cto+50°and shall be IP65 and IK06 rated. Lifetime shall be at least L70:50000 burning hours at 50°C . Luminaire shall be conforming to BIS(IS10322)and shall be complete with all necessary accessories required for proper working of fixture including weatherproof connection cables ,waterproof connectors etc. as required. 30 W | 81.00 | job |  | 20366.00 | 1649646.00 | 21400.00 | 1733400.00 | 1649646.00 | PAVAN QUICK SERVICE
3.00 | Supply,Installation,Testing and Commissioning of LED RGBW Linear Wall Washer luminaire of length 1Meter atleast for Facade lighting with aluminium extruded housing, of following wattage. Luminaire shall be capable of producing dynamic color changing light for with 16 million colors by DMX/Ethernet based control. The beam angle of the fittings shall be narrow, medium, wide or asymmetric as per the requirement. Luminaire shall be complete with driver and capable of operating at line voltage without any separate power supply from 100-270VAC , 50Hz with powerfactor>0.9. Fixture shall be suitable to operate at an ambient temperature range of-10°Cto+50°and shall be IP65 and IK06 rated. Lifetime shall be at least L70:50000 burning hours at 50°C . Luminaire shall be conforming to BIS(IS10322)and shall be complete with all necessary accessories required for proper working of fixture including weatherproof connection cables ,waterproof connectors etc. as required. 80 W | 16.00 | each |  | 32290.00 | 516640.00 | 33800.00 | 540800.00 | 516640.00 | PAVAN QUICK SERVICE
4.00 | Supply,Installation,Testing and Commissioning of LED RGBW floodlighting luminaire for facade lighting with Die-cast aluminium housing,powder coated finish, of following wattage. Luminaire shall be capable of producing dynamic color changing light for with 16 million colors by DMX/Ethernet based control. The beam angle of the fittings shall be narrow, medium, wide or asymmetric as per the requirement. Luminaire shall be complete with driver and capable of operating at linevoltage without any separate power supply from 100-270VAC , 50Hz with powerfactor>0.9. Fixture shall be suitable to operate at anambient temperature range of-10°Cto+50°and shall be IP65 and IK06 rated. Lifetime shall be at least L70:50000 burning hours at 50°C . Luminaire shall be conforming to BIS(IS10322)and shall be complete with all necessary accessories required for proper working of fixture including weatherproof connection cables ,waterproof connectors etc. as required. 55 W | 16.00 | each |  | 38860.00 | 621760.00 | 40415.00 | 646640.00 | 621760.00 | PAVAN QUICK SERVICE
5.00 | Supply,Installation,Testing and Commissioning of LED RGBW floodlighting luminaire for facade lighting with Die-cast aluminium housing,powder coated finish, of following wattage. Luminaire shall be capable of producing dynamic color changing light for with 16 million colors by DMX/Ethernet based control. The beam angle of the fittings shall be narrow, medium, wide or asymmetric as per the requirement. Luminaire shall be complete with driver and capable of operating at linevoltage without any separate power supply from 100-270VAC , 50Hz with powerfactor>0.9. Fixture shall be suitable to operate at anambient temperature range of-10°Cto+50°and shall be IP65 and IK06 rated. Lifetime shall be at least L70:50000 burning hours at 50°C . Luminaire shall be conforming to BIS(IS10322)and shall be complete with all necessary accessories required for proper working of fixture including weatherproof connection cables ,waterproof connectors etc. as required. 90 W | 30.00 | each |  | 45629.00 | 1368870.00 | 47662.00 | 1429860.00 | 1368870.00 | PAVAN QUICK SERVICE
6.00 | SITC of high power Non-Integral IP68 flexible LED strip light sealed with anti-UV polyurethane. The power consumption shall be 55W per 5M role & 450Lm/meter. . The strip light shall be IK06. The strip light shall be supplied with all mounting clips, IP67 electrical connectors, 65W-70W non-integral power supply & DMX decoder per roll complete as required. | 17.00 | No's |  | 14499.00 | 246483.00 | 15287.00 | 259879.00 | 246483.00 | PAVAN QUICK SERVICE
7.00 | Supply Aluminium profile for flexible LED strip light for mounting on surface of rock/stone façade neatly with fasteners/ fixing arrengment etc complete as required. | 85.00 | r m |  | 590.00 | 50150.00 | 600.00 | 51000.00 | 50150.00 | PAVAN QUICK SERVICE
8.00 | SITC of Compact master Content Program Controller (DMX controller) with suitable size capability DMX512 universes,playback scenes and animations stored in its SD card, and it can be used for offline scenes scheduling, setting brightness, white balance and playback speed adjustments. It should be able to amplify the DMX signal in cascaded connection & support automatic playback scheduling. It should support power-on startup and scheduled timing start along with capability of unattended operation and remote scene triggering if needed. The Input voltage shall be 12VDC & shall have RJ45 port on Input side. The IEC classification shall be Class III. It should operate on DM512 protocol. The Content Program Controller shall have one SD card slot for maximum 32GB card & the SD card being used shall be FAT32 format. The Content Program Controller shall come with 220-240V to 12V DC power supply. The IP rating of content program controller shall be IP20 . The working temperature range shall be -10°C to 50°C complete as required. •Operating Temperature - 10 to 50 Centigrade • Minimum supported LED nodes up to 10000 • Network Data compatibility Ethernet protocol. • The software composer required to create light shows for DMX controller/DMX programming. • Connector/Cable: (2) RJ45 ports, shielded Cat. 6 or better data cable of required length to be included for comunication • Work as stand alone or computer driven controller. • Environment: Dry indoor location. •Ethernet keypad module for the DMX controller for selecting multible scene. •Ethernet Compact keypad that triggers the controller •Secure Digital SD card drive for flexible show •USB 2.0 interface for downloading shows and configuring from attached PC • All others items required for sucesssful functioning of DMXcontroller including the programming for all days through out the year as directed by EIC shall be considered and included in the quoted rate. | 1.00 | Job |  | 278013.00 | 278013.00 | 302900.00 | 302900.00 | 278013.00 | PAVAN QUICK SERVICE
9.00 | Design,Supply,installation,Testing and commissioning of splitter with input voltage range 190-240V AC, power consumption less than 15W made up of with CRCA sheet with powder coated, Ingress protection rating IP20. This unit takes DMX signal from DMX controller and split the signal in to 8 seperate output channels. The ouput terminals of splitters are optically isolated from the input.Splitters should be capable to amplify the DMX signal.Operating temperature shall be -10° to 50°C. | 1.00 | No's |  | 16250.00 | 16250.00 | 16900.00 | 16900.00 | 16250.00 | PAVAN QUICK SERVICE
10.00 | SITC of 2M long lead cable with IP67 5-Pin connector at one end. The Pin material should be copper. The cable shall have insulation resistance of ≥ 10Mꭥ complete as required. | 6.00 | No's |  | 1500.00 | 9000.00 | 1805.00 | 10830.00 | 9000.00 | PAVAN QUICK SERVICE
11.00 | SITC of 2M long jump cable with IP67 4-Pin connector at one end. The Pin material should be copper. The operating voltage shall be 60V DC. cable shall have insulation resistance of ≥ 10Mꭥ complete as required. | 10.00 | No's |  | 3500.00 | 35000.00 | 4250.00 | 42500.00 | 35000.00 | PAVAN QUICK SERVICE
12.00 | Supply and laying of DMX cable in existing conduit to make connection s with light controllers and amplifire as per the design complete as required. | 1000.00 | mtr |  | 173.00 | 173000.00 | 175.00 | 175000.00 | 173000.00 | PAVAN QUICK SERVICE
13.00 | Supply of the following 1100 volts grade, copper conductor FRLS PVC Insulated Sheathed Flexible Cable as per IS694 and latest amendment and as per other relevant standards and tender specification. 4C X 2.5 sqmm | 500.00 | mtr |  | 130.00 | 65000.00 | 135.00 | 67500.00 | 65000.00 | PAVAN QUICK SERVICE
14.00 | Supply of the following 1100 volts grade, copper conductor FRLS PVC Insulated Sheathed Flexible Cable as per IS694 and latest amendment and as per other relevant standards and tender specification. 4C X 4 sqmm | 500.00 | mtr |  | 187.00 | 93500.00 | 190.00 | 95000.00 | 93500.00 | PAVAN QUICK SERVICE
15.00 | Supply of following size of 1.1 KV grade, XLPE insulated PVC sheated Copper Conductor armoured cable confirming to IS: 7098 part -I amended upto date. 4 core X 4 Sq.mm | 1000.00 | Mtr |  | 312.00 | 312000.00 | 315.00 | 315000.00 | 312000.00 | PAVAN QUICK SERVICE
16.00 | Supply of following size of 1.1 KV grade, XLPE insulated PVC sheated Aluminium Conductor armoured cable confirming to IS: 7098 part -I amended upto date. 4 core X 25 Sq.mm | 1000.00 | Meter |  | 274.00 | 274000.00 | 275.00 | 275000.00 | 274000.00 | PAVAN QUICK SERVICE
17.00 | Supply of following size of 1.1 KV grade, XLPE insulated PVC sheated Aluminium Conductor armoured cable confirming to IS: 7098 part -I amended upto date. 3 core X 2.5 Sq.mm | 1000.00 | Meter |  | 150.00 | 150000.00 | 160.00 | 160000.00 | 150000.00 | PAVAN QUICK SERVICE
18.00 | Supply of following size of 1.1 KV grade, XLPE insulated PVC sheated Aluminium Conductor armoured cable confirming to IS: 7098 part -I amended upto date. 3 core X 1.5 Sq.mm | 1000.00 | Meter |  | 111.00 | 111000.00 | 115.00 | 115000.00 | 111000.00 | PAVAN QUICK SERVICE
19.00 | Supplying and fixing following 4way, Vertical type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder coating including earthing etc as required ( i/c the following MCB’s) a) 4 way (4 + 12), Double door | 1.00 | Job |  | 11200.00 | 11200.00 | 11500.00 | 11500.00 | 11200.00 | PAVAN QUICK SERVICE
20.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole - 10A | 10.00 | Each |  | 182.00 | 1820.00 | 185.00 | 1850.00 | 1820.00 | PAVAN QUICK SERVICE
21.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Double pole - 32 A | 2.00 | Each |  | 535.00 | 1070.00 | 550.00 | 1100.00 | 1070.00 | PAVAN QUICK SERVICE
22.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple pole and neutral - 63 A | 1.00 | Each |  | 1396.00 | 1396.00 | 1400.00 | 1400.00 | 1396.00 | PAVAN QUICK SERVICE
23.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 20 mm | 500.00 | mtr |  | 120.00 | 60000.00 | 125.00 | 62500.00 | 60000.00 | PAVAN QUICK SERVICE
24.00 | Laying of following sizes of FRLS PVC insulated copper conductor, cable in the existing surface/ recessed steel/ PVC conduit as required. 4C X 2.5 sqmm | 500.00 | Mtr |  | 72.00 | 36000.00 | 75.00 | 37500.00 | 36000.00 | PAVAN QUICK SERVICE
25.00 | Laying of following sizes of FRLS PVC insulated copper conductor, cable in the existing surface/ recessed steel/ PVC conduit as required. 4C X 4 sqmm | 500.00 | Mtr |  | 72.00 | 36000.00 | 75.00 | 37500.00 | 36000.00 | PAVAN QUICK SERVICE
26.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providng and fixing 2 nos. 3 pin 5/6 amps modular socket outlets and 2 nos 5/6 amps modular switches, connection etc. as required. | 6.00 | Each |  | 899.00 | 5394.00 | 900.00 | 5400.00 | 5394.00 | PAVAN QUICK SERVICE
27.00 | UPS SYSTEM Supply, installation, testing and commissioning of high performance IGBT inverter and IGBT rectifier based fully microprocessor controlled (three phase Input & three phase Output) online Transformerless UPS system suitable for input and output parameters as per specifications. The UPS shall be provided with external K13 rated copper wound Galvanic Isolation transformer at the complete output of the UPS i.e. after the static switch (As per IEC 1100 -2005). The UPS shall be provided in powder coated fan cooled enclosure painted in colour as per specifications. The UPS shall be suitable for normal, emergency, recharge, by-pass and maintenance mode. The system be expandable in such a manner that addition of another module of similar capacity can double the system output with common by-pass. The UPS shall have a microprocessor based display and control panel. UPS shall have own batteries with 30 minute battery back-up. Complete system must be provided as per specifications approved drawing and as per site requirement including inter connecting cables from battery to UPS, UPS to panel etc.& supports for complete system as required. 10 kVA on line 415 V AC UPS with 30 minutes balancing battery back up. | 1.00 | Set |  | 357610.00 | 357610.00 | 455000.00 | 455000.00 | 357610.00 | PAVAN QUICK SERVICE
28.00 | Design, fabrication, supply, installation, testing and commissioning of Flambeau/ Mashal traditional ornamental decorative highly suitable spectacular Cast Aluminium–Antique looking mixed with Victorian-urban classical culture Flambeau/ Mashal fixed on specified exiting concrete/stone decorated columns/foundation, as shown in the enclosed drawing/picture(in the tender document) as per dimensions and specification mentioned in the Technical specification of contract. The overall Antique Mashal size shall be 1300 to 1500 mm and thickness 10 mm to 12 mm. Handle made up of die-cast aluminum of sufficient strength and coated with four layer colours (layer – 1 Epoxy primer, layer – 2 Epoxy top coat, Layer – 3 Antique coat, Layer-4 Polyurethane Laquer) , the top flame structure to be made of good quality FRP material should be transulcent. LED decorative lighting(to resemble Flame-with combination of white,warm white,yellow colour and other suitable led/led strips) of wattage not exceeding 30W to meet the asthetic design. | 10.00 | Job |  | 46000.00 | 460000.00 | 46000.00 | 460000.00 | 460000.00 | PAVAN QUICK SERVICE, LAD AND ASSOCIATE
29.00 | Fabrication, Supply, Installation,Testing and commissioning Of SS(Satainless Steel) Letters Made Of Gold Anti-fingerprint Stainless Steel (approved Make) Grade 304 With 50mm Depth Raising Made Out Of Laser Cut Shape In Required Design, Language And Font Including Buffing, Polishing And Fixing by Sufficient Number Of Fasteners High Quality Chemical Tape/adhesive/fast Pf Approved Make All Complete As Per Architectural Drawing And Direction Of Engineer In‐Charge. A. Kolhapur Airport. B. कोल्हापुर हवाई अड्डा C. कोल्हापूर विमानतळ | 1.00 | Job |  | 564850.00 | 564850.00 | 565000.00 | 565000.00 | 564850.00 | PAVAN QUICK SERVICE
30.00 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works(For guarding of lights on cement concrete road.) | 500.00 | Kg |  | 143.00 | 71500.00 | 155.00 | 77500.00 | 71500.00 | PAVAN QUICK SERVICE
| Total in Figures |  |  |  |  | 7999999.00 |  | 8396043.00
Lowest Amount Quoted BY: PAVAN QUICK SERVICE(7999999.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of theme-based facia Illumination system at New Terminal building Tender ID: 2023_AAI_160693_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PAVAN QUICK SERVICE | 7999999.00 | L1
| 2 | LAD AND ASSOCIATE | 8396043.00 | L2