## BoQ1
Government eProcurement System Created By: VIVEK SHRIVASTAVA Created Date/Time: 19-Aug-2023 02:38 PM Tender Title: Design supply installation testing and commissioning of facade lighting at Jabalpur airport Jabalpur Madhya Pradesh Tender ID: 2023_AAI_161761_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Upgradation of Jabalpur Airport to make it suitable for the operation of AB-320 type of Aircraft. SH: Design, supply, installation, testing, and commissioning of facade lighting at Jabalpur airport, Jabalpur, Madhya Pradesh
Contract No: 2023_AAI_161761_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bajaj Electricals Limited(GSTN-27AAACB2484Q1Z8) |  | Instapower Ltd(GSTN-05AAACI9712L1ZG) |  | M R ELECTRICALS(GSTN-27AARPV8927A1Z5) |  | Bhasha Associate(GSTN-23ACXPC3844K2ZA) |  | Ascent Electrification Engineers(GSTN-24AAOFA2574R1ZU) |  | Variant Infratech Private Limited(GSTN-NA) |  | B L ENTERPRISES(GSTN-NA) |  | GAYATRI ELECTRICAL(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply,Installation ,testing & commissioning of minimum 75 Watt RGBW LED flood light with integral driver/external driver as per OEM design with minimum 3 KV internal surge protection and efficiency of 85% . System lumen output of RGBW LED flood light will not less than 3000 lumens & housing made of Die-cast aluminium alloy / extruded aluminium alloy for better heat decepitation and having IP 66 protection. The luminaire bracket shall be so designed that the luminaire can be tilted as per required angle. The luminaire should have beam angle in the range of 10-15 degree & the lens shall be made of anti-aging & anti-PMMA material. The optical fibre cover shall be minimum IK06 and made of clear tempered glass. The fixture shall come with power & DMX cable of required length (upto 1 Mtr). Fixture shall satisfacorily temperature range of -10°C to 50°C. The fixture shall be suitable to operate on voltage 240 VAC, 50Hz (±10 %). The luminaire shall have declared life of 50,000 burning hours at L70 . The luminaire shall be compatible with DMX512 controller . The luminaire shall be supplied with necessary IP67 connectors for connecting lead/jump cables as required. The agency have to submit BIS certificate, LM79 report from NABL accredited laboratory and LM80 report issued by LED manufacturer.The installation shall be done as per drawing (attached in tender document),site condition and as directed by EIC etc. complete as required. | 6.00 | Each |  | 18351.00 | 110106.00 | 30000.00 | 180000.00 | 28050.00 | 168300.00 | 104700.00 | 628200.00 | 44938.80 | 269632.80 | 24500.00 | 147000.00 | 32000.00 | 192000.00 | 32960.00 | 197760.00 | 110106.00 | Bajaj Electricals Limited
2.00 | Design, Supply,Installation ,testing & commissioning of minimum 48 Watt circular RGBW LED flood light with integral driver/external driver as OEM design with minimum 3 KV internal surge protection and efficiency of 85% . System lumen output of RGBW LED flood light will not less than 2000 lumens & housing made of Die-cast aluminium alloy / extruded aluminium alloy for better heat decepitation and having IP 66 protection. The luminaire bracket shall be so designed that the luminaire can be tilted as per required angle. The luminaire should have beam angle in the range of 10-35 degree as per site requirement design & the lens shall be made of anti-aging & anti-PMMA material. The optical fibre cover shall be minimum IK06 and made of clear tempered glass .The fixture shall come with power & DMX cable of required length (upto 1 Mtr). Fixture shall operating temperature range of -10°C to 50°C. The fixture shall be suitable to operate on voltage 240 VAC, 50Hz (±10 %). The luminaire shall have declared life of 50,000 burning hours at L70 . The luminaire shall be compatible with DMX 512 controller . The luminaire shall be supplied with necessary IP67 connectors for connecting lead/jump cables as required. The agency have to submit BIS certificate, LM79 report from NABL accredited laboratory and LM80 report issued by LED manufacturer.The installation shall be done as per drawing (attached in tender document),site condition and as directed by EIC etc. complete as required. | 104.00 | Each |  | 16140.00 | 1678560.00 | 20400.00 | 2121600.00 | 23550.00 | 2449200.00 | 65350.00 | 6796400.00 | 33447.60 | 3478550.40 | 14000.00 | 1456000.00 | 19500.00 | 2028000.00 | 19420.00 | 2019680.00 | 1456000.00 | Variant Infratech Private Limited
3.00 | Design, Supply,Installation,testing & commissioning of 1000mm (±100 mm) long RGBW Linear LED light with integral driver/external driver as OEM design with minimum 3 KV internal surge protection efficiency of 85% . System lumen output of RGBW LED flood light will not less than 3000 lumens & housing made of Die-cast aluminium alloy / extruded aluminium alloy for better heat decepitation and having IP 66 protection. The luminaire bracket shall be so designed that the luminaire can be tilted as per required angle. The luminaire should have multiple beam angle option in the range of 15 X 40 degree (±10 %) and to be used as per site/ design requirement . The fixture shall come with power & DMX cable of required length (upto 2 Mtr). Fixture shall operating temperature range of -10°C to 50°C. The fixture shall be suitable to operate on voltage 240 VAC, 50Hz (±10 %) . The luminaire shall have declared life of 50,000 burning hours at L70 . The luminaire shall be compatible with DMX 512 controller . The luminaire shall be supplied with necessary IP67 connectors for connecting lead/jump cables as required. The agency have to submit BIS certificate , LM79 report from NABL accredited laboratory and LM80 report issued by LED manufacturer. | 10.00 | Each |  | 18940.00 | 189400.00 | 37200.00 | 372000.00 | 42150.00 | 421500.00 | 104445.00 | 1044450.00 | 53557.20 | 535572.00 | 24500.00 | 245000.00 | 38500.00 | 385000.00 | 32730.00 | 327300.00 | 189400.00 | Bajaj Electricals Limited
4.00 | Design , Supply , Installation ,testing & commissioning of IP 68 flexible Minimum 10 watt/Meter LED strip light. The lumen output of minimum 400 lm/meter . The strip light beam angle in range of 110- 120 degree (±10 %). The luminaire shall have declared life of 30,000 burning hours at L70. The Fixture should be Dotless Homogenous Light source. The strip light shall be minimum IK 06.The fixture shall be suitable to operate on voltage 240 VAC, 50Hz (±10 %). The strip should be supplied with all mounting clips,suitable aluminium profile ,IP 67 connectors, DMX decoder per roll of 4 Mtr. - 5 Mtr. as per OEM design and other acessories as per site requirement.The agency have to submit BIS certificate , LM79 report from NABL accredited laboratory and LM80 report issued by LED manufacturer.The installation shall be done as per drawing (attached in tender document),site condition and as directed by EIC etc. complete as required.(Rate to be quoted for per meter quantity) | 1500.00 | Meter |  | 2638.00 | 3957000.00 | 3000.00 | 4500000.00 | 1980.00 | 2970000.00 | 3000.00 | 4500000.00 | 2257.20 | 3385800.00 | 2400.00 | 3600000.00 | 3150.00 | 4725000.00 | 3275.00 | 4912500.00 | 2970000.00 | M R ELECTRICALS
5.00 | Supply , Installation ,testing & commissioning of Compact master Content Program Controller (DMX controller) with capability to control minimum 8 DMX512 universes, playback scenes and animations stored in its SD card, and it can be used for offline scenes scheduling, setting brightness, white balance and playback speed adjustments. It should be able to amplify the DMX signal in cascaded connection & support automatic playback scheduling. It should support power-on startup and scheduled timing start along with capability of unattended operation and remote scene triggering if needed. The Content Program Controller shall have integrated/external LCD display & support IR remote control as per OEM design . The Content Program Controller (DMX controller) shall have one SD card slot for minimum 32GB card . The necessary power adopter as per OEM design is included along with Content Program Controller (DMX controller) to operate on 240 V (±10 %) ,50 HZ supply. The IP rating of content program controller (DMX controller) shall be minimum IP20 & shall comply to CE certifications. The Content program controller (DMX controller) shall be fully compatible and able to satisfactorly operate as per desired theme of façade lighting luminaires mentioned at item No. 1.00 to 4.00. The installation shall be done as site condition and as directed by EIC etc. complete as required. | 1.00 | Job |  | 260660.00 | 260660.00 | 150000.00 | 150000.00 | 513000.00 | 513000.00 | 312500.00 | 312500.00 | 193572.00 | 193572.00 | 135000.00 | 135000.00 | 130000.00 | 130000.00 | 313600.00 | 313600.00 | 130000.00 | B L ENTERPRISES
6.00 | Supply , Installation ,testing & commissioning of DMX Amplifier/splitter of 4-Pole DMX cable with IP67 connector input side & a cable for DC Input with IP67 2-Pole connector at output side and complying to DMX512 protocol. The Compact signal amplifier shall support magnetic isolation protection, protects the controllers and ensures that the DMX signal can be normally transmitted to various luminaires, improving the reliability and stability of the entire control system. The DMX controller shall be minimum IP66 rated. Amplifier shall support online automatic addressing & should be able to amplify the signal for up to 100 m or 64 DMX512 luminaires as per site requirement. The amplifier shall be housed in Aluminium casing/OEM recommended casing. The amplifier shall have factory fitter connecting wires with IP67 rated connectors. Supply of power pack for DMX amplifier with charger/adopter suitable to operate on 240 V (±10 %) ,50 Hz (if required) is included. The installation shall be done as site condition and as directed by EIC etc. complete as required. | 20.00 | Each |  | 60362.00 | 1207240.00 | 27600.00 | 552000.00 | 33750.00 | 675000.00 | 10000.00 | 200000.00 | 28044.00 | 560880.00 | 8400.00 | 168000.00 | 16000.00 | 320000.00 | 17220.00 | 344400.00 | 168000.00 | Variant Infratech Private Limited
7.00 | Supply and fixing of 2M long lead cable with IP67 4-Pin connector at one end. The fire rating of the cable shall be UL94-V0 or equivalent standard. The connector shall be made of PA66. The Pin material should be copper. The cable shall have insulation resistance of ≥ 10Mꭥ. | 30.00 | Each |  | 595.00 | 17850.00 | 5250.00 | 157500.00 | 4420.00 | 132600.00 | 11250.00 | 337500.00 | 3693.60 | 110808.00 | 700.00 | 21000.00 | 1000.00 | 30000.00 | 1025.00 | 30750.00 | 17850.00 | Bajaj Electricals Limited
8.00 | Supply and fixing of of 2M long jump cable with IP67 4-Pin connector at one end. The fire rating of the cable shall be UL94-V0 or equivalent standard. The connector shall be made of PA66. The Pin material should be copper. The cable shall have insulation resistance of ≥ 10Mꭥ. | 90.00 | Each |  | 595.00 | 53550.00 | 4500.00 | 405000.00 | 4485.00 | 403650.00 | 11325.00 | 1019250.00 | 3693.60 | 332424.00 | 700.00 | 63000.00 | 1000.00 | 90000.00 | 1025.00 | 92250.00 | 53550.00 | Bajaj Electricals Limited
9.00 | Supply,Installation.testing & Commissioning of Outdoor type External Lighting Feeder Pillar Panel conforming to IEC-439/IS 8623, made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 54 protection, double door, free standing, floor mounting, dust and vermin proof ,compartmentalized, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system . Panel should have continuous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary civil works e.g. PCC,Iron angle etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS: 63 A,4P, 10 kA,MCB Curve C -1 Nos. 32 Amp DP Power Contractor - 3 Nos. OUTGOINGS: 16Amp MCB Curve C -18 Nos. Auto Manual selector switch- 3Nos. ON/OFF push button-3 sets Timer - 3 Nos. Surge Protection Device - Type 1+2, 3 Pole + NPE, Imax = 50 kA, Modular Type, conforming to EN/IEC 61643-11 with 32A, FP C-Series MCB including complete connection with copper flexible cable - 1 Set 1 Lot of control wiring & 1 Set of designation plates. LED type RYB Indicating Lamps for incomer - 01 set | 2.00 | JOB |  | 119883.00 | 239766.00 | 150000.00 | 300000.00 | 64350.00 | 128700.00 | 55000.00 | 110000.00 | 150480.00 | 300960.00 | 165000.00 | 330000.00 | 105000.00 | 210000.00 | 200000.00 | 400000.00 | 110000.00 | Bhasha Associate
10.00 | Supply of 4 core 16 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS: 7098 (Part -I),1988 ammended upto date | 700.00 | Meter |  | 150.00 | 105000.00 | 225.00 | 157500.00 | 127.40 | 89180.00 | 140.00 | 98000.00 | 167.94 | 117558.00 | 160.00 | 112000.00 | 160.00 | 112000.00 | 170.00 | 119000.00 | 89180.00 | M R ELECTRICALS
11.00 | Supply of 3 core ,2.5 sq.mm of XPLE insulated PVC shealthed ,copper conductor armoured power cable of 1.1 KV grade conforming to IS: 7098 (Part -I),1988 ammended upto date | 1500.00 | Meter |  | 119.00 | 178500.00 | 195.00 | 292500.00 | 94.90 | 142350.00 | 125.00 | 187500.00 | 142.20 | 213300.00 | 85.00 | 127500.00 | 140.00 | 210000.00 | 145.00 | 217500.00 | 127500.00 | Variant Infratech Private Limited
12.00 | Supply and laying of catageory 6A 4 pair UTP cable in existing cable tray/existing GI pipe/existing raceway/ existing HDPE pipe /existing PVC pipe as required. | 1200.00 | Meter |  | 107.00 | 128400.00 | 150.00 | 180000.00 | 61.10 | 73320.00 | 65.00 | 78000.00 | 140.90 | 169080.00 | 30.00 | 36000.00 | 80.00 | 96000.00 | 100.00 | 120000.00 | 36000.00 | Variant Infratech Private Limited
13.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/recess/existing cable tray/existing GI pipe/existing raceway/ existing HDPE pipe /existing GI pipe/existing PVC pipe as required. upto 35 Sq mm. | 2200.00 | Meter |  | 27.00 | 59400.00 | 150.00 | 330000.00 | 58.50 | 128700.00 | 50.00 | 110000.00 | 43.78 | 96316.00 | 30.00 | 66000.00 | 50.00 | 110000.00 | 80.00 | 176000.00 | 59400.00 | Bajaj Electricals Limited
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade ae required. 4 X 16 sq. mm . | 8.00 | Each |  | 447.00 | 3576.00 | 525.00 | 4200.00 | 650.00 | 5200.00 | 250.00 | 2000.00 | 970.30 | 7762.40 | 500.00 | 4000.00 | 400.00 | 3200.00 | 800.00 | 6400.00 | 2000.00 | Bhasha Associate
15.00 | Supply and fixing of 25 mm dia medium class GI conduit along with aceessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | 1000.00 | Meter |  | 255.00 | 255000.00 | 157.50 | 157500.00 | 351.00 | 351000.00 | 130.00 | 130000.00 | 232.56 | 232560.00 | 750.00 | 750000.00 | 220.00 | 220000.00 | 120.00 | 120000.00 | 120000.00 | GAYATRI ELECTRICAL
16.00 | Supply and fixing of 32 mm dia medium class GI conduit along with aceessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | 500.00 | Meter |  | 368.00 | 184000.00 | 237.00 | 118500.00 | 422.50 | 211250.00 | 221.00 | 110500.00 | 294.12 | 147060.00 | 1100.00 | 550000.00 | 300.00 | 150000.00 | 150.00 | 75000.00 | 75000.00 | GAYATRI ELECTRICAL
17.00 | Supply , Installation testing & commissioning of minimum IP 65 polycarbonate junction box with 16 Amp connector terminal suitable for terminating cables. | 20.00 | Each |  | 2534.00 | 50680.00 | 29250.00 | 585000.00 | 1950.00 | 39000.00 | 10000.00 | 200000.00 | 4377.60 | 87552.00 | 1100.00 | 22000.00 | 2000.00 | 40000.00 | 2500.00 | 50000.00 | 22000.00 | Variant Infratech Private Limited
18.00 | Supply ,Installation,testing & commissioning of advance maintenance free Chemical Gel Earthing of Dual Pipe Technology (GI) of 3mtr longh 50mm dia of outer shell (MS) with the 25mm dia inner shell (MS) of 80-100 microns galvanized earth electrode filled with highly conducting metallic compunds with the permanent sealing at both the ends with the lead terminal of 32X10mm size at the top along with 50 Kgs of Chemical mixture of Resistance Lowering Grounding Minerals. The loss on ignition by mass of the chemical compund shall be less than 20%. The Chemical compund should be tested and certified by any International accredited and BIS( Bureau of Indian Standards) accredited laboratory. The earth electrode shall be dully tested & certifed by CPRI (Central Power Research Institute), Govt. of India. The chemical earth electrode manufacturers should be an ISO 9001:2008 & ISO 14001: 2004 certified organization. The Earth pit should be covered with heavy duty polyplastic weather proof chamber etc. as required & approved by the Engineer in Charge. | 4.00 | Set |  | 10644.00 | 42576.00 | 40500.00 | 162000.00 | 6370.00 | 25480.00 | 15000.00 | 60000.00 | 17100.00 | 68400.00 | 9500.00 | 38000.00 | 30000.00 | 120000.00 | 20000.00 | 80000.00 | 25480.00 | M R ELECTRICALS
19.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface / recess/ existing HDPE Pipe/existing GI Pipe for connections etc. as required. | 200.00 | Meter |  | 194.00 | 38800.00 | 135.00 | 27000.00 | 156.00 | 31200.00 | 165.00 | 33000.00 | 228.46 | 45692.00 | 450.00 | 90000.00 | 200.00 | 40000.00 | 150.00 | 30000.00 | 27000.00 | Instapower Ltd
20.00 | Supplying & laying of PE80, PN6, 63 mm dia HDPE pipe ISI marked as per IS: 4984/2016 with latest amendment up to date along with all necessary accessories like coupler and other required accessories etc. direct in ground (750mm below ground level) including excavation and refilling the trench complete as required. | 250.00 | Meter |  | 355.00 | 88750.00 | 420.00 | 105000.00 | 132.60 | 33150.00 | 200.00 | 50000.00 | 485.64 | 121410.00 | 80.00 | 20000.00 | 250.00 | 62500.00 | 400.00 | 100000.00 | 20000.00 | Variant Infratech Private Limited
| Total in Figures |  |  |  |  | 8848814.00 |  | 10857300.00 |  | 8991780.00 |  | 16007300.00 |  | 10474889.60 |  | 7980500.00 |  | 9273700.00 |  | 9732140.00
Lowest Amount Quoted BY: Variant Infratech Private Limited(7980500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Design supply installation testing and commissioning of facade lighting at Jabalpur airport Jabalpur Madhya Pradesh Tender ID: 2023_AAI_161761_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Variant Infratech Private Limited | 7980500.00 | L1
| 2 | Bajaj Electricals Limited | 8848814.00 | L2
| 3 | M R ELECTRICALS | 8991780.00 | L3
| 4 | B L ENTERPRISES | 9273700.00 | L4
| 5 | GAYATRI ELECTRICAL | 9732140.00 | L5
| 6 | Ascent Electrification Engineers | 10474889.60 | L6
| 7 | Instapower Ltd | 10857300.00 | L7
| 8 | Bhasha Associate | 16007300.00 | L8