## BoQ1
Government eProcurement System Created By: Mayank Gaur Created Date/Time: 15-Sep-2023 03:57 PM Tender Title: Provision of dynamic lighting system for illumination of ATC tower at DATS Complex, IGI Airport, New Delhi Tender ID: 2023_AAI_163329_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg.-E), AAI, DATS Complex, IGI Airport, New Delhi.
Name of Work: Provision of dynamic lighting system for illumination of ATC tower at DATS Complex, IGI Airport.
Contract No: AAI/DATS/E-E/Dynamic lighting/2023-24/ENIT-02
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bajaj Electricals Limited(GSTN-27AAACB2484Q1Z8) |  | SACHDEVA ELECTRICALS(GSTN-07AALPS3645Q1ZU) |  | B L ENTERPRISES(GSTN-NA) |  | Variant Infratech Private Limited(GSTN-NA) |  | Surya Roshni Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SUB HEAD-I Supply of DYNAMIC LIGHT FIXTURE- Large Projector Light, Not less than 400 W, LED, RGBW, IP 66 The housing in light weight, made of high strength die cast aluminium and coated by static powder making it weather resistant.The luminaire shape and dimension shall be as per the site requirement after approval by the EIC . Screen protection in tempered glass with high impact resistance (=˃IK08). High precision dial ensures precision angle adjustment. Fixture shall be suitable to operate at ambient temperature range of -10°C to +50°C. Pure Polyester powder coating in Standard Colour.Precise structure and multi-protection silicon rubber seal guarantees the fixture ≥IP65 rated. Power LED Module with high efficacy LED's on Printed Circuit Board with metal core plate.The LEDs shall have minimum CRI=˃80 & SDCM<=4. Electronic Power Supply for LED module, which offers protection against Short Circuit, over-voltage & over- current, with-in-built surge protection. Light fixture should be standard DMX512 protocol compatible, the DMX decoder function should be inbuilt in the light fixture, Each light fixture should be individually addressable & should be able to operate with standard DMX512 equipment. The luminaire shall be capable of producing dynamic colour changing light with 16 million colours as light fixture shall be programmable using required bit control DMX protocol/Ethernet based control. The luminaries shall be with Anti-aging and anti-UV high optical efficiency and lens shall be UL/VDE/ PMMA lens of approved PC for each LED and clear tempered glass for better illumination and beam angle should not more than 9˚ ,as per site requirement . Luminaire should have IP67 rated male/female connectors for DMX512 through wiring . Anti-glare accessory to be provided to restrict glare.Estimated Lifetime should be at least 50,000 burning hours at L70 at 50 degree centigrade . LM80 report from LED Manufacturer should be submitted. BIS safety test report as per IS10322 from Intertek/UL lab or any other BIS certified Lab & BIS Certificate with manufacturer name same as brand proposed should be submitted. Minimum Light Fixture Lumen output is 14000Lumens@ full power.Necessary cage arrangements are to be made for the safety of the LIGHT FIXTURE as per the site requirement | 40.00 | Nos. | 4618716.00 | 61187.00 | 2447480.00 | 93184.00 | 3727360.00 | 72000.00 | 2880000.00 | 132775.00 | 5311000.00 | 55680.00 | 2227200.00 | 2227200.00 | Surya Roshni Limited
2.00 | Supply of DYNAMIC LIGHT FIXTURE- Linear Wall Washer, Not less than 60W, LED, RGBW, (DMX 512 Compatible), IP 66 The housing in light weight, made of high strength aluminium and coated by static powder making it weather resistant.The luminaire shape and dimension shall be as per the site requirement after approval by the EIC. Protection screen in ultra white tempered glass with high impact resistance (≥IK 06). High precision dial ensures precision angle adjustable as per site requirement . Pure Polyster powder coating in Standard Colour, Precise structure and multi-protection silicon rubber seal guarantees the fixture ≥IP65 rated. Power LED module with high efficacy LED's, on Printed Circuit Board with metal core plate. Electronic Power Supply for LED Module, which offers Protection against Short Circuit, Over-Voltage & Over-Current, with in-built surge protection . Light fixture should be standard DMX512 protocol compatible, The DMX decoder function should be inbuilt in the light fixture, Each light fixture should be individually addressable & should be able to operate with any standard DMX512 equipment.The luminaire shall be capable of producing dynamic colour changing light with 16 million colours as light fixture shall be programmable using required bit control DMX protocol/Ethernet based control Lens made of PC. Estimated Lifetime should be at least 50,000 burning hours at L70 at 50 degree centigrade. LM80 report from LED Manufacturer should be submitted. BIS safety test report as per IS10322 from Intertek/UL lab or any other BIS certified Lab & BIS Certificate with manufacturer name same as brand proposed should be submitted. Minimum Light Fixture Lumen output is 1500lumens at full power. | 165.00 | Nos. | 5858.00 | 17952.00 | 2962080.00 | 35268.00 | 5819220.00 | 22500.00 | 3712500.00 | 21500.00 | 3547500.00 | 15140.00 | 2498100.00 | 2498100.00 | Surya Roshni Limited
3.00 | Installation testing and commissioning of Light fixtures (including all the accessories) mentioned in BOQ item no. 1 & 2 | 205.00 | Nos. | 7404.00 | 3224.00 | 660920.00 | 678.00 | 138990.00 | 500.00 | 102500.00 | 2340.00 | 479700.00 | 2475.00 | 507375.00 | 102500.00 | B L ENTERPRISES
4.00 | Supply of Universe (512 Channels) DMX controller & Xlor Connectors, with following features & specifications: Designed for DIN rail mounting, Delivered with 512 DMX channels. It's Key Features includes. DMX Stand ALone controller . Up to 1x DMX512 universes (512 channels). RDM compatible. USB & Ethernet connectivity for programming/ control. Stand alone made with 99 scenes. Play scenes in 5 areas/ zones/ microSD slot. 8+3 dry contact trigger ports. Test scenes rotary switch. Window/ Mac software to set dynamic colours/ effects. LS cloud compatiblity (optional). Technical Data Input Power 12v DC (8-15V range), Output Protocol DMX512 (x1), Programmablity PC, Mac, Android, iOS, Connecting-USB-C Etherent Screw terminals for 1 DMX/ RDM Universes, 8+3 Contact ports, 12v power-in Battery holder (CR2032), microSD slot Memory SD card, Environment IP 20 0˚C to +50˚C, Buttons Rotary switch, OS Requirements Mac OS x 10.8-10.14 Window 7/8/10 Standards CE, ETL, Low voltage, EMC, and RoHS. DMX Controller Make-Nicolaudie/Pharos/Madrix/Enttec/chromateq | 1.00 | Nos. | 4545.00 | 126509.00 | 126509.00 | 99000.00 | 99000.00 | 140000.00 | 140000.00 | 215527.00 | 215527.00 | 60000.00 | 60000.00 | 60000.00 | Surya Roshni Limited
5.00 | Supply of 6-port DMX Splitter (Din Rail Mountable) with following features & specifications: DMX signal splitter enables branching in complex DMX installtions. The individual outputs are galvanically isolated from input and between each other. The output signals are appropriately reinforces, which guarantees correct operation of the entire installation. DMX Splitter is manufactured in a housing adapted for mounting on standard DIN 35mm rails. Specification- Power Supply- DC12-24V, DMX Channels-512, Nos. of DMX inout-1 & output-6, Optical Isolation of DMX Lines, Built-in Terminator, breakdown voltage of the isolation > 1000V, current consumption-<500mA, Weight-0.2 Kgs., W-105mm, H-86mm & D-60mm or dimension as per standard similar model of Manufacturer of Light Fixture. DMX Splitter Make- PXM/ Swisson/ Sundrax/ Pharos/ Enttec | 2.00 | Nos. | 3131.00 | 77930.00 | 155860.00 | 39000.00 | 78000.00 | 27500.00 | 55000.00 | 10410.00 | 20820.00 | 7150.00 | 14300.00 | 14300.00 | Surya Roshni Limited
6.00 | Installation, Programming & Commissioning of DMX controller and splitter mentioned in BOQ item no. 4 & 5. | 1.00 | Job | 100000.00 | 69820.00 | 69820.00 | 88888.00 | 88888.00 | 150000.00 | 150000.00 | 123158.00 | 123158.00 | 450000.00 | 450000.00 | 69820.00 | Bajaj Electricals Limited
7.00 | Supply, Installation, Testing and Commissioning of DMX cable with the following specs .cable should be true DMX512 construction flexible and easy to use , rugged black matte PVC jacket ,corroision resistant tinned copper braid , meets or exceeds DMX standards ,24 AWG 4conductors stranded bare copper ,duofoil tape etc.as suitable for the site condition . DMX Cable Make- Belden/ Van Damme/ Sommer | 1000.00 | Mtr. | 89.00 | 209.00 | 209000.00 | 125.00 | 125000.00 | 150.00 | 150000.00 | 289.00 | 289000.00 | 115.00 | 115000.00 | 115000.00 | Surya Roshni Limited
8.00 | SUB HEAD-II Supply of 3Cx 2.5 sqmm armoured Copper conductor cable, XLPE Insulated, cores laid up, PVC tape/PVC Extruded Innersheathed for Multicore Cables, 1.1 kV grade as per IS 7098 (Part 1) 1988 | 830.00 | Mtr. | 137.00 | 173.00 | 143590.00 | 136.00 | 112880.00 | 150.00 | 124500.00 | 120.00 | 99600.00 | 120.00 | 99600.00 | 99600.00 | Surya Roshni Limited, Variant Infratech Private Limited
9.00 | Supply and laying of 3Cx 2.5 sqmm flexible Copper conductor cable, PVC insulated & FR PVC Round sheathed, 1.1 kV grade confirming to IS 694 in the existing PVC/steel /HDPE pipe as required. | 400.00 | Mtr. | 287.00 | 186.00 | 74400.00 | 98.00 | 39200.00 | 120.00 | 48000.00 | 120.00 | 48000.00 | 250.00 | 100000.00 | 39200.00 | SACHDEVA ELECTRICALS
10.00 | SUB HEAD-II Supply of 4C x 16 sqmm solid/stranded Aluminium armoured conductor cable, XLPE Insulated, cores laid up, PVC tape/PVC Extruded Innersheathed for Multicore Cables, 1.1 kV grade as per IS 7098 (Part 1) 1988. | 150.00 | Mtr. | 132.00 | 207.00 | 31050.00 | 153.00 | 22950.00 | 145.00 | 21750.00 | 200.00 | 30000.00 | 130.00 | 19500.00 | 19500.00 | Surya Roshni Limited
11.00 | SUB HEAD-III Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 50.00 | Mtr. | 297.00 | 364.00 | 18200.00 | 180.00 | 9000.00 | 130.00 | 6500.00 | 50.00 | 2500.00 | 265.00 | 13250.00 | 2500.00 | Variant Infratech Private Limited
12.00 | SUB HEAD-III Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sqmm | 880.00 | Mtr. | 1385.00 | 81.00 | 71280.00 | 12.00 | 10560.00 | 50.00 | 44000.00 | 45.00 | 39600.00 | 120.00 | 105600.00 | 10560.00 | SACHDEVA ELECTRICALS
13.00 | SUB HEAD-III Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. (Clamped with 1 mm thick saddle) Upto 35 sqmm | 50.00 | Mtr. | 1385.00 | 107.00 | 5350.00 | 60.00 | 3000.00 | 80.00 | 4000.00 | 280.00 | 14000.00 | 120.00 | 6000.00 | 3000.00 | SACHDEVA ELECTRICALS
14.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on existing cable tray as required. (Clamped with 1 mm thick saddle) Upto 35 sqmm | 50.00 | Mtr. | 918.00 | 107.00 | 5350.00 | 45.00 | 2250.00 | 60.00 | 3000.00 | 285.00 | 14250.00 | 120.00 | 6000.00 | 2250.00 | SACHDEVA ELECTRICALS
15.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 297.00 | 32225.00 | 64450.00 | 16600.00 | 33200.00 | 20000.00 | 40000.00 | 6435.00 | 12870.00 | 7920.00 | 15840.00 | 12870.00 | Variant Infratech Private Limited
16.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. Pipe (including pipe) from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 15.00 | Mtr. | 222.20 | 412.00 | 6180.00 | 1734.00 | 26010.00 | 300.00 | 4500.00 | 1120.00 | 16800.00 | 200.00 | 3000.00 | 3000.00 | Surya Roshni Limited
17.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 300.00 | Mtr. | 429.25 | 52.00 | 15600.00 | 21.00 | 6300.00 | 40.00 | 12000.00 | 20.00 | 6000.00 | 58.00 | 17400.00 | 6000.00 | Variant Infratech Private Limited
18.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required​.
18.10 | 25 mm | 400.00 | Mtr. | 505.00 | 448.00 | 179200.00 | 145.00 | 58000.00 | 210.00 | 84000.00 | 410.00 | 164000.00 | 158.00 | 63200.00 | 58000.00 | SACHDEVA ELECTRICALS
19.00 | Supplying and fixing 25 mm dia MS flexible pipe with PVC coating along with all ancillaries and accessories like couplers etc. as required. | 300.00 | Mtr. | 404.00 | 358.00 | 107400.00 | 140.00 | 42000.00 | 175.00 | 52500.00 | 180.00 | 54000.00 | 94.00 | 28200.00 | 28200.00 | Surya Roshni Limited
20.00 | Supplying and fixing following way , horizontal type three pole and neutral ,sheet steel ,MCB distribution board ,415V , on surface /recess, complete with tinned copper bus bar ,neutral bus bar ,earth bar ,din bar , interconnections ,power painted including earth etc. as required .(but without MCB/RCCB/Isolator) 4 Way (4 +12), Double door | 2.00 | Nos. | 404.00 | 53605.00 | 107210.00 | 5500.00 | 11000.00 | 9000.00 | 18000.00 | 8200.00 | 16400.00 | 33870.00 | 67740.00 | 11000.00 | SACHDEVA ELECTRICALS
21.00 | Supply and fixing of 5 Ato 32 Amp rating ,240/415V ,10KA ,c cureve miniature circuit breaker suitable for inductive load of following poles in the exixting MCB DB complete with connections, teting and commisioning etc. as required .
21.10 | Single pole | 24.00 | Nos. | 5050.00 | 448.00 | 10752.00 | 170.00 | 4080.00 | 150.00 | 3600.00 | 290.00 | 6960.00 | 4495.00 | 107880.00 | 3600.00 | B L ENTERPRISES
22.00 | TPN (32 A) | 2.00 | Nos. | 3030.00 | 1164.00 | 2328.00 | 2600.00 | 5200.00 | 1250.00 | 2500.00 | 1755.00 | 3510.00 | 2695.00 | 5390.00 | 2328.00 | Bajaj Electricals Limited
| Total in Figures |  |  |  |  | 7474009.00 |  | 10462088.00 |  | 7658850.00 |  | 10515195.00 |  | 6530575.00
Lowest Amount Quoted BY: Surya Roshni Limited(6530575.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of dynamic lighting system for illumination of ATC tower at DATS Complex, IGI Airport, New Delhi Tender ID: 2023_AAI_163329_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Surya Roshni Limited | 6530575.00 | L1
| 2 | Bajaj Electricals Limited | 7474009.00 | L2
| 3 | B L ENTERPRISES | 7658850.00 | L3
| 4 | SACHDEVA ELECTRICALS | 10462088.00 | L4
| 5 | Variant Infratech Private Limited | 10515195.00 | L5