## BoQ1
Government eProcurement System Created By: RAJITH V Created Date/Time: 13-Sep-2023 05:03 PM Tender Title: Providing new VCB HT panel in place of old OCB HT panel including HT cable laying and provisional ring main unit for NPH yard t o OPH yard at Madurai Airport. Tender ID: 2023_AAI_163330_1
Tender Inviting Authority: Airports Authority of India, Madurai Airport, Madurai -625 022.
Name of Work: Providing new VCB HT panel in place of old OCB HT panel including HT cable laying and provisional ringmain unit for NPH yard to OPH yard at Madurai Airport.
Contract No: 2023_AAI_163330_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Balaji Engineering(GSTN-33ADGPV2628A1ZV) |  | J.K ENGINEERING ASSOCIATES(GSTN-NA) |  | paoweretch engineers(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of outdoor type (IP 55 or better from CRCA Sheet of 3mm thick for frame work & covers) floor mounted metal clad, (11 KV) Switch Board VCB panel with 7 Nos. VCBs, totally enclosed & fully interlocked, truck mounting, horizontal draw out, horizontal isolation type vacuum breaker as per IS / IEC 62271-100 (2007) for breakers & IEC 62271-200 (2003), for panels / IS3247 as amended up to date, having capacities as mentioned below, free standing extensible on both sides, single break, trip free mechanism, motorised charged and auto/ manually closing breaker suitable for use on 11 KV, 3 Phase, 50Hz A.C. supply with short circuit fault level of 500 MVA, complete with self contained short time current 26.3 kA for 3 sec, Internal Arc Test for AFLR 26.3 kA for 1 sec at individual compartments i.e busbar, VCB and cable compartment, rack in and rack out mechanism, air insulated but encapsulated copper bus bars capacity meeting fault level current, inbuilt DC power pack, breaker featured with mechanical ON / OFF indicator with hand trip device, Breaker control TNC switch and all accessories such as shunt trip coil and auxiliary switch of 4NO+4NC, motorised and manually operated spring assisted closing mechanism, emergency trip push button, interconnections, space heaters, earthing, etc. and equipped with following switchgears and accessories, connections suitable for cable upto 3C X 300 sqmm XLPE cable of 11 KV grade (cable entry from bottom), separate earthing switch shall be provided for cable earthing. The earthing truck shall be so designed that it is impossible to earth a live. cable terminations suitable for 3C x 300sq.mm. XLPE 11 KV cable etc. as per site requirement. | 1.00 | Job |  | 5168999.00 | 5168999.00 | 4438400.00 | 4438400.00 | 4345000.00 | 4345000.00 | 4000000.00 | 4000000.00 | 4627500.00 | 4627500.00 | 3877000.00 | 3877000.00 | 3877000.00 | paoweretch engineers
1.10 | Incomer 1 No. consisting of following; 1 No. of 800 Amp , 11 KV, 3 Ph, 3POLE VCB 1 No - Multifunction Meter with accuracy class 0.5 LED display of I ,V, Hz, Active, Reactive, Apparent Power & Energy, Power factor, %THD , Maximum demand load, (complying with IEC61557-12) with RS 485 & Ethernet port and protection MCB and required accessories to complete the system 3 No. Cast resin drawout type PTs 11 KV / √3 / 110 √3, class 0.5,100 VA burden including HT HRC fuse on 11 KV Side and MCBs on secondary side protction. 1 No. Voltmeter (0-15KV) digital type, selector switch for voltmeter and protection fuses/MCB for HT metering up to 12KV on incomer. 1No. Ammeter (0-300 A) dual scale ammeter, digital type, selector switches for ammeter. 3 No. Cast resin insulated Dual core 3 CTs 300/150/ 5-5A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. Aux. relays for Anti Pumping & indication. Trip Circuit supervision relay Master Trip Circuit Relay 1 No. Micro processor based over current, short circuit 51/50 & earth fault numerical IDMT relay with having dual redundancy port for IEC 61850 ring topology, RS 485 modbus communication facility consisting 3 element for over current relay and one earth fault capable of storing minimum last 10 trip history. 3 No. Arc flash protection sensors with minimum 3 meters length compatible with the proposed feeder protection relay for VCB, Busbar & cable compartments. 1 No. Over & under voltage protection relay 1 No. Over & under frequency relay 1 No. Alarm annunciator with minimum 8 windows and buzzer, ACK, rest, test push button for transformer faults and electrical faults in respective window. Busbar 800 Amps TP, 12 KV Copper Bus bar with encapsulated insulation sleeves with cast epoxy support insulator to withstand full short circuit currents upto 26.3 kA for 3 second.
1.20 | Outgoings 6 Nos. each consisting of following; 6 Nos. 800 Amp, 11 KV VCB horizontal draw out type VCB with motorized spring charge mechanism, T/N/C switch and required safety switchgears complete Aux. relays for Anti Pumping & indication. Trip Circuit supervision relay '- Master Trip Circuit Relay 1 No. Micro processor based over current, short circuit 51/50 & earth fault numerical IDMT relay having dual port IEC 61850, RS 485 modbus communication facility consisting 3 element for over current relay and one earth fault capable of storing minimum last 10 trip history. 1 No - Multifunction Meter with accuracy class 0.5 LED display of I ,V, Hz, Active, Reactive , Apparent Power & Energy, Power factor, %THD , Maximum demand load, (complying with IEC61557-12) with RS 485 & Ethernet port and protection MCB and required accessories to complete the system. 3 No. Arc flash protection sensors with minimum 3 meters length compatible with the proposed feeder protection relay for VCB, Busbar & cable compartments. 3 No. Cast resin insulated Dual core 3 CTs 100/50/5-5A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. 1 No. Alarm annunciator with minimum 8 windows and buzzer, ACK, rest, test push button for transformer faults and electrical faults in respective window. Busbar 800 Amps TP, 12 KV Copper Bus bar with encapsulated insulation sleeves with cast epoxy support insulator to withstand full short circuit currents upto 26.3 kA for 3 second All I/C & O/G Breaker have following Accessories & indication 6A MCB 6A MCB for spring charge DC Control Supply healthy & fails Surge Arrestor of type 1, 11KV grade shall be provided for all phases of each incomer AC Supply control ON/OFF Switch Circuit breaker failure Alarm indication VCB spring charge indication LED Illumination lamp ON / OFF with limit Switch T-N-C (Trip, Neutral, Close) breaker control switch with indication arrangement. All control wiring with protection & test terminal block as required. Emergency trip push button 2A MCB for lamp 60 watts space heater with thermostat 16 Amp MCB for space heater and plug point 6/16 Amps 5 Pin with piano type switch socket outlet
2.00 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for for 3 core X 120 Sq.mm, XLPE aluminium conductor cable of 11 KV grade as required | 1.00 | Job |  | 16999.00 | 16999.00 | 8550.00 | 8550.00 | 14500.00 | 14500.00 | 10000.00 | 10000.00 | 9800.00 | 9800.00 | 11000.00 | 11000.00 | 8550.00 | vk sam engineering
3.00 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 300 Sq.mm, XLPE aluminium conductor cable of 11 KV grade as required | 1.00 | Job |  | 19999.00 | 19999.00 | 9975.00 | 9975.00 | 16000.00 | 16000.00 | 15000.00 | 15000.00 | 13800.00 | 13800.00 | 12500.00 | 12500.00 | 9975.00 | vk sam engineering
4.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 19999.00 | 79996.00 | 19950.00 | 79800.00 | 14500.00 | 58000.00 | 15000.00 | 60000.00 | 15800.00 | 63200.00 | 26500.00 | 106000.00 | 58000.00 | Awasthi Electric Works
5.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including thermite weld connection/ terminating with nut, bolt, spring, washer etc. as required. | 70.00 | Mtr |  | 999.00 | 69930.00 | 1520.00 | 106400.00 | 1200.00 | 84000.00 | 1000.00 | 70000.00 | 1600.00 | 112000.00 | 727.00 | 50890.00 | 50890.00 | paoweretch engineers
6.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr |  | 1499.00 | 29980.00 | 1853.00 | 37060.00 | 1550.00 | 31000.00 | 1500.00 | 30000.00 | 2100.00 | 42000.00 | 2011.00 | 40220.00 | 29980.00 | CHENNAI ENGINEERING SERVICES
7.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and walll suspension bracket and MS angle complete as required & as per specifications. | 2.00 | Job |  | 9999.00 | 19998.00 | 5700.00 | 11400.00 | 10500.00 | 21000.00 | 5000.00 | 10000.00 | 7600.00 | 15200.00 | 5682.00 | 11364.00 | 10000.00 | Balaji Engineering
8.00 | Supply, installation, testing and commissioning of 6kg ABC (Powder Type) Fire Extinguisher, Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and MS angle complete and conforming to IS:15683 as required and as per specifications. | 2.00 | Job |  | 3999.00 | 7998.00 | 2375.00 | 4750.00 | 5000.00 | 10000.00 | 5000.00 | 10000.00 | 3800.00 | 7600.00 | 1838.00 | 3676.00 | 3676.00 | paoweretch engineers
9.00 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint ‘FIRE’ and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. | 2.00 | Set |  | 3499.00 | 6998.00 | 2613.00 | 5226.00 | 5000.00 | 10000.00 | 5000.00 | 10000.00 | 4500.00 | 9000.00 | 2382.00 | 4764.00 | 4764.00 | paoweretch engineers
10.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class C, 2.5 mm thick or better suitable for 11KV AC grade and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ± 20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-In-Charge. | 20.00 | Sqm |  | 1499.00 | 29980.00 | 1520.00 | 30400.00 | 1500.00 | 30000.00 | 2500.00 | 50000.00 | 1800.00 | 36000.00 | 3309.00 | 66180.00 | 29980.00 | CHENNAI ENGINEERING SERVICES
11.00 | Supply of 4C X 25 Sq.mm XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade as per IS 7098 part I 1988 with upto date amendments etc complete as required. | 350.00 | Mtr |  | 209.00 | 73150.00 | 162.00 | 56700.00 | 152.00 | 53200.00 | 250.00 | 87500.00 | 172.00 | 60200.00 | 171.00 | 59850.00 | 53200.00 | Awasthi Electric Works
12.00 | Supply of 3C X 10 Sq.mm XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade as per IS 7098 part I 1988 with upto date amendments etc complete as required. | 75.00 | Mtr |  | 119.00 | 8925.00 | 144.00 | 10800.00 | 98.00 | 7350.00 | 250.00 | 18750.00 | 105.00 | 7875.00 | 103.00 | 7725.00 | 7350.00 | Awasthi Electric Works
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing HDPE/DWC/HUME METAL pipe as required. Upto 35 sq. mm | 380.00 | Mtr |  | 29.00 | 11020.00 | 38.00 | 14440.00 | 40.00 | 15200.00 | 35.00 | 13300.00 | 32.00 | 12160.00 | 200.00 | 76000.00 | 11020.00 | CHENNAI ENGINEERING SERVICES
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4C X 25 sq.mm | 2.00 | Job |  | 799.00 | 1598.00 | 238.00 | 476.00 | 300.00 | 600.00 | 300.00 | 600.00 | 450.00 | 900.00 | 1000.00 | 2000.00 | 476.00 | vk sam engineering
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3C X 10 sq.mm | 1.00 | Job |  | 599.00 | 599.00 | 190.00 | 190.00 | 250.00 | 250.00 | 350.00 | 350.00 | 300.00 | 300.00 | 824.00 | 824.00 | 190.00 | vk sam engineering
16.00 | Supplying and making end termination with aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3C X 10 sq.mm | 5.00 | Job |  | 599.00 | 2995.00 | 190.00 | 950.00 | 150.00 | 750.00 | 350.00 | 1750.00 | 160.00 | 800.00 | 21.00 | 105.00 | 105.00 | paoweretch engineers
17.00 | Supply of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205, Part 24 complete with fitting and cutting, jointing etc. complete as required. 50 mm dia (outer dia) | 750.00 | Mtr |  | 39.00 | 29250.00 | 48.00 | 36000.00 | 90.00 | 67500.00 | 100.00 | 75000.00 | 60.00 | 45000.00 | 60.00 | 45000.00 | 29250.00 | CHENNAI ENGINEERING SERVICES
18.00 | Laying of 50mm dia DWC pipe direct in ground (75 cm below ground level) in all types of soil including excavation and refilling the trench but excluding sand cushioning and protective covering etc. Complete as required | 720.00 | Mtr |  | 99.00 | 71280.00 | 133.00 | 95760.00 | 90.00 | 64800.00 | 100.00 | 72000.00 | 185.00 | 133200.00 | 500.00 | 360000.00 | 64800.00 | Awasthi Electric Works
19.00 | Supply of 6 core multi mode armoured Optical Fibre Cable 50/125 μm, OM4 multi mode 6 core armoured gel filled with multi loose tube (LSZH) to meet the relavant IS standard etc. as required. | 350.00 | Mtr |  | 39.00 | 13650.00 | 120.00 | 42000.00 | 90.00 | 31500.00 | 150.00 | 52500.00 | 48.00 | 16800.00 | 222.00 | 77700.00 | 13650.00 | CHENNAI ENGINEERING SERVICES
20.00 | Laying of OFC cable in the existing Cable tray/Hume/DWC HDPE/GI Pipe/MS Conduit/PVC conduit/PVC casing capping etc. as required. | 340.00 | Mtr |  | 59.00 | 20060.00 | 34.00 | 11560.00 | 25.00 | 8500.00 | 25.00 | 8500.00 | 20.00 | 6800.00 | 60.00 | 20400.00 | 6800.00 | J.K ENGINEERING ASSOCIATES
21.00 | Supply, installation and testing of 19" rack mountable LIU fully loaded with SC type splicing tray, pigtails and other accessories a) LIU with 6 nos. of SC interface per LIU etc. as required. | 2.00 | Job |  | 14999.00 | 29998.00 | 10925.00 | 21850.00 | 16500.00 | 33000.00 | 75000.00 | 150000.00 | 5800.00 | 11600.00 | 13115.00 | 26230.00 | 11600.00 | J.K ENGINEERING ASSOCIATES
22.00 | Supply, installation and testing of multi mode SC to SC type Duplex patch cords of 3 mtr length compatible with patch panel as per pigtail type etc. as required. | 7.00 | Job |  | 399.00 | 2793.00 | 1443.00 | 10101.00 | 900.00 | 6300.00 | 500.00 | 3500.00 | 630.00 | 4410.00 | 2204.00 | 15428.00 | 2793.00 | CHENNAI ENGINEERING SERVICES
23.00 | Supply, installation and testing of OFC to E-thernet media convertor with required power supply etc. as required. | 2.00 | Job |  | 6999.00 | 13998.00 | 4275.00 | 8550.00 | 6000.00 | 12000.00 | 15000.00 | 30000.00 | 9500.00 | 19000.00 | 8405.00 | 16810.00 | 8550.00 | vk sam engineering
24.00 | Supply Installation and testing of 19" rack mountable 16 port Gigabit managed access E-thernet switch with 04 SFP ports and V-LAN support etc. as required. | 1.00 | Job |  | 32999.00 | 32999.00 | 18050.00 | 18050.00 | 42000.00 | 42000.00 | 15000.00 | 15000.00 | 58000.00 | 58000.00 | 33005.00 | 33005.00 | 15000.00 | Balaji Engineering
25.00 | Supply and laying of CAT 6 or superior UTP cable with all termination crimping etc. as required. | 15.00 | Mtr |  | 59.00 | 885.00 | 714.00 | 10710.00 | 70.00 | 1050.00 | 100.00 | 1500.00 | 48.00 | 720.00 | 67.00 | 1005.00 | 720.00 | J.K ENGINEERING ASSOCIATES
26.00 | OFC splicing for termination to LIU units etc. as required. | 2.00 | Job |  | 2999.00 | 5998.00 | 2375.00 | 4750.00 | 4000.00 | 8000.00 | 20000.00 | 40000.00 | 2000.00 | 4000.00 | 2606.00 | 5212.00 | 4000.00 | J.K ENGINEERING ASSOCIATES
27.00 | Supply, Installation, Testing and Commissioning of 24 window alarm annunciator with serial communication feature, settings facility by DIP switches and jumpers, the annunciator shall have communication equipments like RS485/RS232 Modbus port, RTU-Slave protocol and communication facility to other Annunciators and devices such as DCS, SCADA, PLC, computer, printer etc. complete as required. The annunciator shall have the following features; 1) Two Operation Modes (Stand-alone and Serial) 2) Fully field configurable (Manually or by software) 3) Supports 4 built-in and 4 external pushbuttons: Acknowledge, Reset, Test, and Mute Item includes annunciator programming for 24 No.s VCB status signals from remote bays. | 1.00 | Job |  | 24999.00 | 24999.00 | 16150.00 | 16150.00 | 22000.00 | 22000.00 | 65000.00 | 65000.00 | 50000.00 | 50000.00 | 40100.00 | 40100.00 | 16150.00 | vk sam engineering
28.00 | Design, Fabrication, Assembling, Supply, Installation, Testing and Commissioning of MV panel outdoor Cubical type with rain canopy, Floor mounted, free standing, dust & vermin proof conforming to IEC 61439 suitable for 415V, 3Ph, 4 wire, 50Hz supply system fabricated in compartmentalized design of Form 3 B and Ingress protection of IP 54 from CRCA sheet of 3mm thick for frame work and covers and 3mm thick for gland plates i/c cleaning and finishing complete as per OEM process for powder coating in approved shade, extendable type, 100A TPN aluminium busbars of high conductivity, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mmx50mmx 5mm thick, entire panel shall have common GI earth Bar having minimum size of 25mm x 3mm at the rear with 2 Nos of earth studs, provision for cable entry from bottom of the panel, front access shall be available to all components in Panel which require adjustment, maintenance or replacement and each compartment should be provided with door and pad locking arrangement including supply and installation of all items as below, including providing foundation and as per technical specification with all accessories. Incomer: i). One No. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection, ON/OFF/TRIP Indication Lamps, phase spreaders to connect 25 sqmm cable as required. ii) R,Y ,B Phase Indication LED lamps for each phase with 3 Nos of 2A ,MCBS & Breaker Indication Lamps (ON/OFF/TRIP) with 2A control MCBs -1 Sets. Outgoing: i) Three Nos. of 16 A, 10 KA, 4P MCB ii) 6 Nos. of 10 A, 10 KA, SP MCB iii) 10A 4Pole contactor along with analog timer - 2 set. suitable wiring shall be provided. One set of 100A Al. bus bars with at par neutral bus bar as required. All accessories such as fuses, auxiliary contactors, auxiliary switches, etc. including providing Empty Cubicle Space (2 No.) suitable for 16A 4P MCB as required. | 1.00 | Job |  | 64999.00 | 64999.00 | 156750.00 | 156750.00 | 55000.00 | 55000.00 | 125000.00 | 125000.00 | 84000.00 | 84000.00 | 117402.00 | 117402.00 | 55000.00 | Awasthi Electric Works
29.00 | Rerouting of exisiting 11KV cable from existing gantry substation to proposed switching VCB panels including taking out existing 11KV cable, excavating new trench of 1200mm depth, supply and laying of 100mm dia DWC HDPE pipe and re-laying the existing cable and new cable to the VCB panel (For rerouting no extra cost will be paid) etc. complete as per site requirement and E-I-C instructions. | 130.00 | Mtr |  | 1999.00 | 259870.00 | 855.00 | 111150.00 | 800.00 | 104000.00 | 250.00 | 32500.00 | 750.00 | 97500.00 | 750.00 | 97500.00 | 32500.00 | Balaji Engineering
30.00 | Supply of 6mtr GI OCTAGONAL continuously tapered (Bottom and Top dia of the pole not less than 130mm & 70mm respectively) Street Light Pole including Double Arm bracket not less than 700 mm length and 60 mm dia suitable for Wind Velocity as per IS 875, fabricated out of 3mm thick High Tensile Steel Sheet /Plate in single section with rigid flange plate (250x250x12mm Thick min.) welded with the base of pole for fixing on foundation bolts for installation on a precast foundation including supply of 4 Nos. of foundation bolt (M24x750mm) and providing weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5mm thick backalite sheet with stud type connector and DP MCB 6A, provision for earthing etc., complete as reqired. | 5.00 | Each |  | 11999.00 | 59995.00 | 13870.00 | 69350.00 | 12000.00 | 60000.00 | 10000.00 | 50000.00 | 11500.00 | 57500.00 | 13475.00 | 67375.00 | 50000.00 | Balaji Engineering
31.00 | SITC of 45W LED roadway luminaire with high power LED as Light source, inbuilt driver with aluminium/suitable alloy housing etc. as per tender specification for the proposed NDB approach road etc. as required. | 10.00 | Job |  | 3999.00 | 39990.00 | 2898.00 | 28980.00 | 1590.00 | 15900.00 | 4000.00 | 40000.00 | 3220.00 | 32200.00 | 2106.00 | 21060.00 | 15900.00 | Awasthi Electric Works
32.00 | Supply of 3C X 120 Sq.mm XLPE insulated PVC sheathed aluminium conductor armoured power cable of 11 KV grade, Unearthed conforming to IS: 7098 (Part-II) amended upto date. | 100.00 | Mtr |  | 2659.00 | 265900.00 | 1207.00 | 120700.00 | 1290.00 | 129000.00 | 1500.00 | 150000.00 | 1000.00 | 100000.00 | 551.00 | 55100.00 | 55100.00 | paoweretch engineers
33.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 Core, XLPE aluminium conductor cable of 11 KV grade as required. 3C X 120 Sq.mm | 2.00 | Job |  | 39999.00 | 79998.00 | 15675.00 | 31350.00 | 28000.00 | 56000.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 17500.00 | 35000.00 | 20000.00 | Balaji Engineering
34.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 Core, XLPE aluminium conductor cable of 11 KV grade as required. 3C X 300 Sq.mm | 2.00 | Job |  | 44999.00 | 89998.00 | 16150.00 | 32300.00 | 32000.00 | 64000.00 | 15000.00 | 30000.00 | 15500.00 | 31000.00 | 25000.00 | 50000.00 | 30000.00 | Balaji Engineering
35.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe with charcoal/ coke and salt etc. as required. | 2.00 | Set |  | 10999.00 | 21998.00 | 7125.00 | 14250.00 | 7500.00 | 15000.00 | 7500.00 | 15000.00 | 7300.00 | 14600.00 | 17764.00 | 35528.00 | 14250.00 | vk sam engineering
36.00 | Providing, laying 6 SWG dia G.I. Wire in ground in existing trench (75 cm deep) and re-filling etc. complete as required. | 400.00 | Mtr |  | 39.00 | 15600.00 | 114.00 | 45600.00 | 30.00 | 12000.00 | 30.00 | 12000.00 | 45.00 | 18000.00 | 26.00 | 10400.00 | 10400.00 | paoweretch engineers
37.00 | Providing Concrete foundation platform for installing 11KV outdoor VCB panel as supplied in item number 1, including providing concrete M25 grade design Mix foundation of nominal dimension (9000X6000 mm) with depth of 900 mm (600 mm above ground level & 300 mm Below ground level), 100mm base concrete with 1:3:6 PCC, RCC rafting with 10 mm steel rod with spacing 150 mm in foundation, suitable size covered cable trench/pipes for entry of 11KV cables, control cables in rear/front side side of Panel in the concrete platform etc. as required. Necessary steps as required to be provided in the platform for accessing the panel. Supply and fixing of fencing all around the pedestal made out of 40x40x6 MM MS angle with 6mm size 25 X 25mm welded mesh, with Gate of size 1200(W) x 1800(H) mm. Proper supports shall be provided with MS Flats wherever necessary to prevent the welded mesh from warping. The 75x 40 mm. channel vertical support for the gate shall be fixed into the ground with PCC with 2.5 Mtr. height, 40 mm MS fabricated Poles around the yard with suitable size of MS angles, MS Channels, MS flats, fixing wire mesh, fencing, concrete foundation with spacing not less than 2 mtrs span between poles. MS Poles and the wire mesh shall be painted with approved color as per E.I.C Direction. The length of the fencing should cover all sides of the foundation with sufficient clearance from sides of the pedestal, complete etc. as per site requirement. | 1.00 | Job |  | 699999.00 | 699999.00 | 997500.00 | 997500.00 | 675000.00 | 675000.00 | 30000.00 | 30000.00 | 480000.00 | 480000.00 | 300000.00 | 300000.00 | 30000.00 | Balaji Engineering
38.00 | Installation, testing & commissioning of 6 Mtr. Height Octagonal Street Light Pole with all accessories in RCC foundation with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) foundation of size 50x50x150 cm (120 cm below the ground and 30 cm above the ground) (or as per OEM's Standard which ever is better) including excavation and refilling, positioning of template and foundation bolts (supplied with pole to match with pole base plate) and providing and fixing of PE 63, PN 6, HDPE pipe of size 50 mm dia (2 pieces of each minimum 0.75 Mtr length) in the foundation for loop-in loop-out of the cable, numbering the pole etc. complete as required. | 5.00 | Job |  | 6999.00 | 34995.00 | 5700.00 | 28500.00 | 3500.00 | 17500.00 | 4000.00 | 20000.00 | 6000.00 | 30000.00 | 7000.00 | 35000.00 | 17500.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 7428416.00 |  | 6727428.00 |  | 6196900.00 |  | 5424750.00 |  | 6336665.00 |  | 5795353.00
Lowest Amount Quoted BY: Balaji Engineering(5424750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing new VCB HT panel in place of old OCB HT panel including HT cable laying and provisional ring main unit for NPH yard t o OPH yard at Madurai Airport. Tender ID: 2023_AAI_163330_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering | 5424750.00 | L1
| 2 | paoweretch engineers | 5795353.00 | L2
| 3 | Awasthi Electric Works | 6196900.00 | L3
| 4 | J.K ENGINEERING ASSOCIATES | 6336665.00 | L4
| 5 | vk sam engineering | 6727428.00 | L5
| 6 | CHENNAI ENGINEERING SERVICES | 7428416.00 | L6