## BoQ1
Government eProcurement System Created By: MUNSHAM SREEDHAR BABU Created Date/Time: 29-Sep-2023 12:08 PM Tender Title: Construction of New Terminal Building and associated work at Leh Airport. SH Installation Testing and Commissioning of On Grid Solar Photo Voltaic Power plant System Tender ID: 2023_AAI_165280_1
Tender Inviting Authority: Senior Manager (E-E), Project Office, AAI, Leh Airport.
Name of Work: Construction of New Terminal Building & associated work at Leh Airport. SH : Installation, Testing & Commissioning of On-Grid Solar Photo-Voltaic Power Plant System
Contract No: Tender Reference Number : AAI/ENGGE/LEH/NTB/2023-24/02 Tender Id: 2023_AAI_165280_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NEWSOL PV POWER PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I Installation, Testing & Commissioning of Solar PV System
2.00 | Design,Shifting, Installation, Testing and Commissioning of provided Monocrystalline Solar PV Modules of Jakson make, Brand -Helia, Model JH-550M, having power rating 550 Wp (Qty.= 1152 Nos. approx.) as specified in Technical data sheet, required to be transported from Gwalior Airport to Leh Airport i/c necessary packing as required, loading, unloading duly mounted on Flushed Type Terminal Building Roof top (made up of Standing seam Double skin Insulated Roofing over MS Structure) of New Terminal Building with suitable mounting structure & the same shall be designed & installed by suitable size solar clamp and anodized aluminium channels alongwith the suitable size fasteners to maintain proper ventillation of the arrays of modules, holding of module with metallic roof sheet groove and solar module tightly without drilling / puncturing the metallic roof sheet i/c carrying out shadow analysis and shall capable to withstand the wind speed up to 150KMPH with anti-corrosion feature considering altitude of 3515m above MSL, ambient temperature Max. 40°C; Min. -30°C including levelling, connecting Modules with not less than Single Core 4sqmm, 1500V PV Copper Wire to form a Array-String, providing and fixing of suitable size IP 65 DC outdoor type Junction box (JB) for connecting the module output with the provision for Isolation, String Monitoring and Control for each String including suitable mounting arrangement for JB, providing and laying of DC Cabling not less than Single Core 6 Sq.mm (1.5 KV) Copper Cable of suitable runs from the JB to Inverter subject to voltage drop shall not exceed 2%, in 50 mm dia heavy duty UPVC Pipe including SS clamping which shall be laid on covered GI perforated cable tray of suitable size as required, Termination of Cables with glands and lugs, Earthing of Modules and Structures throughout with 25 X 5 MM GI Strip, Marking of DC Cable Routes etc. as required. | 1.00 | Job |  | 5200000.00 | 5200000.00 | 5200000.00 | NEWSOL PV POWER PRIVATE LIMITED
3.00 | Design,Shifting, Installation, Testing and Commissioning of Total Capacity of 500 KW (AC) Power Conditioning Unit/Inverter Grid Connected Photovoltaic with duly provided Outdoor Type IP 66 String Inverter of each Capacity 125 KW (AC) having Make- Growatt, Model- MAX125KTL3-XLV (Qty.-04 Nos.) i/c transportation of said inverters from Gwalior Airport to Leh Airport i/c necessary packing as required, loading, unloading etc followed with mounting arrangement, connection, interconnections, earthing, termination of DC cables with necessary glands and lugs into Inverters etc. complete all as required as specified. | 1.00 | Job |  | 600000.00 | 600000.00 | 600000.00 | NEWSOL PV POWER PRIVATE LIMITED
4.00 | Design, Supply, Installation, Testing and Commissioning of a Solar Radiation and Environment/Weather Monitoring System (WMS) to monitor and communicate the Parameters Like Global Horizontal Irradiance – Pyranometer, Collector Plane Irradiance – Pyranometer, Ambient Temperature, Module Temperature, Wind Speed and Direction, Relative Humidity Rain Fall/Precipitation including providing and fixing of requisite Instruments/Sensors/Computer Hardware and licence free Software etc. complete all as required. Note:- Scope of Communication through OFC cable has been considered in seperate BOQ item. | 1.00 | Job |  | 500000.00 | 500000.00 | 500000.00 | NEWSOL PV POWER PRIVATE LIMITED
5.00 | Design, Supply, Installation, Testing and Commissioning of SCADA System for SPV PP for Local and Remote Web Based Monitoring to Monitor / Communicate and Control as applicable for Environment Monitoring System/PV Modules/String Monitoring Unit/Inverter/DC-AC Switch Gears/LT Panels for Electrical Parameters and Weather Parameters including providing and fixing of requisite Computer Hardware and Software etc.complete all as required and as specified. Note1:- The SCADA System consist of two PC Systems with one Desktop at Server installed in BMS room of Utility building and one Desktop shall be provided in the AAI Electrical room of Terminal building for remote performance monitoring of the System. Note2:- Scope of Communication through OFC cable has been considered in seperate BOQ item | 1.00 | Job |  | 350000.00 | 350000.00 | 350000.00 | NEWSOL PV POWER PRIVATE LIMITED
6.00 | Provision of DG Sets & Solar PV power Plant control systems by developing logic in such a way that whenever the Grid supply fails and DG sets are put in operation, the controller will ramp down the solar power generation by controlling the Inverters to avoid DG hunting etc including laying of suitable size controlling and communication cables, fixing of tower lamp Annunciation buzzer in Power house, Electrical control room etc. complete all as required and as specified. Note1:- Atleast Two nos. of controller panel are required to be provide. One in Terminal building and one in Utility building. Note2 :- The Quote for this item covers the scope of providing and laying of controlling and communication cables. | 1.00 | Job |  | 400000.00 | 400000.00 | 400000.00 | NEWSOL PV POWER PRIVATE LIMITED
7.00 | SITC of 5 KVA UPS along with suitably designed VRLA Battery having minimum back up time of 1 Hour with MS Racks for SCADA System including providing and fixing Copper Wiring (with suitable size Cable) for Input and Output Cabling, termination etc., as required. | 1.00 | Job |  | 200000.00 | 200000.00 | 200000.00 | NEWSOL PV POWER PRIVATE LIMITED
8.00 | SH-IISITC OF LT COMBINATION PANEL
9.00 | Fabrication, Supply, Installation, Testing and Commissioning of 3 phase, 415V TPN, 50Hz, AC System, draw out Cubicle type, Single front, free standing floor mounted, Totally enclosed, top cable entry, metal enclosed switchboards (LT AC Combination Panel) suitable for operation at indoor site conditions (min. temp. -5 degree celsius, design temp. +40 degree celsius, storage temp. of -22 degree celsius, altitude of 3515 m above m.s.l.) made out of 2mm Thick CRCA Sheet Steel for Outer Shell and 1.6 mm Thick CRCA Sheet for Inner Partition complete with all accessories, interconnection, CTs, PTs, connection, earthing, powder coated, provision of bottom base channel and locking arrangements etc.,as per approved drawings, specifications complete all as required and comprising of the following:
10.00 | 1 Set of 415V, 1600 A, Al. Bus-bars, 50 KA for 1 Sec switch board with following feeders.
11.00 | A) Six Nos. (04 nos Working + 02 Nos. Spare) of 320 A, 50 KA, 4P MCCB (Ics=100%Icu) with Microprcessor based Releases for OC/SC/EF Protection and ROM as INCOMER (w r t Solar from Individual Inverter) with Resin Cast C.T. operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication Lamps and Phase Indication Lamps,All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
12.00 | B) One No. of 1250 A, 50 KA, 4P , MDO , ACB with Microprcessor based Releases for OC/SC/EF Protection and ROM as OUTGOING (w r t Grid), with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required.
13.00 | Total LT Panel mentioned above | 1.00 | Job |  | 2000000.00 | 2000000.00 | 2000000.00 | NEWSOL PV POWER PRIVATE LIMITED
14.00 | SH-III CABLING WORKS
15.00 | Supply of XLPE insulated and PVC sheathed Aluminium Conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required: a) 3.5 X 300 SQ MM | 550.00 | Mtr |  | 1500.00 | 825000.00 | 825000.00 | NEWSOL PV POWER PRIVATE LIMITED
16.00 | Supply of XLPE insulated and PVC sheathed Copper Conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required: a) 3.5 X 95 SQ MM | 100.00 | Mtr |  | 1200.00 | 120000.00 | 120000.00 | NEWSOL PV POWER PRIVATE LIMITED
17.00 | Laying and Fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) on the existing cable tray as required. | 1000.00 | Mtr |  | 1500.00 | 1500000.00 | 1500000.00 | NEWSOL PV POWER PRIVATE LIMITED
18.00 | Laying and Fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 35 sq. mm and upto 95 sq. mm (clamped with 40x3mm MS flat clamp) on the existing cable tray as required. | 100.00 | Mtr |  | 1000.00 | 100000.00 | 100000.00 | NEWSOL PV POWER PRIVATE LIMITED
19.00 | Supplying and making indoor end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 300 SQ MM | 8.00 | Nos |  | 1500.00 | 12000.00 | 12000.00 | NEWSOL PV POWER PRIVATE LIMITED
20.00 | Supplying and making indoor end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 95 SQ MM | 8.00 | Nos |  | 1500.00 | 12000.00 | 12000.00 | NEWSOL PV POWER PRIVATE LIMITED
21.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required a) 3.5 X 300 SQ MM | 4.00 | Nos |  | 20000.00 | 80000.00 | 80000.00 | NEWSOL PV POWER PRIVATE LIMITED
22.00 | Supply of 06 F OFC of Single Mode, armoured, multi tube, double sheath, suitable for outdoor application conforming to ITU-T-G652 & IEC60973 & 60794 with up-to date amendments as required. | 1000.00 | Mtr |  | 500.00 | 500000.00 | 500000.00 | NEWSOL PV POWER PRIVATE LIMITED
23.00 | Supply of Permanently Lubricated HDPE Pipe of 40 mm Outer dia and 33 mm inner dia made of PE 100 Material and suitable for Pressure PN 6 as required on the existing cable tray as required. | 700.00 | Mtr |  | 1000.00 | 700000.00 | 700000.00 | NEWSOL PV POWER PRIVATE LIMITED
24.00 | Supply and making of splicing and termination of 06 F OFC in Terminal box including providing all accessories and Specialised Manpower complete as reqired. | 10.00 | Job |  | 800.00 | 8000.00 | 8000.00 | NEWSOL PV POWER PRIVATE LIMITED
25.00 | Laying [by Pulling/Blowing] of OFC of up to 24F with PLB-HDPE Pipe, Sealing of Pipes etc., as required on the existing cable tray as required. | 700.00 | RM |  | 800.00 | 560000.00 | 560000.00 | NEWSOL PV POWER PRIVATE LIMITED
26.00 | SH-IV EARTHING WORKS
27.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Nos |  | 20000.00 | 80000.00 | 80000.00 | NEWSOL PV POWER PRIVATE LIMITED
28.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required.-(Module Strucure Continuous Earthing is not covered ) | 150.00 | Mtr |  | 700.00 | 105000.00 | 105000.00 | NEWSOL PV POWER PRIVATE LIMITED
29.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required.-(Module Strucure Continuous Earthing is not covered ) | 200.00 | Mtr |  | 700.00 | 140000.00 | 140000.00 | NEWSOL PV POWER PRIVATE LIMITED
30.00 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/recessed conduit/submain wiring/cable as required.(Module Strucure Continuous Earthing is not covered). | 250.00 | Mtr |  | 700.00 | 175000.00 | 175000.00 | NEWSOL PV POWER PRIVATE LIMITED
31.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/coke and salt as required. | 4.00 | Nos |  | 650.00 | 2600.00 | 2600.00 | NEWSOL PV POWER PRIVATE LIMITED
32.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required-(Module Strucure Continuous Earthing is not covered). | 150.00 | Mtr |  | 500.00 | 75000.00 | 75000.00 | NEWSOL PV POWER PRIVATE LIMITED
33.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required-(Module Strucure Continuous Earthing is not covered). | 350.00 | Mtr |  | 500.00 | 175000.00 | 175000.00 | NEWSOL PV POWER PRIVATE LIMITED
34.00 | SH-V LIGHTING CONDUCTOR & FIRE PROTECTION ITEMS
35.00 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, GI tube, having single prong at top, with 85 mm dia 6 mm thick GI base plate including holes etc. complete as required. | 6.00 | Job |  | 15000.00 | 90000.00 | 90000.00 | NEWSOL PV POWER PRIVATE LIMITED
36.00 | Providing and laying G.I. tape 32 mm X 6 mm from finial on surface as required. | 200.00 | Mtr |  | 300.00 | 60000.00 | 60000.00 | NEWSOL PV POWER PRIVATE LIMITED
37.00 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode (Finial) directly in ground as required. | 20.00 | Mtr |  | 300.00 | 6000.00 | 6000.00 | NEWSOL PV POWER PRIVATE LIMITED
38.00 | Providing & fixing of Carbon-dioxide (CO2) Type fire extinguishers conforming to IS 2878-1976 and cylinder fully charged of 4.5 Kg capacity as required. | 5.00 | Job |  | 5000.00 | 25000.00 | 25000.00 | NEWSOL PV POWER PRIVATE LIMITED
39.00 | Supply and fixing of foam type fire extinguishers [Portable Type of 9 Litre Capacity] as required | 5.00 | Job |  | 5000.00 | 25000.00 | 25000.00 | NEWSOL PV POWER PRIVATE LIMITED
40.00 | Supply and fixing of foam type fire extinguishers [Portable Type of 9 Litre Capacity] as required | 2.00 | Nos |  | 5000.00 | 10000.00 | 10000.00 | NEWSOL PV POWER PRIVATE LIMITED
41.00 | Supply and fixing of Safety Instruction Chart (in words) duly framed with 5mm thick glass complete as required. | 3.00 | Job |  | 5000.00 | 15000.00 | 15000.00 | NEWSOL PV POWER PRIVATE LIMITED
42.00 | Providing & fixing a set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour and written with white paint 'Fire' and mounted on MS angle iron frame with bracket of appropriate size and capacity including filling sand complete as required. | 1.00 | Job |  | 5000.00 | 5000.00 | 5000.00 | NEWSOL PV POWER PRIVATE LIMITED
43.00 | SH-VI APPROVALS
44.00 | Preparation of Drawings, necessary data i/c Liasoning Work for getting Approval and obtaining sanction for energization of Solar PV system and associated Electrical System from Central Electricity Authority/EB/Any other Nodal Agency of Central/State Government as required. | 1.00 | Job |  | 250000.00 | 250000.00 | 250000.00 | NEWSOL PV POWER PRIVATE LIMITED
45.00 | Carrying out of Glare Analysis and Reflection Analysis for Airport Operation with respect to positioning of PV Modules, Submission of Reports, Assisting AAI in getting NOC/Clearance from AAI NOC Wing/DGCA/Other Statutories Bodies related to Safety, Recommendation for suitable installation Procedure for Safe Operation of Aircrafts etc., as required. | 1.00 | Job |  | 150000.00 | 150000.00 | 150000.00 | NEWSOL PV POWER PRIVATE LIMITED
46.00 | SH-VII PART B. OPERATION & ALL INCLUSIVE COMPREHENSIVE ANNUAL MAINTENANCE CONTRACT (AICAMC)
47.00 | Operation & All Inclusive Comprehensive ANNUAL Maintenance Contract of Grid Connected 500 KW (AC) at Roof Top of New Terminal Building at Leh Airport as per the SCC & as specified.
48.00 | Operation of 500KW AC solar PV plant during one year DLP- First year | 1.00 | Year |  | 700000.00 | 644840.00 | 644840.00 | NEWSOL PV POWER PRIVATE LIMITED
49.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Second year | 1.00 | Year |  | 750000.00 | 636525.00 | 636525.00 | NEWSOL PV POWER PRIVATE LIMITED
50.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Third year | 1.00 | Year |  | 800000.00 | 625440.00 | 625440.00 | NEWSOL PV POWER PRIVATE LIMITED
51.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS- Fourth year | 1.00 | Year |  | 850000.00 | 612170.00 | 612170.00 | NEWSOL PV POWER PRIVATE LIMITED
52.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Fifth year | 1.00 | Year |  | 900000.00 | 597150.00 | 597150.00 | NEWSOL PV POWER PRIVATE LIMITED
53.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Sixth year | 1.00 | Year |  | 950000.00 | 580735.00 | 580735.00 | NEWSOL PV POWER PRIVATE LIMITED
54.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Seventh year | 1.00 | Year |  | 1000000.00 | 563100.00 | 563100.00 | NEWSOL PV POWER PRIVATE LIMITED
55.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS- Eighth year | 1.00 | Year |  | 1050000.00 | 544740.00 | 544740.00 | NEWSOL PV POWER PRIVATE LIMITED
56.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS- Ninth year | 1.00 | Year |  | 1100000.00 | 525690.00 | 525690.00 | NEWSOL PV POWER PRIVATE LIMITED
57.00 | Operation & CMC of 500KWAC Solar Module + 4X125KVA Inverter + SCADA system + WMS - Tenth year | 1.00 | Year |  | 1150000.00 | 506345.00 | 506345.00 | NEWSOL PV POWER PRIVATE LIMITED
| Total in Figures |  |  |  |  | 20892335.00
Lowest Amount Quoted BY: NEWSOL PV POWER PRIVATE LIMITED(20892335.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Terminal Building and associated work at Leh Airport. SH Installation Testing and Commissioning of On Grid Solar Photo Voltaic Power plant System Tender ID: 2023_AAI_165280_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NEWSOL PV POWER PRIVATE LIMITED | 20892335.00 | L1