## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 11-Oct-2023 02:41 PM Tender Title: Provision of perimeter lighting and associated works at SGRDJ International Airport, Amritsar. Tender ID: 2023_AAI_166207_1
Tender Inviting Authority: <Asstt. GM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Provision of perimeter lighting and associated works at SGRDJ International Airport, Amritsar.>
Tender ID: <2023_AAI_ 166207 _1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Instapower Ltd(GSTN-05AAACI9712L1ZG) |  | Power And Instrumentation Guj Ltd(GSTN-24AACCP4292Q1ZW) |  | surbhi association(GSTN-23AGKPD2522N1ZK) |  | ANU ENGINEERING CORPORATION(GSTN-03AJDPK9181G1Z9) |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA) |  | Mankha Electrotech Pvt Ltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and erection of Hot Dip Galvanized octagonal pole of 3 mm thickness 4 Mtr. Long with top dia 70 mm and bottom dia 135 mm with base plate of size 200X200X12 mm, including cost of foundation accessories, nuts and bolts etc. The foundation bolts ( "J" type or as per manufacturer design) should be hot dipped galvanized, Terminal plate consisting of 2 nos. 100 A, 4 pole natural links including connection etc. with suitable connecting arrangement for 2 nos. MCBs and door locking arrangement including RCC 1:2:4 foundation (of size as per OEM Design) for fixing the pole with all labour & material required to complete the job in all respect upto the entire satisfaction of Engineer - In - Charge
1.10 | Single Arm Bracket | 45.00 | Nos. |  | 7395.00 | 332775.00 | 11300.00 | 508500.00 | 11000.00 | 495000.00 | 11500.00 | 517500.00 | 7000.00 | 315000.00 | 16680.00 | 750600.00 | 315000.00 | JCC ENGINEERS PRIVATE LIMITED
1.20 | Double arm Bracket | 5.00 | Nos. |  | 9425.00 | 47125.00 | 11700.00 | 58500.00 | 11500.00 | 57500.00 | 12000.00 | 60000.00 | 8011.00 | 40055.00 | 17640.00 | 88200.00 | 40055.00 | JCC ENGINEERS PRIVATE LIMITED
2.00 | Supply and fixing of galvanized pipe (45 degree bend suitable for street light) dia upto 50 mm and 1.5M long including accessories (Like Clamps, Bolts etc.) to mount on existing wall complete as required. | 10.00 | Nos. |  | 2900.00 | 29000.00 | 2300.00 | 23000.00 | 1000.00 | 10000.00 | 1500.00 | 15000.00 | 1500.00 | 15000.00 | 828.00 | 8280.00 | 8280.00 | Mankha Electrotech Pvt Ltd
3.00 | SITC of tubular FRP pole of 76 mm nominal diameter of 1 Mtr length/height including 32 mm dia bracket of length minimum 30 cm for fixing light fixtures, with 200 x 200 x 5 mm base plate and required holes for installation with base including concrete foundation and bolt etc. as required including painting with synthetic enamel paint etc. complete upto the satisfaction of EIC. | 20.00 | Nos. |  | 972.00 | 19440.00 | 6100.00 | 122000.00 | 10000.00 | 200000.00 | 12500.00 | 250000.00 | 3140.00 | 62800.00 | 12144.00 | 242880.00 | 19440.00 | Instapower Ltd
4.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incomers and necessary interlocking, floor mounted with MS angle leg ( 50 mm x 50 mm x 4mm thick), making PCC work etc., i/c providing following switch gears:- INCOMING :- MCCB FP 100A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos INSTRUMENTS :- -2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. -2 Sets of RYB phase LED indicating lamps each controlled by 2 amp MCB. Bus Bar:- 125 Amps Aluminium busbar for 3 phase and neutral - 1 Set OUTGOINGS :- MCCB FP 40 A, 25KA with built in thermal magnetic release- 4 Nos 40 A TP Contactor operated with digital/analog 24 hrs Timer - 4 Nos | 3.00 | Nos. |  | 110500.00 | 331500.00 | 223000.00 | 669000.00 | 140000.00 | 420000.00 | 150000.00 | 450000.00 | 80000.00 | 240000.00 | 103500.00 | 310500.00 | 240000.00 | JCC ENGINEERS PRIVATE LIMITED
5.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted Feeder panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of suitable size at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars, cable gland plates, arrangement for incomers , floor mounted with MS angle leg, making PCC work etc., i/c providing following switch gears:- Bus Bar:- 100 Amps Aluminium busbar for phase and neutral - 1 Set OUTGOINGS :- MCCB FP 63A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 01 Nos. | 6.00 | Nos. |  | 31050.00 | 186300.00 | 27000.00 | 162000.00 | 16500.00 | 99000.00 | 30000.00 | 180000.00 | 11000.00 | 66000.00 | 43125.00 | 258750.00 | 66000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supply of Energy efficient 45-48 watt LED street light fixtures with sufficient number of LEDs, control gear / driver and all other associated accessories and having color temperature 5700 K and conforming to the degree of protection IP65 complete as required and as specified. | 80.00 | Nos. |  | 1800.00 | 144000.00 | 1500.00 | 120000.00 | 1850.00 | 148000.00 | 1900.00 | 152000.00 | 3000.00 | 240000.00 | 2376.00 | 190080.00 | 120000.00 | Power And Instrumentation Guj Ltd
7.00 | Supply of 1.1 KV grade, XLPE insulated and PVC sheathed Aluminium conductor, armored LT Cable, conforming to IS 7098 (Part -1) 1988 with upto date amendments and as specified, of following sizes.
7.10 | 4C x 16 Sqmm | 2700.00 | Mtr |  | 123.05 | 332235.00 | 125.00 | 337500.00 | 142.00 | 383400.00 | 150.00 | 405000.00 | 200.00 | 540000.00 | 179.40 | 484380.00 | 332235.00 | Instapower Ltd
7.20 | 3.5C x 50 Sqmm | 4500.00 | Mtr |  | 235.75 | 1060875.00 | 256.00 | 1152000.00 | 275.00 | 1237500.00 | 280.00 | 1260000.00 | 300.00 | 1350000.00 | 478.86 | 2154870.00 | 1060875.00 | Instapower Ltd
7.30 | 3.5C X 95 Sqmm | 300.00 | Mtr |  | 400.20 | 120060.00 | 435.00 | 130500.00 | 480.00 | 144000.00 | 490.00 | 147000.00 | 500.00 | 150000.00 | 752.10 | 225630.00 | 120060.00 | Instapower Ltd
8.00 | Supply of Pole mounted SMC junction box with suitable Bottom Entry for 02(two) nos. 4C x 16 Sqmm cable and IP 55 for out door use including, 01No. of 6 Amp SPN MCB, Din channel, Connecter, PVC Glands for above cable and Suitable accessories required for mounting JB on existing pole (Like clamp, Nut Bolts etc.) Complete as per site requirement. | 430.00 | Nos. |  | 2040.00 | 877200.00 | 2000.00 | 860000.00 | 1200.00 | 516000.00 | 1800.00 | 774000.00 | 400.00 | 172000.00 | 1440.00 | 619200.00 | 172000.00 | JCC ENGINEERS PRIVATE LIMITED
9.00 | Supply & Laying 3X2.5 Sqmm Cu flexible wire inside street light pole for connection of MCB to light fixtures as required and as specified. | 1800.00 | Mtr |  | 135.00 | 243000.00 | 83.00 | 149400.00 | 100.00 | 180000.00 | 200.00 | 360000.00 | 90.00 | 162000.00 | 100.63 | 181134.00 | 149400.00 | Power And Instrumentation Guj Ltd
10.00 | Supply of HDPE pipes, conforming to IS 14930 (Part II) with upto date amendments of following size complete as required.
10.10 | 50 mm dia. | 2600.00 | Mtr |  | 78.00 | 202800.00 | 88.00 | 228800.00 | 105.00 | 273000.00 | 100.00 | 260000.00 | 95.00 | 247000.00 | 57.50 | 149500.00 | 149500.00 | Mankha Electrotech Pvt Ltd
10.20 | 63 mm dia. | 4500.00 | Mtr |  | 93.60 | 421200.00 | 140.00 | 630000.00 | 115.00 | 517500.00 | 145.00 | 652500.00 | 120.00 | 540000.00 | 80.50 | 362250.00 | 362250.00 | Mankha Electrotech Pvt Ltd
10.30 | 90 mm dia | 250.00 | Mtr |  | 128.40 | 32100.00 | 280.00 | 70000.00 | 130.00 | 32500.00 | 270.00 | 67500.00 | 400.00 | 100000.00 | 126.50 | 31625.00 | 31625.00 | Mankha Electrotech Pvt Ltd
11.00 | Laying of HDPE pipes of Size 90 mm and below, direct in ground upto a depth of 0.75 Mtr. including excavation and refilling the trench etc. complete as required. | 6760.00 | Mtr |  | 36.00 | 243360.00 | 80.00 | 540800.00 | 75.00 | 507000.00 | 135.00 | 912600.00 | 40.00 | 270400.00 | 80.50 | 544180.00 | 243360.00 | Instapower Ltd
12.00 | Laying of HDPE pipes of Size 90 mm and below, direct in open/on surface with required accessories like clamp, joint etc. complete as required. | 130.00 | Mtr |  | 30.00 | 3900.00 | 45.00 | 5850.00 | 25.00 | 3250.00 | 90.00 | 11700.00 | 30.00 | 3900.00 | 80.50 | 10465.00 | 3250.00 | surbhi association
13.00 | Laying of HDPE Pipe of Size 90 mm and below, in road crossing and hard surface upto a depth of 1 Mtr. through HDD/ Horizontal boaring as required & as per the direction of Engineer-in-charge. | 90.00 | Mtr |  | 1200.00 | 108000.00 | 600.00 | 54000.00 | 800.00 | 72000.00 | 500.00 | 45000.00 | 500.00 | 45000.00 | 149.50 | 13455.00 | 13455.00 | Mankha Electrotech Pvt Ltd
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC / HDPE / DWC / HUME / STONEWARE / METAL pipe complete as required.
14.10 | 4C x 16 Sqmm | 2530.00 | Mtr |  | 36.00 | 91080.00 | 30.00 | 75900.00 | 20.00 | 50600.00 | 10.00 | 25300.00 | 10.00 | 25300.00 | 15.00 | 37950.00 | 25300.00 | JCC ENGINEERS PRIVATE LIMITED, ANU ENGINEERING CORPORATION
14.20 | 3.5C x 50 Sqmm | 4450.00 | Mtr |  | 60.00 | 267000.00 | 45.00 | 200250.00 | 25.00 | 111250.00 | 10.00 | 44500.00 | 10.00 | 44500.00 | 30.00 | 133500.00 | 44500.00 | JCC ENGINEERS PRIVATE LIMITED, ANU ENGINEERING CORPORATION
14.30 | 3.5C X 95 Sqmm | 250.00 | Mtr |  | 60.00 | 15000.00 | 65.00 | 16250.00 | 50.00 | 12500.00 | 15.00 | 3750.00 | 10.00 | 2500.00 | 49.00 | 12250.00 | 2500.00 | JCC ENGINEERS PRIVATE LIMITED
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size (clamped with 1mm thick saddle) on wall surface / open complete as required.
15.10 | 4C x 16 Sqmm | 70.00 | Mtr |  | 36.00 | 2520.00 | 45.00 | 3150.00 | 20.00 | 1400.00 | 70.00 | 4900.00 | 10.00 | 700.00 | 10.00 | 700.00 | 700.00 | JCC ENGINEERS PRIVATE LIMITED, Mankha Electrotech Pvt Ltd
15.20 | 3.5C x 50 Sqmm | 50.00 | Mtr |  | 60.00 | 3000.00 | 50.00 | 2500.00 | 25.00 | 1250.00 | 80.00 | 4000.00 | 10.00 | 500.00 | 20.00 | 1000.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
15.30 | 3.5C X 95 Sqmm | 50.00 | Mtr |  | 60.00 | 3000.00 | 70.00 | 3500.00 | 60.00 | 3000.00 | 90.00 | 4500.00 | 10.00 | 500.00 | 30.00 | 1500.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
16.00 | Supplying and making end termination with aluminium lugs, with brass compression gland for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (Each set contains lugs for all cores and a brass gland)
16.10 | 3.5C x 50 Sqmm | 20.00 | Set |  | 1260.00 | 25200.00 | 350.00 | 7000.00 | 350.00 | 7000.00 | 150.00 | 3000.00 | 100.00 | 2000.00 | 350.00 | 7000.00 | 2000.00 | JCC ENGINEERS PRIVATE LIMITED
16.20 | 3.5C X 95 Sqmm | 6.00 | Set |  | 1440.00 | 8640.00 | 475.00 | 2850.00 | 800.00 | 4800.00 | 200.00 | 1200.00 | 100.00 | 600.00 | 450.00 | 2700.00 | 600.00 | JCC ENGINEERS PRIVATE LIMITED
17.00 | Installation, Testing and commissioning of 01 nos. LED street light fixtures on the existing octagonal pole with bracket complete required. | 80.00 | EA |  | 540.00 | 43200.00 | 150.00 | 12000.00 | 80.00 | 6400.00 | 50.00 | 4000.00 | 10.00 | 800.00 | 200.00 | 16000.00 | 800.00 | JCC ENGINEERS PRIVATE LIMITED
18.00 | Installation of SMC junction Box on existing pole including Supplying and making end termination for two (02) cables of size 4C x 16 Sqmm of 1.1 KV grade complete as required. The job includes excavation, removing existing loop in/loop out cable, termination into new junction box and making good of the excavated surface etc. as per site requirement. | 350.00 | Nos. |  | 342.00 | 119700.00 | 200.00 | 70000.00 | 300.00 | 105000.00 | 100.00 | 35000.00 | 10.00 | 3500.00 | 450.00 | 157500.00 | 3500.00 | JCC ENGINEERS PRIVATE LIMITED
19.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal / coke and salt as required. | 15.00 | EA |  | 9360.00 | 140400.00 | 6000.00 | 90000.00 | 6500.00 | 97500.00 | 5500.00 | 82500.00 | 4000.00 | 60000.00 | 4500.00 | 67500.00 | 60000.00 | JCC ENGINEERS PRIVATE LIMITED
20.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 2500.00 | Mtr |  | 20.25 | 50625.00 | 25.00 | 62500.00 | 22.00 | 55000.00 | 35.00 | 87500.00 | 15.00 | 37500.00 | 33.00 | 82500.00 | 37500.00 | JCC ENGINEERS PRIVATE LIMITED
21.00 | Supplying and fixing of Octagonal pole side covers (Loop in /Loop out Box Cover) with necessary locking arrangement and suitable for existing street light poles. | 180.00 | Nos. |  | 276.75 | 49815.00 | 700.00 | 126000.00 | 220.00 | 39600.00 | 800.00 | 144000.00 | 100.00 | 18000.00 | 560.00 | 100800.00 | 18000.00 | JCC ENGINEERS PRIVATE LIMITED
32.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 5554050.00 |  | 6493750.00 |  | 5790950.00 |  | 6963950.00 |  | 4755555.00 |  | 7246879.00
Lowest Amount Quoted BY: JCC ENGINEERS PRIVATE LIMITED(4755555.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of perimeter lighting and associated works at SGRDJ International Airport, Amritsar. Tender ID: 2023_AAI_166207_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | JCC ENGINEERS PRIVATE LIMITED | 4755555.00 | L1
| 2 | Instapower Ltd | 5554050.00 | L2
| 3 | surbhi association | 5790950.00 | L3
| 4 | Power And Instrumentation Guj Ltd | 6493750.00 | L4
| 5 | ANU ENGINEERING CORPORATION | 6963950.00 | L5
| 6 | Mankha Electrotech Pvt Ltd | 7246879.00 | L6