## BoQ1
Government eProcurement System Created By: Bidyut Roy Created Date/Time: 01-Nov-2023 03:09 PM Tender Title: Development of Solapur Airport for VFR operations Sh Airside Electrical works for Tender ID: 2023_AAI_169058_1
Tender Inviting Authority: Asst. GENERAL MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, KOLHAPUR AIRPORT, KOLHAPUR.
Name Of Work :- Development of Solapur Airport for VFR operations. SH: Airside Electrical works for VFR operations.
Contract No: 2023_AAI_169058_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Manish Electricals(GSTN-23ABLPM9012E1ZW) |  | AMA Private Limited(GSTN-27AAACA1016F1ZE)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of PAPI System (one set of 04 units) along with all its accessories i/c. 200W lamps , lense , filters , checking stick base holder etc. complete as required as per ICAO specification frangible as ICAO and DGCA CAR and confirming to technical specifications and all test reports confirming to photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc as per requirement.(type test certificate to be provided before supply). | 2.00 | Set |  | 493250.00 | 986500.00 | 475000.00 | 950000.00 | 380000.00 | 760000.00 | 760000.00 | AMA Private Limited
2.00 | Installation, testing and commissioning of PAPI System (04 units) along with all its accessories i/c. transformer housing boxes, bases for checking stick including finalization of location, taking level & setting right angles (minimum 03 times) by Total Station / Theodolite, excavation, RCC foundation (1:2:4) upto required level, plastering, refilling, providing foundation bolts and nuts, fitting, fixing, cleaning, marking, earthing, connecting, providing pipe for secondary leads, painting and ground calibration of the system etc. complete as required. | 2.00 | Job |  | 75000.00 | 150000.00 | 90000.00 | 180000.00 | 40000.00 | 80000.00 | 80000.00 | AMA Private Limited
3.00 | Supply of calibration kit ,clinometer, sprit level, checking stick & base plates etc complete for above mentioned PAPI set. | 1.00 | Set |  | 120000.00 | 120000.00 | 75000.00 | 75000.00 | 80000.00 | 80000.00 | 75000.00 | Manish Electricals
4.00 | Design, Supply, installation, testing and commissioning of guidance sign boards of various sizes (as per annexure) made of anodised 2 mm thick aluminium frame with suitable angle support with 1.5 mmm thick aluminium back cover and 4 mm thick poly carbonate sheet with glare free face, the letter and symbols should be screen printed with required colouring, suitable arrangement shall be made to function on both main and standby (runway/taxiway) circuits with internal control circuits. Suitable arrangements shall be made for water tightness and locking arrangement, sign boards shall be uniformly internally illuminated with required number of LED lights to achieve required illumination level, operated on input source of 2.5 A to 6.6 A constant current without any flickering, including its supporting legs, breakable coupling and base frame and foundation etc. photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc as per requirement.complete as required as per specification attached etc as required(type test certificate to be provided before supply). | 30.00 | sq.mm |  | 39255.00 | 1177650.00 | 34000.00 | 1020000.00 | 38000.00 | 1140000.00 | 1020000.00 | Manish Electricals
5.00 | Supply and installation of ICAO complied LED model illuminated frangible Wind sock/Wind indicator (WDI) with LED obstruction Light(with photometric report-4C) , with frangible wind pole and with all accessories along with RCC civil foundation and an all aorund paved area as per ICAO/DGCA car requirement with white visble band of paint work dia 15meters as per ICAO norms complete as required as follows(type test certificate to be provided before supply, all test reports confirming to photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc).:(make: SGS lattice type franfible 4.5 mtr or equivalent) 1.Minimum 4.5 meter height FRP(fiber-reinforced plastic) fragible lattice mast (min 500mmx500mm) confirming to ICAO annex-14. 2.Mounting arrangement & provision of sufficent LED light fixtures to meet minimum lux level requirement as per ICAO standard. 3.One no. LED obstruction light aluminium cast body and red polycarbonate dome. 4.Arrangment for titling down of mast for maintenance. | 1.00 | Job |  | 220000.00 | 220000.00 | 210000.00 | 210000.00 | 225000.00 | 225000.00 | 210000.00 | Manish Electricals
6.00 | Supply and installation of ICAO complied frangible H-Indicator with LED Light/LED model as required with all accessories and RCC foundtion complying IP 65 complete as required.(type test certificate to be provided before supply, all test reports confirming to photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc).with all around paved area 4.5meterX4.5meter compelete etc as required. | 1.00 | Job |  | 220000.00 | 220000.00 | 190000.00 | 190000.00 | 245000.00 | 245000.00 | 190000.00 | Manish Electricals
7.00 | Supply, installation, testing and commissioning of medium intensity LED type aviation obstruction light luminair with lamp, fixtures, mounting clamp, nut bolt etc. complete as required. (Make-intertek or equivalent )type test certificate to be provided before supply, all test reports confirming to photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc) | 6.00 | Job |  | 5500.00 | 33000.00 | 7000.00 | 42000.00 | 5500.00 | 33000.00 | 33000.00 | Techno Electricals, AMA Private Limited
8.00 | Supply and installation of ICAO complied rotating aerodrome beacon 30 flashes per minute ,white and green lights suitable to operate on 240V 50 hz AC supply complete as required including necessary RCC civil foundation as per OEM recommendation compet as required..(type test certificate to be provided before supply, all test reports confirming to photometry 4C requirement test report as per ICAO annex 14 and DGCA CAR etc)(Make : EMA or equivalent as per ICAO norms) | 1.00 | Job |  | 525000.00 | 525000.00 | 525000.00 | 525000.00 | 450000.00 | 450000.00 | 450000.00 | AMA Private Limited
9.00 | Supply installation testing and commissioning of Crash siren (Horizontal Double mounting carbon brush less AC motor) suitable for operation at 240V 50 hz AC supply and audible range range should of 3 Km including civil foundation RCC complete as required. | 1.00 | Job |  | 22425.00 | 22425.00 | 15000.00 | 15000.00 | 25000.00 | 25000.00 | 15000.00 | Manish Electricals
10.00 | Supply of CI isolating transformer housing box, water tight round type , metal container of outside dia 330mm, height 450mm made of 10 mm thick cast iron moulding all around, except the top surface which is 15mm thick , cast iron moulding suitable to receive light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole at one/both side surface centre 3'' above bottom surface suitable to receive one number of 50mm dia & one number 15 mm dia. 'B' class GI pipe with check nuts. The box should have 2 nos earth bolts M10 x 30 mm inside near the hold ( 4 '' away from the hole centre) and having a drain hole at the bottom tapped to receive 1/2'' dia GI pipe and having clear opening of 220 mm at the top surface and 6 nos M10 tapped hole at the hole a) Single Hole CI housing Box | 100.00 | Nos |  | 5462.00 | 546200.00 | 5600.00 | 560000.00 | 4800.00 | 480000.00 | 480000.00 | AMA Private Limited
11.00 | Installation of Transformer housing Box having single/double entry with a base concrete of 1:3:6 (1;cement, 3: coarse sand, 6: concrete of 20mm nominal size) of size 630X630X100mm thick and all around concrete of 1:2:4 (1;cement, 2: coarse sand, 4: concrete of 20mm nominal size) 150mm and top slope as specified including providing & fixing 150mm long 15mm dia "b" class GI pipe with check nut for drainage of water at the bottom. Fixing of 50mm dia GI pipe & 15mm dia G.I. pipe to the housing box by provinding double check nut for 50mm dia GI pipe alingment of housing box, top slopping with concrete etc.. complete as required (As per drawing/ technical specifications). | 124.00 | Job |  | 2800.00 | 347200.00 | 2400.00 | 297600.00 | 3000.00 | 372000.00 | 297600.00 | Manish Electricals
12.00 | Supplying and laying of 50mm dia 'B' Class ISI marked GI pipe in the newly constructing Runway/Taxiway shoulder along with civil concrete bituminous work , embeding the pipe in the concrete/Bituminous, alignment etc. for connecting to the existing transformer housing box complete as required but excluding the scope of excavation | 744.00 | Meter |  | 650.00 | 483600.00 | 675.00 | 502200.00 | 575.00 | 427800.00 | 427800.00 | AMA Private Limited
13.00 | Supply and laying of 15mm dia 'B' Class ISI marked G.I. pipe in the newly constructing Runway/taxi way shoulder along with civil concrete/bituminous work, embeding the pipe in the concerete/bituminous, alignmnet etc for connecting to the existing transformer housing box complete as required. | 744.00 | Meter |  | 310.00 | 230640.00 | 240.00 | 178560.00 | 325.00 | 241800.00 | 178560.00 | Manish Electricals
14.00 | Supply of cast iron iron (CI) collar of 330mm dia of following height , 10mm thick cast iron moulding all round except top surface , which is 15mm thick 220mm opening on top & bottom, with 6 nos M10 tapped hole on top and 6 nos. Throught holes at bottom to pass M10 bolts at 260 mm PCD fixon eaxisting transformer housing box with M 10 size SS bolt, washer gasket etc. (a) 150 mm | 20.00 | Nos. |  | 3000.00 | 60000.00 | 3400.00 | 68000.00 | 2700.00 | 54000.00 | 54000.00 | AMA Private Limited
15.00 | Supply of cast iron iron (CI) collar of 330mm dia of following height , 10mm thick cast iron moulding all round except top surface , which is 15mm thick 220mm opening on top & bottom, with 6 nos M10 tapped hole on top and 6 nos. Throught holes at bottom to pass M10 bolts at 260 mm PCD fixon eaxisting transformer housing box with M 10 size SS bolt, washer gasket etc. (a) 200 mm | 80.00 | Nos. |  | 3200.00 | 256000.00 | 3500.00 | 280000.00 | 2800.00 | 224000.00 | 224000.00 | AMA Private Limited
16.00 | Supply of cast iron iron (CI) collar of 330mm dia of following height , 10mm thick cast iron moulding all round except top surface , which is 15mm thick 220mm opening on top & bottom, with 6 nos M10 tapped hole on top and 6 nos. Throught holes at bottom to pass M10 bolts at 260 mm PCD fixon eaxisting transformer housing box with M 10 size SS bolt, washer gasket etc. (a) 250 mm | 20.00 | Nos. |  | 3600.00 | 72000.00 | 3650.00 | 73000.00 | 2900.00 | 58000.00 | 58000.00 | AMA Private Limited
17.00 | Installation of C.I. colar (size varies from 150 mm height to 250 mm height) on the existing transformer housing box with M-10 bolts and base plate gasket including removal of runway edge light fitting from the transformer housing box and re-installation of runway edge light fitting on he collar, connections i/e dismantelling, cutting, bitemenous surface and making a slope of suitable grading with 1:3:6 and making surface good etc. complete as required. | 120.00 | Nos. |  | 1500.00 | 180000.00 | 700.00 | 84000.00 | 3000.00 | 360000.00 | 84000.00 | Manish Electricals
18.00 | Supply of CI isolating transformer housing box, water tight round type , metal container of outside dia 330mm, height 450mm made of 10 mm thick cast iron moulding all around, except the top surface which is 15mm thick , cast iron moulding suitable to receive light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole at one/both side surface centre 3'' above bottom surface suitable to receive one number of 50mm dia & one number 15 mm dia. 'B' class GI pipe with check nuts. The box should have 2 nos earth bolts M10 x 30 mm inside near the hold ( 4 '' away from the hole centre) and having a drain hole at the bottom tapped to receive 1/2'' dia GI pipe and having clear opening of 220 mm at the top surface and 6 nos M10 tapped hole at the hole a) Double Hole CI housing Box | 24.00 | Nos. |  | 5500.00 | 132000.00 | 5800.00 | 139200.00 | 4800.00 | 115200.00 | 115200.00 | AMA Private Limited
19.00 | SITC of FAA & ICAO complied indoor type microprocessor based, air cooled constant current regulator of Thyristor control electronic type suitable for use on 240/415 VAC; 50 Hz, input AC supply with below mentioned output power at 20 amps with 5 steps variation of current output suitable for local and remote control operation with 24/48 VDC control supply complete with output current indicated on multifunction digital display, over current, over voltage, earth fault protection and earth leakage meter, positive back indication equipments relay contactor etc. as required as per specification along with proper base channel for mounting arrengment of following rating(calibration reports of the meters used in the CCR manufacturing should be submitted) : 30 KW CCR with 25 KW Tapping. | 1.00 | Nos. |  | 475267.00 | 475267.00 | 512000.00 | 512000.00 | 575000.00 | 575000.00 | 475267.00 | Techno Electricals
20.00 | SITC of FAA & ICAO complied indoor type microprocessor based, air cooled constant current regulator of Thyristor control electronic type suitable for use on 240/415 VAC; 50 Hz, input AC supply with below mentioned output power at 6.6 amps with 5 steps variation of current output suitable for local and remote control operation with 24/48 VDC control supply complete with output current indicated on multifunction digital display, over current, over voltage, earth fault protection and earth leakage meter, positive back indication equipments relay contactor etc. as required as per specification along with proper base channel for mounting arrengment of following rating (calibration reports of the meters used in the CCR manufacturing should be submitted: 7.5 KW CCR with 4 KW Tapping. | 2.00 | Nos. |  | 244375.00 | 488750.00 | 281250.00 | 562500.00 | 325000.00 | 650000.00 | 488750.00 | Techno Electricals
21.00 | SITC of FAA & ICAO complied indoor type microprocessor based, air cooled constant current regulator of Thyristor control electronic type suitable for use on 240/415 VAC; 50 Hz, input AC supply with below mentioned output power at 6.6 amps with 5 steps variation of current output suitable for local and remote control operation with 24/48 VDC control supply complete with output current indicated on multifunction digital display, over current, over voltage, earth fault protection and earth leakage meter, positive back indication equipments relay contactor etc. as required as per specification along with proper base channel for mounting arrengment of following rating(calibration reports of the meters used in the CCR manufacturing should be submitted : 4 KW CCR. | 1.00 | Nos. |  | 185000.00 | 185000.00 | 200000.00 | 200000.00 | 225000.00 | 225000.00 | 185000.00 | Techno Electricals
22.00 | Installation, Testing, Commissioning of CCR including connection of control cable, power cable along with acessories connection complete as required. | 4.00 | Job |  | 7000.00 | 28000.00 | 10000.00 | 40000.00 | 10000.00 | 40000.00 | 28000.00 | Techno Electricals
23.00 | Supply of True RMS (make: Fluke) clamp meter with full calibartion certificate complete as required confirming to ICAO 9157 (part 5-Electrical equipment) complete as required. | 1.00 | Job |  | 44000.00 | 44000.00 | 60000.00 | 60000.00 | 4500.00 | 4500.00 | 4500.00 | AMA Private Limited
24.00 | Supply of following sizes of XLPE insulated PVC sheathed, Aluminium conductor armoured electric cable of 1.1 KV grade confirming to IS 7098 PART-I with upto date amended. (a)4 X 25 sq.mm | 1500.00 | Meter |  | 175.00 | 262500.00 | 240.00 | 360000.00 | 270.00 | 405000.00 | 262500.00 | Techno Electricals
25.00 | Supplying and making indoor end termination with brass double compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (a)4 X 25 sq.mm | 4.00 | Set |  | 400.00 | 1600.00 | 500.00 | 2000.00 | 900.00 | 3600.00 | 1600.00 | Techno Electricals
26.00 | Supply of 6 sqmm. XLPE insulated & PE Sheathed unshielded (unscreened) Stranded copper conductor single core airfield lighting cable of 5KV grade confirming to IS 7098 Part-II with upto date amendement s as required and conforming to technical specifications enclosed(conforming to IS: 7098-Part II (latest edition) | 8000.00 | Meter |  | 93.00 | 744000.00 | 95.00 | 760000.00 | 90.00 | 720000.00 | 720000.00 | AMA Private Limited
27.00 | Supply of 16 sqmm. XLPE insulated & PE unshielded (unscreened) Sheathed Stranded copper conductor single core airfield lighting cable of 5KV grade confirming to IS 7098 Part-II with upto date amendement s as required and conforming to particuar specifications.(conforming to IS: 7098-Part II (latest edition) complete as reuired. | 5000.00 | Meter |  | 211.00 | 1055000.00 | 225.00 | 1125000.00 | 190.00 | 950000.00 | 950000.00 | AMA Private Limited
28.00 | Supply of 2 x 4 sq.mm size secondary lead made out of multi stranded copper conductor, EPR insulalted PCP sheathed, treated 600V grade cable as specified in particular specification and as required. | 200.00 | Meter |  | 165.00 | 33000.00 | 250.00 | 50000.00 | 140.00 | 28000.00 | 28000.00 | AMA Private Limited
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in existing HDPE/HUME/RCC/GI pipe complete as required. Upto 35 sq.mm | 10000.00 | Meter |  | 15.00 | 150000.00 | 20.00 | 200000.00 | 20.00 | 200000.00 | 150000.00 | Techno Electricals
30.00 | Supplying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 10000.00 | Meter |  | 70.00 | 700000.00 | 65.00 | 650000.00 | 190.00 | 1900000.00 | 650000.00 | Manish Electricals
31.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 10000.00 | Meter |  | 105.00 | 1050000.00 | 120.00 | 1200000.00 | 120.00 | 1200000.00 | 1050000.00 | Techno Electricals
32.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing cable as required | 9000.00 | Meter |  | 22.00 | 198000.00 | 25.00 | 225000.00 | 14.00 | 126000.00 | 126000.00 | AMA Private Limited
33.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 117.00 | Job |  | 400.00 | 46800.00 | 480.00 | 56160.00 | 750.00 | 87750.00 | 46800.00 | Techno Electricals
34.00 | Supply of MIRL halogen type Taxiway Edge Elevated type light fixtures45 Watts & meeting ICAO requirments 6.6 amps current, complete with base plate, breakablecoupling, mounting assembly, gasket, BLUE lens, one 2 pole-plug with leads etc. conforming to particular specification as required.. and confirming to ICAO requirements as per the enclosed particular/technical specifications complete as required. (type test certificate to be provided before supply, all test reports confirming to photometry 4C requirement,frangibility test report as per ICAO annex 14 and DGCA CAR etc).: | 30.00 | Nos |  | 4000.00 | 120000.00 | 3800.00 | 114000.00 | 3000.00 | 90000.00 | 90000.00 | AMA Private Limited
35.00 | Supply of 200 watts 6.6 Amps 2 pin Halogen lamp suitable for the HIRL fitting./ Suitable for Existing AMA make elevated type HIRL fitting. | 74.00 | Nos |  | 500.00 | 37000.00 | 550.00 | 40700.00 | 355.00 | 26270.00 | 26270.00 | AMA Private Limited
36.00 | Supply of pre-focus 2 pin lamp holder for 200 W/45 W, 6.6 A HIRL/MIRL fittings | 20.00 | Nos |  | 600.00 | 12000.00 | 300.00 | 6000.00 | 450.00 | 9000.00 | 6000.00 | Manish Electricals
37.00 | Supply of 45 Watts 6.6/6.6 Amps 5KV grade 50 Hz series type isolating transformer conforming to relevant IS, encapsulated in polyster resin finally moulded with neoprene type rubber with primary & secondary connections as specified in particular specifications complete as required. | 60.00 | Nos |  | 4000.00 | 240000.00 | 3500.00 | 210000.00 | 3200.00 | 192000.00 | 192000.00 | AMA Private Limited
38.00 | Supply of 200 Watts 6.6/6.6 Amps 5KV grade 50 Hz series type isolating transformer conforming to relevant IS, encapsulated in polyster resin finally moulded with neoprene type rubber with primary & secondary connections as specified in particular specifications complete as required. | 30.00 | Nos |  | 4800.00 | 144000.00 | 5000.00 | 150000.00 | 4500.00 | 135000.00 | 135000.00 | AMA Private Limited
39.00 | Supply of 5 KV, Cu grade plug and receptacle of type I class "B" connector suitable for field attachment with 5 KV grade PVC insulated PVC sheathed/ XLPE insulated cable single core 16 Sq.mm copper conductor cable conforming to the relevant IS specification etc. complete as required. | 50.00 | Nos |  | 450.00 | 22500.00 | 450.00 | 22500.00 | 450.00 | 22500.00 | 22500.00 | Techno Electricals, Manish Electricals, AMA Private Limited
40.00 | Supply of 5 KV, Cu grade plug and receptacle of type I class "B" connector suitable for field attachment with 5 KV grade PVC insulated PVC sheathed single core 6 Sq.mm copper conductor cable conforming to the relevant IS specification etc. complete as required. | 90.00 | Nos |  | 450.00 | 40500.00 | 450.00 | 40500.00 | 450.00 | 40500.00 | 40500.00 | Techno Electricals, Manish Electricals, AMA Private Limited
41.00 | Making field connections by crimping 6/16 Sq.mm plug and receptacle with existing 6/16 sq.mm single core PVC copper conductor PVC insulated, PVC sheathed cable/XLPE cable including filling the gap with water sealing compound, applying HT insulation tape, over which PVC tape etc. as required. | 210.00 | Job |  | 80.00 | 16800.00 | 200.00 | 42000.00 | 150.00 | 31500.00 | 16800.00 | Techno Electricals
42.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 50.00 | cum |  | 1250.00 | 62500.00 | 800.00 | 40000.00 | 6000.00 | 300000.00 | 40000.00 | Manish Electricals
43.00 | Supply of following filters suitable for aviation ground lighting system generally conforming to relevant IS. Clear filter for PAPI Unit. (one set of 04 Units) | 1.00 | set |  | 8800.00 | 8800.00 | 50000.00 | 50000.00 | 4500.00 | 4500.00 | 4500.00 | AMA Private Limited
44.00 | Supply of following filters suitable for aviation ground lighting system generally conforming to relevant IS. Red filter for PAPI Unit. (one set of 04 Units) | 1.00 | set |  | 16000.00 | 16000.00 | 50000.00 | 50000.00 | 5500.00 | 5500.00 | 5500.00 | AMA Private Limited
45.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 18.00 | set |  | 8000.00 | 144000.00 | 7500.00 | 135000.00 | 7000.00 | 126000.00 | 126000.00 | AMA Private Limited
46.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 11.00 | set |  | 8000.00 | 88000.00 | 7500.00 | 82500.00 | 7000.00 | 77000.00 | 77000.00 | AMA Private Limited
47.00 | Constructing masonry Chamber 120x120x100 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve, with C.I. surface box 100 mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) , i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design | 6.00 | Job |  | 13000.00 | 78000.00 | 12000.00 | 72000.00 | 25000.00 | 150000.00 | 72000.00 | Manish Electricals
48.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering 1:2:4 (1 cement : 2 coarse sand (zone-III) : 4 graded stone aggregate 20 mm nominal size) | 50.00 | cum |  | 6500.00 | 325000.00 | 7000.00 | 350000.00 | 6000.00 | 300000.00 | 300000.00 | AMA Private Limited
49.00 | Supply of 6 mm thick powder coated MS cover plate to cover the CI transformer bousing box of 300 mm ouside dia with 6 nos. M10 tapped holes and required dia hole at the centre for entry of scondary lead as required.(Supply of bolt included) | 24.00 | nos |  | 750.00 | 18000.00 | 1200.00 | 28800.00 | 1200.00 | 28800.00 | 18000.00 | Techno Electricals
50.00 | kerf cutiing with machine in runway/taxiway bitumen surface of suitable deopth and width ( min : 200 mm) and refilling the same with seleant material of sufficient strength for runway complete as required. | 150.00 | mtrs |  | 425.00 | 63750.00 | 750.00 | 112500.00 | 375.00 | 56250.00 | 56250.00 | AMA Private Limited
51.00 | Execution of HDD(horizontal direction drilling ) inluding provision of HDPE 100mm pipe in the drilled hole along with necessary excavation (using machine )at a depth of around 3 mtr to cross the bitumen/ concrete area road/taxiway/runway etc complete as required. | 70.00 | mtrs |  | 1700.00 | 119000.00 | 1600.00 | 112000.00 | 900.00 | 63000.00 | 63000.00 | AMA Private Limited
| Total in Figures |  |  |  |  | 12779982.00 |  | 13050720.00 |  | 14143470.00
Lowest Amount Quoted BY: Techno Electricals(12779982.00)

## BOQ Summary
BOQ Summary Details Tender Title: Development of Solapur Airport for VFR operations Sh Airside Electrical works for Tender ID: 2023_AAI_169058_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Techno Electricals | 12779982.00 | L1
| 2 | Manish Electricals | 13050720.00 | L2
| 3 | AMA Private Limited | 14143470.00 | L3