## BoQ1
Government eProcurement System Created By: ARUN KUMAR K Created Date/Time: 08-Nov-2023 04:42 PM Tender Title: Provision of Baggage Handling System Tender ID: 2023_AAI_169832_1
Tender Inviting Authority: Asst. General Manager (Engg-E), Airports Authority of India, Bangalore.
Name of Work: Provision of Baggage Handling System (Arrival Carousel) at Mysuru Airport.
Contract No: Tender ID: 2023_AAI_169832_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GANNON DUNKERLEY AND CO LTD(GSTN-19AAACG1846P1Z6) |  | PREMIER ENGINEERING TECHNICS PVT. LTD.(GSTN-27AADCP1420F1ZW) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA) |  | Fox Solutions Private Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I : SITC OF ARRIVAL CAROUSEL & ASSOCIATED ITEMS
1.01 | ARRIVAL CAROUSEL Design, Supply, Installation, Testing and Commisioning of heavy duty endless slat type Arrival Carousel Baggage handling system having nominal useful width of 950 mm having rubber slats black in colour with smooth top of PVC/PU/Rubber, Antistatic, flame retardant, height of 450 mm from finished floor level and speed of 24-30 meter per minute. The Carousel shall have die cast aluminium chain block friction type, suitable capacity drive unit complete with overlapping slats, finished chain track, unit frame work tension adjustment device, stainless steel side covering (inner & outer) in the passenger area as well as in non-passenger area, toe kick plate at inner & outer sides, infill, rubber slat of suitable dimension with MS slat support having live loading capacity of 35 Kg per linear meter, all accessories including cutting and drilling of holes, testing and commissioning etc complete as required as per attached technical specifications and site requirements. (Note : The Quantity indicated is tendative and may vary as per site conditions. The successful bidder shall design & prepare the layout drawings/detailed working drawings based on actual site conditions and submit for approval of AAI after award of work) | 48.50 | Meter |  | 50000.00 | 2425000.00 | 60000.00 | 2910000.00 | 41250.00 | 2000625.00 | 37113.40 | 1799999.90 | 1799999.90 | Fox Solutions Private Limited
2.00 | PLC BASED CONTROL PANEL Design, Fabrication, Supply, Installation, Testing and Commissioning of PLC based Control Panel of cubical type, indoor floor/ wall mounted, compartmentalized, fabricated out of CRCA sheet steel of 2mm thickness and duly powder coated, front openable & accessible, all doors shall be provided with high quality neoprene rubber gasket, door interlock, emergency stop button(s), enclosure of the panel shall be minimum IP-42 & suitable for operation on 415 volts, 3 Phase, 50Hz AC supply i/c earthing, connections and comprising of the following components as required suitable for Arrival Carousel Baggage Handling System.
2.01 | INCOMER:415 Volts, TPN, MCCB with breaking capacity of 25 KA (Ics=100% Icu) with over load & short circuit protection. The rating of the MCCB shall be so selected that only about 80% of its full current carrying is utilized for meeting the requirement of the specific application. Protections : i) Single Phase protection ii) Phase reversal protection iii) Under voltage protection. Indication lamps (LED type) for R, Y, B and Power 'ON' with suitable rating protection MCBs. Metering : a) Digital type Ammeter of required range with selector switch & required nos and ratings of current Transformers. b) Digital type Voltmeter with selector switch and protection MCB. Required Surge protection device (70 KA minimum with Neutral protection) OUTGOINGS: i) For Motor : Two/Four pole MPCB of suitable current rating & breaking capacity of 10 KA (min) and Soft starter for each conveyor motor. (ii) For Rolling Shutter : i) Two/Four Pole MPCB of suitable current rating & breaking capacity of 10 KA for each shutter motor, (ii) interlocking with conveyor & limit switches / sensors, (iii) Auto-Manual switches, separate push button for UP/DOWN movement etc | 1.00 | Each |  | 250000.00 | 250000.00 | 165000.00 | 165000.00 | 175000.00 | 175000.00 | 380000.00 | 380000.00 | 165000.00 | PREMIER ENGINEERING TECHNICS PVT. LTD.
3.00 | GRAVITY ROLLER CONVEYOR Design, Supply, Installation, Testing & Commissioning of feeding gravity rollers of suitable length and in convenient sections as per site requirements with roller capacity of 35 kg per linear meter, 60/65 mm pitch/ dia or as per manufacturers recommendation, width section 1000 mm and height suitably matched and sloped, complete in all respect including conveyor frame section, rollers, supports including cutting & drilling of holes, equipment grouting etc. complete as per attached technical specifications and site requirements. | 3.00 | Meter |  | 35000.00 | 105000.00 | 45000.00 | 135000.00 | 33750.00 | 101250.00 | 30000.00 | 90000.00 | 90000.00 | Fox Solutions Private Limited
4.00 | DRAUGHT CURTAIN : Supply, Installation, Testing & Commissioning of Draught curtain for the wall opening of conveyor belt, of suitable size fabricated with 3mm thick Nylon Rubber flaps, to be fixed by SS flat strip as per size of shutter opening etc.complete as required as per attached technical specifications and site requirements. | 2.00 | Each |  | 10000.00 | 20000.00 | 8500.00 | 17000.00 | 8000.00 | 16000.00 | 5000.00 | 10000.00 | 10000.00 | Fox Solutions Private Limited
5.00 | ELECTRICALLY OPERATED ROLLING SHUTTER : Supply, Installation, Testing & Commissioning of Electrically operated rolling shutter with arrangement for auto and manual operation to suit the opening in wall, fabricated out of mild steel duly powder coated and provided with suitable rated tubular geared single phase motor directly coupled to the shaft of the shutter, limit switch or sensor interlock with conveyor starter, complete with guide channels, wiring, earthing, painting etc. as required for the successful operation of the shutter complete as required as per attached technical specifications and site requirements suitable for minimum opening size of 1500mm (L) X 1350mm (W). | 2.00 | Each |  | 60000.00 | 120000.00 | 135000.00 | 270000.00 | 75000.00 | 150000.00 | 50000.00 | 100000.00 | 100000.00 | Fox Solutions Private Limited
6.00 | SUPPLY OF POWER CABLE Supply of XLPE insulated and PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade of following sizes conforming to IS-7098 (Part-1) :1988 with upto date amendments etc complete as required.
6.01 | 3.5C x 35 Sq.mm | 200.00 | Mtr |  | 300.00 | 60000.00 | 230.00 | 46000.00 | 367.92 | 73584.00 | 3500.00 | 700000.00 | 46000.00 | PREMIER ENGINEERING TECHNICS PVT. LTD.
7.00 | LAYING OF POWER CABLE Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of size upto 35 Sqm through existing cladded structure using suitable clamping arrangement including removal of existing Aluminium cladding & closing after laying the cable, providing suitable sealants wherever as required | 200.00 | Meter |  | 100.00 | 20000.00 | 250.00 | 50000.00 | 250.00 | 50000.00 | 90.00 | 18000.00 | 18000.00 | Fox Solutions Private Limited
8.00 | END TERMINATION Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor power cable of 1.1 KV grade as required. 3.5C x 35 Sq.mm | 3.00 | Set |  | 300.00 | 900.00 | 750.00 | 2250.00 | 2000.00 | 6000.00 | 350.00 | 1050.00 | 900.00 | GANNON DUNKERLEY AND CO LTD
9.00 | GI EARTH WIRE Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 400.00 | Meter |  | 12.00 | 4800.00 | 15.00 | 6000.00 | 25.00 | 10000.00 | 90.00 | 36000.00 | 4800.00 | GANNON DUNKERLEY AND CO LTD
10.00 | SH:-II: AICMC FOR FIVE YEARS (AFTER COMPLETION OF DLP OF TWO YEARS) All Inclusive Comprehensive Maintenance (AICMC) of the Arrival Carousel Baggage Handling System as covered under SH - I including carrying out preventive maintenance (Quarterly basis), trouble shooting and break down maintenance (whenever required) complete with all spares, consumables, required manpower for servicing/repair etc. as per the recommendations of the manufacturer and as per the instructions of Engineer incharge, standard engineering practice and as per attached special conditions for maintaining the above systems in acceptable functional, operational and serviceable condition.
10.01 | First Year (After completion of DLP of 02 years) | 1.00 | Year |  | 150000.00 | 117270.00 | 216100.00 | 168946.98 | 403069.84 | 315120.00 | 150000.00 | 117270.00 | 117270.00 | Fox Solutions Private Limited, GANNON DUNKERLEY AND CO LTD
10.02 | Second Year (After completion of DLP of 02 years) | 1.00 | Year |  | 165000.00 | 118833.00 | 224800.00 | 161900.96 | 468173.29 | 337178.40 | 150000.00 | 108030.00 | 108030.00 | Fox Solutions Private Limited
10.03 | Third Year (After completion of DLP of 02 years) | 1.00 | Year |  | 181500.00 | 120425.25 | 233800.00 | 155126.30 | 543754.16 | 360780.89 | 130000.00 | 86255.00 | 86255.00 | Fox Solutions Private Limited
10.04 | Fourth Year (After completion of DLP of 02 years) | 1.00 | Year |  | 199650.00 | 122046.04 | 243200.00 | 148668.16 | 631499.75 | 386035.80 | 130000.00 | 79469.00 | 79469.00 | Fox Solutions Private Limited
10.05 | Fifth Year (After completion of DLP of 02 years) | 1.00 | Year |  | 219615.00 | 123665.21 | 253000.00 | 142464.30 | 733542.96 | 413058.04 | 130000.00 | 73203.00 | 73203.00 | Fox Solutions Private Limited
11.00 | Note : 1. Rate quoted shall be inclusive of all taxes, duties, cess, fee, royalty charges etc. levied under any statute but exclusive of Goods & Services Tax (GST), which shall be paid to the contractor for any taxable supply / services / works against a valid tax invoice as per terms and conditions of the contract. 2. For further details of BOQ please refer tender document.
| Total in Figures |  |  |  |  | 3607939.50 |  | 4378356.70 |  | 4394632.13 |  | 3599276.90
Lowest Amount Quoted BY: Fox Solutions Private Limited(3599276.90)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Baggage Handling System Tender ID: 2023_AAI_169832_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Fox Solutions Private Limited | 3599276.90 | L1
| 2 | GANNON DUNKERLEY AND CO LTD | 3607939.50 | L2
| 3 | PREMIER ENGINEERING TECHNICS PVT. LTD. | 4378356.70 | L3
| 4 | DElite System Engineering (India) Pvt. Ltd. | 4394632.13 | L4