## BoQ1
Government eProcurement System Created By: ANGELO J LAWRENCE Created Date/Time: 26-Oct-2023 05:10 PM Tender Title: Up-gradation of Passenger Terminal Building and Airside Facilities at Trichy International Airport. S.H. Miscellaneous Electrical Works. Tender ID: 2023_AAI_169861_1
Tender Inviting Authority: Asst. General Manager (Engg-E)
Name of Work: UP GRADATION OF PASSENGER TERMINAL BUILDING AND AIRSIDE FACILITIES AT TIRUCHIRAPPALLI (TRICHY) INTERNATIONAL AIRPORT. SH: MISCELLANEOUS ELECTRICAL WORKS.
Contract No: AAI/TRY/ENGG (E)/PROJECT-MIS/23 Tender ID: : 2023_AAI_169861_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | Manish Electricals(GSTN-23ABLPM9012E1ZW) |  | Edge Telecom Pvt Ltd(GSTN-NA) |  | LAKSHMI ELECTRICAL WORKS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Installation of LED slim type Sign boards size of 1300mm x 700mm x 200mm on New NITB airside at height of 6mts including providing supporting arrangment with painted M.S angle from the existing supporting concrete /steel beam ( suitable to withstand weight of 20Kg) , including supply & fixing loopin loopout polycorbanate Junction Box of size (90 x90 x52) mm with connector , 6A MCB SP with suitable double compressor gland for looping cables of 4Cx16sqmm size & PVC gland for Sign board connecting cable on wall/Surface area ,including, fixing, welding ,accessories ,and civil works if necessary (LED sign boards shall be supplied by AAI). | 5.00 | Job |  | 8999.00 | 44995.00 | 35000.00 | 175000.00 | 70000.00 | 350000.00 | 1550.00 | 7750.00 | 7750.00 | LAKSHMI ELECTRICAL WORKS
2.00 | Supply and Fixing of Single phase, 230V Digital timer with inbult override facility in Existing highmast sub feeder panel including DIN RAIL,Wiring, connections and Accessories etc. | 13.00 | Nos |  | 2499.00 | 32487.00 | 4000.00 | 52000.00 | 18000.00 | 234000.00 | 1950.00 | 25350.00 | 25350.00 | LAKSHMI ELECTRICAL WORKS
3.00 | Supply and fixing of LED highbay downlight luminaries, IP65,, having minimum lumen output of 8250 lm, system efficacy not less than 110 lumen/watt, control driver with more than 4kV surge suppressor, made up of pressure die cast aluminum alloy housing with toughened glass/tempered protective custom moulded poly carponate diffuser fixed to the housing with SS screws, powered by built in potted, isolated electronic LED driver, suitable to operate on single phase, 50HZ AC supply i/c. provision og suitable clamps, interconnection with 3Cx2.5 PVC insulated flexible copper cable with PVC gland as per site condition, including providing poly carbonate loop-in & loop-out box with 16 Sq.mm connected. meeting with requirements specified in the technical specification. | 30.00 | Nos |  | 6499.00 | 194970.00 | 6500.00 | 195000.00 | 7500.00 | 225000.00 | 5900.00 | 177000.00 | 177000.00 | LAKSHMI ELECTRICAL WORKS
4.00 | Supply, Installation, Testing and Commissioning of 60 KVA UPS rated high performance IGBT based PWM technology (three phase Input & three phase Output) online UPS system suitable for input and output parameters as per input THDI < 3%, input power factor <0.99, output power factor 0.9 to 1.0, efficiency 95%, True Online Double Conversion (VFI SS 111 as per IEC 62040-3) ,3 phase input (415 V ± 10% , 50 Hz ± 5% ), and three phase output (415 V ± 3%, 50 Hz ± 1%) with 30 minutes battery backup. The UPS shall have Galvanic Isolation Transformer Inbuilt/External K13 rated copper Wound (After Static Switch) transformer. The UPS shall be made of MS sheet 2mm thick, provided in powder coated fan cooled enclosure painted in colour as per specifications. The UPS shall be suitable for normal, emergency, recharge, by-pass and maintenance mode including bypass arrangement. The Static Bypass Module should be 100% fully rated and suitable terminal box for cables entry from top. The UPS shall have a microprocessor based display and control panel with protections, inbuilt pase reversal protection, Digital Display to monitor & control the various Parameter, Inbuilt static bypass module at the bypass line. Complete system must be provided as per specifications approved drawing and as per site requirement including inter connecting cables from battery to UPS, UPS to panel with single core copper cabling etc. UPS shall work on parallel/ hot redundancy mode, cost of supporting kit shall be included. supports for complete system as approved by the Engineer in charge complete in all respect. | 2.00 | Nos |  | 1149999.00 | 2299998.00 | 1500000.00 | 3000000.00 | 600000.00 | 1200000.00 | 1099700.00 | 2199400.00 | 1200000.00 | Edge Telecom Pvt Ltd
5.00 | Execution of items of schedule of rates CPWD DSR-2022 of internal electrical installations as per direction of E-I-C at different locations as per the special Terms and Conditions in addition to General Terms and Conditions of Contract as required. The bidder shall quote the rate for 01 (one) job corresponding to the value of Rs.15,00,000/- (Ex.GST) in INR only and percentage (%) above / below shall be calculated by AAI and paid accordingly. Note: The rate provided in DSR 2022 is inclusive of GST @12%, however the contractor has to quote the amount in rate column, excluding GST, the payment shall be made to contractor as mentioned in special conditions of tender document. | 1.00 | Job |  | 1575000.00 | 1575000.00 | 1400000.00 | 1400000.00 | 1000000.00 | 1000000.00 | 1425000.00 | 1425000.00 | 1000000.00 | Edge Telecom Pvt Ltd
6.00 | Execution of items of schedule of rates CPWD DSR-2022 of External electrical installations as per direction of E-I-C at different locations as per the special Terms and Conditions in addition to General Terms and Conditions of Contract as required. The bidder shall quote the rate for 01 (one) job corresponding to the value of Rs.15,00,000/- (Ex.GST) in INR only and percentage (%) above / below shall be calculated by AAI and paid accordingly. Note: The rate provided in DSR 2022 is inclusive of GST @12%, however the contractor has to quote the amount in rate column, excluding GST, the payment shall be made to contractor as mentioned in special conditions of tender document. | 1.00 | Job |  | 1575000.00 | 1575000.00 | 1400000.00 | 1400000.00 | 1000000.00 | 1000000.00 | 1425000.00 | 1425000.00 | 1000000.00 | Edge Telecom Pvt Ltd
7.00 | Supply, Installation, Testing and Commissioning of Variable Refrigerant Flow type multi unit air-conditioning system complete with indoor and outdoor units with individual controller for cooling & heating application as per the specifications.
7.01 | OUTDOOR UNITS "Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type outdoor units, each comprising of energy efficient multiple scroll compressors, topping up of R410A refrigerant gas and all accessories as per the specifications. The condensing units shall be suitable to work on cooling as well as heating mode. The condensing units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply and complete with auto check function for connection error, auto address setting, etc. The outdoor units shall be low noise type. The outdoor units shall be of following capacities :" 14 HP nominal capacity high COP outdoor unit comprising of 1 modules of requisite capacity | 1.00 | Nos |  | 409999.00 | 409999.00 | 35000.00 | 35000.00 | 275000.00 | 275000.00 | 283350.00 | 283350.00 | 35000.00 | Manish Electricals
7.02 | INDOOR UNITS Supply, Installation, testing and commissioning of following type of Indoor Units for variable refrigerant Volume/ flow airconditioning system suitable for 220 ± 10 % volt, 50 Hz, 1 phase AC supply equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section, internally insulated outer cabinet, insulated drain pan, insulation, pipe connections etc. complete with PVC insulated FRLS copper conductor electric wire upto 1.5 metre length & sockets etc. as per m specifications and as required. 3.3 TR Ceiling Mounted Type 4-way Cassette Unit with cordless remote control, drain pump complete with fittings etc | 3.00 | Nos |  | 53999.00 | 161997.00 | 30000.00 | 90000.00 | 58000.00 | 174000.00 | 46400.00 | 139200.00 | 90000.00 | Manish Electricals
7.03 | Refrigerant Piping Supply & Installation of interconnecting 28.6 mm dia with 19 mm thick insulation (As per Specifications) of one end expanded refrigerant copper pipe work of following outer diameter, insulated with 19/13 mm thick insulation (as per Specifications) between each set of indoor & outdoor units with outer mechanical protection of aluminium cladding for all exposed pipes as per specification. All piping inside the room shall be properly fixed/supported with suitable size of clamp/M/S. hanger and all external piping shall run in M.S. painted cable tray (separate item) etc. as reqd. | 30.00 | Mtrs |  | 3999.00 | 119970.00 | 650.00 | 19500.00 | 1200.00 | 36000.00 | 2350.00 | 70500.00 | 19500.00 | Manish Electricals
7.04 | Supply, Installation, testing and commissioning of necessary fittings, Y-joints and headers etc. | 2.00 | Nos |  | 5999.00 | 11998.00 | 10000.00 | 20000.00 | 35000.00 | 70000.00 | 9375.00 | 18750.00 | 11998.00 | CHENNAI ENGINEERING SERVICES
7.05 | Supplying, fixing, testing and commissioning of Main centralized controller Push Button Type suitable for groups of indoor units to be installed for control. (BMS Compatible) | 1.00 | Nos |  | 59999.00 | 59999.00 | 5000.00 | 5000.00 | 50000.00 | 50000.00 | 27150.00 | 27150.00 | 5000.00 | Manish Electricals
8.00 | Supply of 1.5TR ,above ISEER 4.5, Split Type Air Conditioners, Invertor with 5 Star Rating, fitted with Hermetically Sealed or Rotary or Scroll or Reciprocating Compressors, Operating on Refriegerant eco friendly green gas suitable for wall mounting , Conforming to IS suitable for operation on 230 V. 50 Hz. Single Phase, AC Supply capable of performing, Dehumidifying, Air Circulating, Filtering, drain and including supply of refrigerant pipe and drain pipe as per OEM standard length , Outdoor Unit support stand as per site requirement. | 10.00 | Nos |  | 39999.00 | 399990.00 | 36000.00 | 360000.00 | 49000.00 | 490000.00 | 38800.00 | 388000.00 | 360000.00 | Manish Electricals
9.00 | Supplying of Wall Mounting Type, 4KVA Capacity, single phase, automatic line voltage stabilzer, suitable operation on 170 volts to 270 volts AC input, 200 volts to 240 volts AC output, single phase, 50HZ AC power supply with built in time delay, high voltage cut off at 275, and low voltage cut off at 165 volts and input,outputand trip indications and suitable for application of 1.5 Ton Air conditioning unit etc as required. | 10.00 | Nos |  | 1999.00 | 19990.00 | 5000.00 | 50000.00 | 6000.00 | 60000.00 | 1600.00 | 16000.00 | 16000.00 | LAKSHMI ELECTRICAL WORKS
10.00 | Installation , Testing & Commissioning of Split AC 1.5 TR including wall cutting, hole cutting, plastering and making wall good condition, fixing of outdoor with stand, stablizer and electrical connection with wire, complete as required. | 10.00 | Jobs |  | 949.00 | 9490.00 | 3000.00 | 30000.00 | 6800.00 | 68000.00 | 2700.00 | 27000.00 | 9490.00 | CHENNAI ENGINEERING SERVICES
11.00 | Supply and fixing of CPRI tested, ISI marked, Class A Electrical insulation mat having minimum thickness of 2mm working voltage upto 3.3kV, confirming to IS: 15652:2006, infront of LT panels. | 320.00 | Sq.mtr |  | 699.00 | 223680.00 | 700.00 | 224000.00 | 2200.00 | 704000.00 | 445.00 | 142400.00 | 142400.00 | LAKSHMI ELECTRICAL WORKS
12.00 | Supply and fixing of CPRI tested, ISI marked, Class B Electrical insulation mat having minimum thickness of 2.5 mm working voltage upto 11 kV, confirming to IS: 15652:2006, in front of HT panels, transformer rooms | 50.00 | Sq.mtr |  | 1099.00 | 54950.00 | 900.00 | 45000.00 | 1900.00 | 95000.00 | 550.00 | 27500.00 | 27500.00 | LAKSHMI ELECTRICAL WORKS
13.00 | Supply and fixing of CPRI tested, ISI marked, Class C Electrical insulation mat having minimum thickness of 3 mm working voltage upto 33 kV, confirming to IS: 15652:2006, infront of HT panels, transformer rooms | 40.00 | Sq.mtr |  | 1149.00 | 45960.00 | 1100.00 | 44000.00 | 1800.00 | 72000.00 | 655.00 | 26200.00 | 26200.00 | LAKSHMI ELECTRICAL WORKS
14.00 | Design, fabrication, assembly, wiring and supply, erection , testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of --kA (specified with the panel) at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, paint finish of approved shade over metal surface cleaned and treated with nine tank process complete with interconnections etc. as per specifications, as required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5sq.mm & 2.5sq.mm for CT's etc. complete as required as per specifications and drawing attached. Incomers: i) 2 No. 250Amps. 4P MCCB '25ka, Icu=Ics with microprocessor based release having O/L ,S/C, earth fault protection equipped with the following: a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF' indicating light with 2A MCB Digital Multifunction Meter, accuracy class 0.5s, with LED/LCD screen of Max Demand Load, I ;V; Hz; Active, Reactive , Apparent Power & Energy; Power factor; % unbalance of current & voltage; , %THD , individual harmonics up to 15th level (complying with IEC61557-12) with RS 485 / Ethernet port with 3 Nos. cast resin current transformers of suitable Amp. ratio, 15 VA metering. ,protection MCBs as required accessories to complete the system. Electrical Interlocking should be provided to ensure healthy supply available at a time. Bus Bar : TPN aluminium extensible type main bus bars of minimum of 300 Amp capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bars supports at required intervals complete. Outgoings: All outgoing with thermal magnetic based adjustable release MCCB with front operating handle for O/C, S/C protection of following capacity and rating, 25 KA (Ics=Icu upto 433 V ) with Set of Digital flush type calibrated KWH meters suitable rating class - 1.0 accuracy , showing KW with 3 Nos. cast resin current transformers of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc. 3 Nos. - 200 Amp. TPN, MCCB 25kA with 'ON' LED indication lamps backed up with 2Amp back up control MCB | 1.00 | Nos |  | 279999.00 | 279999.00 | 350000.00 | 350000.00 | 220000.00 | 220000.00 | 250000.00 | 250000.00 | 220000.00 | Edge Telecom Pvt Ltd
15.00 | Design, fabrication, assembly, wiring and supply, erection , testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of --kA (specified with the panel) at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, paint finish of approved shade over metal surface cleaned and treated with nine tank process complete with interconnections etc. as per specifications, as required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5sq.mm & 2.5sq.mm for CT's etc. complete as required as per specifications and drawing attached. Incomers: i) 160 Amp 4 pole MCCB- 2 set , 2 Nos of 160 Amps. 4P MCCB '25ka, Icu=Ics with micro processor based release having O/ L,S/ C earth fault protection & necessary electrical and mechnical interlocking arrangement between three nos of incomers & two nos of bus coupler equipped with the following: a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/ OFF/ TRIP' indicating lamp with 2A MCB Digital Multifunction Meter, accuracy class 0.5s, with LED/ LCD screen of Max Demand Load, I ;V; Hz; Active, Reactive, Apparent Power & Energy; Power factor; % unbalance of current & voltage;, %THD, individual harmonics up to 15th level (complying with IEC: 61557-12) with RS 485 / Ethernet port with 3 Nos. cast resin current transformers of suitable Amp. ratio, 15 VA metering., protection MCBs as required accessories to complete the system. Bus Bar : 2 sections of TPN copper with 100% Neutral extensible type main bus bars of minimum of 300 Amp 25kA capacity with heat shrinkable coloured sleeves and i/ c DMC/ SMC bus bars supports at required intervals complete. Bus couplers: i) 1 No. 160 Amps. 4P MCCB '25ka, Icu=Ics with O/ L,S/ C protection with ON / OFF/ TRIP Indication lamp with 2A MCB Outgoings: All outgoing MCCB shall be thermal magnetic with with front operating handle for O/ C, S/ C protection of following capacity and rating minimum 25kA (Ics=Icu =100% 433 V) with front operating handle, Spreader links and phase barrier, solid neutral link complete with wiring, connections etc. i) 4 Nos. - 100 Amp. TPN MCCB with ON/OFF indicating lamp with 2A MCB. Ii) 2 Nos. - 63 Amp. TPN MCCB with ON/OFF indicating lamp with 2A MCB. | 1.00 | Nos |  | 286999.00 | 286999.00 | 225000.00 | 225000.00 | 220000.00 | 220000.00 | 300000.00 | 300000.00 | 220000.00 | Edge Telecom Pvt Ltd
| Total in Figures |  |  |  |  | 7807471.00 |  | 7719500.00 |  | 6543000.00 |  | 6975550.00
Lowest Amount Quoted BY: Edge Telecom Pvt Ltd(6543000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Up-gradation of Passenger Terminal Building and Airside Facilities at Trichy International Airport. S.H. Miscellaneous Electrical Works. Tender ID: 2023_AAI_169861_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Edge Telecom Pvt Ltd | 6543000.00 | L1
| 2 | LAKSHMI ELECTRICAL WORKS | 6975550.00 | L2
| 3 | Manish Electricals | 7719500.00 | L3
| 4 | CHENNAI ENGINEERING SERVICES | 7807471.00 | L4