## BoQ1
Government eProcurement System Created By: SYED TANWEER ASHRAF Created Date/Time: 14-Nov-2023 04:10 PM Tender Title: Supply and Laying of Cable to Nav Aids sites CISF Barrack and other associated works at Gaya Airport Gaya. Tender ID: 2023_AAI_169933_1
Tender Inviting Authority: <AGM ( Engg. Elect), AAI, Gaya Airport, Gaya>
Name of Work: <Supply & Laying of Cables to Nav Aids sites, CISF Barrack & other associated works at Gaya Airport, Gaya.>
Contract No: <0631-2210043>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | M/S AMAR ENTERPRISES(GSTN-20AAMFA2722R1ZE) |  | GIRI ENTERPRISES(GSTN-20ACEPG3920H1ZA) |  | Mukherjee Commercial Enterprise(GSTN-19ALVPM0307N1ZJ) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following. XLPE insulated PVC sheathed armoured aluminium conductor cable of 1.1 KV Grade confirming to IS:7098 (Part 1) with upto date amendment etc. complete as required. |  |  | 263.00
1.10 | 3.5 Core x 150 Sq.mm | 2000.00 | Meter | 263.00 | 540.00 | 1080000.00 | 600.00 | 1200000.00 | 600.00 | 1200000.00 | 795.00 | 1590000.00 | 570.00 | 1140000.00 | 1080000.00 | DOSHI ELECTRIC ENGG. CO.
1.20 | 3.5 Core x 185 Sq.mm | 1200.00 | Meter | 263.00 | 680.00 | 816000.00 | 750.00 | 900000.00 | 750.00 | 900000.00 | 995.00 | 1194000.00 | 720.00 | 864000.00 | 816000.00 | DOSHI ELECTRIC ENGG. CO.
2.00 | Laying of one number PVC insulated and PVC sheathed XLPE power cable of 1.1kV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required. |  |  | 263.00
2.10 | Above 95 sq. mm and upto 185 sq. mm | 1800.00 | Meter | 263.00 | 325.00 | 585000.00 | 200.00 | 360000.00 | 500.00 | 900000.00 | 250.00 | 450000.00 | 310.00 | 558000.00 | 360000.00 | M/S AMAR ENTERPRISES
3.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of l.l KV grade of following size in the existing RCC/ HUME/METAL/HDPE pipe as required. |  |  | 263.00
3.10 | Above 95 sq. mm and upto 185 sq. mm | 250.00 | Meter | 263.00 | 40.00 | 10000.00 | 30.00 | 7500.00 | 100.00 | 25000.00 | 100.00 | 25000.00 | 90.00 | 22500.00 | 7500.00 | M/S AMAR ENTERPRISES
3.20 | Upto 35 sq. mm | 200.00 | Meter | 263.00 | 30.00 | 6000.00 | 50.00 | 10000.00 | 50.00 | 10000.00 | 50.00 | 10000.00 | 60.00 | 12000.00 | 6000.00 | DOSHI ELECTRIC ENGG. CO.
4.00 | Laying of one number PVC insulated and PVC sheathed i XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. |  |  | 263.00
4.10 | Above 95 sq. mm and upto 185 sq. mm | 90.00 | Meter | 263.00 | 40.00 | 3600.00 | 20.00 | 1800.00 | 50.00 | 4500.00 | 50.00 | 4500.00 | 40.00 | 3600.00 | 1800.00 | M/S AMAR ENTERPRISES
4.20 | Upto 35 sq. mm | 50.00 | Meter | 263.00 | 30.00 | 1500.00 | 20.00 | 1000.00 | 50.00 | 2500.00 | 30.00 | 1500.00 | 40.00 | 2000.00 | 1000.00 | M/S AMAR ENTERPRISES
5.00 | Laying & Fixing of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required
5.10 | Upto 35 sq. mm | 100.00 | Meter | 263.00 | 100.00 | 10000.00 | 50.00 | 5000.00 | 50.00 | 5000.00 | 80.00 | 8000.00 | 125.00 | 12500.00 | 5000.00 | M/S AMAR ENTERPRISES, GIRI ENTERPRISES
6.00 | Laying & Fixing of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required
6.10 | Upto 35 sq. mm | 50.00 | Meter | 263.00 | 70.00 | 3500.00 | 100.00 | 5000.00 | 50.00 | 2500.00 | 30.00 | 1500.00 | 135.00 | 6750.00 | 1500.00 | Mukherjee Commercial Enterprise
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required |  |  | 263.00
7.10 | 3.5 X 150sq. mm | 4.00 | Set | 263.00 | 700.00 | 2800.00 | 1000.00 | 4000.00 | 800.00 | 3200.00 | 900.00 | 3600.00 | 750.00 | 3000.00 | 2800.00 | DOSHI ELECTRIC ENGG. CO.
7.20 | 3.5 X 185sq. mm | 2.00 | Set | 263.00 | 800.00 | 1600.00 | 1500.00 | 3000.00 | 1000.00 | 2000.00 | 1000.00 | 2000.00 | 850.00 | 1700.00 | 1600.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. |  |  | 263.00
8.10 | 4 C X 25 sq mm | 4.00 | Set | 263.00 | 400.00 | 1600.00 | 500.00 | 2000.00 | 200.00 | 800.00 | 600.00 | 2400.00 | 550.00 | 2200.00 | 800.00 | GIRI ENTERPRISES
9.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required |  |  | 263.00
9.10 | 3.5 X 150 sq. mm | 2.00 | Each | 263.00 | 3500.00 | 7000.00 | 4000.00 | 8000.00 | 10000.00 | 20000.00 | 6000.00 | 12000.00 | 3500.00 | 7000.00 | 7000.00 | DOSHI ELECTRIC ENGG. CO., Awasthi Electric Works
9.20 | 3.5 X 185 sq. mm | 1.00 | Each | 263.00 | 4000.00 | 4000.00 | 5000.00 | 5000.00 | 12000.00 | 12000.00 | 7500.00 | 7500.00 | 3500.00 | 3500.00 | 3500.00 | Awasthi Electric Works
10.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement: 2 coarse: 4 graded stone aggregate 20 mm nominal size) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10 cm including inscription. | 4.00 | Each | 263.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 800.00 | 3200.00 | 1200.00 | 4800.00 | 700.00 | 2800.00 | 1200.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Cutting the bituminous road of up to 15 cm width and 40 cm depth with help of suitable tools & plants / manpower and disposal of debris up to 300 mtrs suitable for laying of upto 100mm dia GI Pipe etc complete as required. | 45.00 | Meter | 263.00 | 200.00 | 9000.00 | 1000.00 | 45000.00 | 500.00 | 22500.00 | 2000.00 | 90000.00 | 400.00 | 18000.00 | 9000.00 | DOSHI ELECTRIC ENGG. CO.
12.00 | Providing and laying following size medium class GI pipe in the existing excavated trench for road/drain crossings with accessories etc. complete as required. |  |  | 263.00
12.10 | 80 mm dia | 45.00 | Meter | 263.00 | 900.00 | 40500.00 | 900.00 | 40500.00 | 1200.00 | 54000.00 | 900.00 | 40500.00 | 900.00 | 40500.00 | 40500.00 | DOSHI ELECTRIC ENGG. CO., M/S AMAR ENTERPRISES, Mukherjee Commercial Enterprise, Awasthi Electric Works
13.00 | Making good the excavated trenches at road crossing, drain crossings or on paved surfaces by providing and layiing cement concrete of grade 1:3:6 (1 cement:3 coarse sand: 6graded stone of aggregate 20mn nominal size). | 3.00 | Cu mtr. | 263.00 | 7000.00 | 21000.00 | 3500.00 | 10500.00 | 7000.00 | 21000.00 | 5000.00 | 15000.00 | 8000.00 | 24000.00 | 10500.00 | M/S AMAR ENTERPRISES
14.00 | Design, manufacture Supply, Installation, Testing and Commissioning of TTA type LT panel, cubicle type, front openable, made of 2 mm thick sheet steel, totally enclosed, IP 52, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, interconnections including supply & installation of following items and as per Technical specification INCOMER 2 Nos. 400 A , FP, 50 kA,motor wound spring charged closing mechanism,drawout type ACB with Microprocessor based release having short circuit, over current, earth fault, zone selective interlocking features with communication port RS 485 (Ics=100%Icu) 2 nos. Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility ( RS485 port ) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses/MCBs. 2 nos. Digital Voltmeter suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of HRC control fuses/MCBs. 2 Sets Indication Lamps (1 Set for each ACB), LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' lamps 2 nos. Digital Ammeter of suitable range (to measure 0-500A), for 3 phase 4 wire operation with LED display and selector switch and CT ratio programmable and auto ranging along with 3 nubmers of class 1.0, 15 VA suitable range CTs. Bus Bars 01 set of Bus bars, 500 Amps, TPN, Aluminium Bus bars Bus coupler 400A FP, 50 kA, motor wound spring charged closing mechanism,drawout type ACB with Microprocessor based release having short circuit, over current, earth fault zone selective interlocking features with communication port RS 485.- 1 No. (Ics=100%Icu) Indication Lamps, LED type 'ON' , 'OFF', 'TRIP' lamps with HRC control fuses/MCBs etc for bus coupler Accessories for Electrical Interlocking Accessories for electrical & Mechanical interlocking among 2 Nos Incomers and Bus coupler as required shall be provided including interconnection etc as required. Outgoing 4 Nos. MCCB, 250 A, 50 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100%Icu) 8 Nos. MCCB, 125 A, 36 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100%Icu) 4 Nos. MCCB, 63 A, 25 kA, Four Pole , with Thermal magnetic release(Ics=100 %Icu) 16 nos. Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility ( RS485 port ) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC Control fuses/MCBs. 16 Sets (1 set for each MCCB) of Extended Rotary operating mechanism, terminal extension spreaders and 'ON' (Red) indication lamp (LED type) with HRC control fuse/MCBs Suitable rating 65 KA class B SPDs for each incomer, 100 mm x 50 mm x 5mm thick base frame channel for the panel & any other provisions / components & accessories etc as required for proper operation , control , protection etc as required. | 1.00 | Set | 263.00 | 1850000.00 | 1850000.00 | 1900000.00 | 1900000.00 | 1100000.00 | 1100000.00 | 1320000.00 | 1320000.00 | 2065000.00 | 2065000.00 | 1100000.00 | GIRI ENTERPRISES
15.00 | Making horizontal boring by HDD method suitable for laying of HDPE Pipe upto the OD of 160 mm at a min. depth of at least 1.2 meter below the common ground surface level i/c connecting,drawing & laying of HDPE Pipe etc complete as required ( Supply of HDPE pipe not included). | 1100.00 | Mtr. | 263.00 | 200.00 | 220000.00 | 550.00 | 605000.00 | 700.00 | 770000.00 | 500.00 | 550000.00 | 600.00 | 660000.00 | 220000.00 | DOSHI ELECTRIC ENGG. CO.
16.00 | Supply of HDPE Pipes of 110 mm dia as per IS:4984:2016 of Material Grade: PE 63 & Pressure Rating of PN 8 etc as required. | 1100.00 | Mtr. | 263.00 | 550.00 | 605000.00 | 450.00 | 495000.00 | 700.00 | 770000.00 | 850.00 | 935000.00 | 555.00 | 610500.00 | 495000.00 | M/S AMAR ENTERPRISES
17.00 | Earthing with GI earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 3.00 | Each | 263.00 | 6500.00 | 19500.00 | 6000.00 | 18000.00 | 15000.00 | 45000.00 | 8000.00 | 24000.00 | 9000.00 | 27000.00 | 18000.00 | M/S AMAR ENTERPRISES
18.00 | Providing· and fixing 25 mm X 5 mm· G.l. strip in 40 mm dia G.l. pipe from earth electrode including connection with G.l. nut, bolt, spring, washer excavation and refilling etc. as required. | 15.00 | Mtr. | 263.00 | 550.00 | 8250.00 | 500.00 | 7500.00 | 1000.00 | 15000.00 | 800.00 | 12000.00 | 590.00 | 8850.00 | 7500.00 | M/S AMAR ENTERPRISES
19.00 | Providing and fixing 25 mm X 5 mm G.l. strip on surface or in recess for connections etc. as required. | 20.00 | Mtr. | 263.00 | 150.00 | 3000.00 | 100.00 | 2000.00 | 400.00 | 8000.00 | 180.00 | 3600.00 | 165.00 | 3300.00 | 2000.00 | M/S AMAR ENTERPRISES
20.00 | Constructing masonary chamber 120 X 120 X 100 cm inside, in brick work with common burnt clay FPS bricks of class designation 7.5 in cement mortar 1:4 ( 1 cement : 4 coarse sand) and RCC top slab 1:2:4 mix ( 1 cement:2 coarse sand : 4 graded stone aggregate 20 mm nominal size), i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement:5 fine sand:10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 ( 1 cement : 3 coarse sand) 12 mm thick, finished with floating coat of neat cement complete as per standard design. | 4.00 | Job | 263.00 | 15000.00 | 60000.00 | 12000.00 | 48000.00 | 30000.00 | 120000.00 | 2000.00 | 8000.00 | 19000.00 | 76000.00 | 8000.00 | Mukherjee Commercial Enterprise
21.00 | Supplying and fixing of 4 pole 63 A Manual Changeover Switch complete with SS enclosure & extended rotary handle suitable for 02 Nos of incomers & 01 Nos of outgoing as required complete with making connections, mounting on wall/surface etc. as required and as instructed by Engineer-in-charge | 1.00 | Each | 263.00 | 7000.00 | 7000.00 | 10000.00 | 10000.00 | 6000.00 | 6000.00 | 15000.00 | 15000.00 | 7300.00 | 7300.00 | 6000.00 | GIRI ENTERPRISES
22.00 | Supplying & Fixing 63 A 4P " C curve" MCB, 415 V, 10 KA suitable for inductive load in metal sheet enclosure on surface or in recess complete with connection, testing & commisioning etc as required | 2.00 | Each | 263.00 | 3500.00 | 7000.00 | 2000.00 | 4000.00 | 3000.00 | 6000.00 | 5000.00 | 10000.00 | 2400.00 | 4800.00 | 4000.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 5384050.00 |  | 5699800.00 |  | 6028200.00 |  | 6339900.00 |  | 6186800.00
Lowest Amount Quoted BY: DOSHI ELECTRIC ENGG. CO.(5384050.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply and Laying of Cable to Nav Aids sites CISF Barrack and other associated works at Gaya Airport Gaya. Tender ID: 2023_AAI_169933_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DOSHI ELECTRIC ENGG. CO. | 5384050.00 | L1
| 2 | M/S AMAR ENTERPRISES | 5699800.00 | L2
| 3 | GIRI ENTERPRISES | 6028200.00 | L3
| 4 | Awasthi Electric Works | 6186800.00 | L4
| 5 | Mukherjee Commercial Enterprise | 6339900.00 | L5