## BoQ1
Government eProcurement System Created By: Amitabh Ranjan Created Date/Time: 30-Oct-2023 03:35 PM Tender Title: Supply and Replacement of cooling Tower for 300 TR chiller plant at Amritsar Airport Tender ID: 2023_AAI_170143_1
Tender Inviting Authority: <SM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Supply & Replacement of Cooling Tower for 300TR chiller plant at Amritsar Airport.>
Tender ID: <2023_AAI_ 170143 _1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Blue Star Limited(GSTN-04AAACB4487D1Z0) |  | VOLTAS LIMITED(GSTN-07AAACV2809D1ZO) |  | PROJENIX PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of FRP induced draft counter flow cooling tower each guaranteed to cool 1400 USGPM of water from 97.5°F to 90°F at a design wet bulb temperature of 83°F with FRP water basin, PVC fills with integral louvers and drift elimination, hot water distribution by gravity complete with statically and dynamically balanced axial flow, direct driven fans with TEFC induction motor suitable for operation on 415±10% volt, 50 Hz. AC supply, suction screen, make up with float valve and quick fill arrangement, overflow and drain connections, with necessary valves, suitable inspection ladders, access arrangement for cooling tower interior, steel supporting structure, anti-vibrating mountings, painting etc. complete as per specification. Heat Rejection capacity minimum 1325000 Kcal/hr (excluding concrete foundation). | 3.00 | Job |  | 949659.00 | 2848977.00 | 915636.00 | 2746908.00 | 775519.00 | 2326557.00 | 2326557.00 | PROJENIX PRIVATE LIMITED
2.00 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends,tees etc.but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
2.10 | 350 mm dia. | 80.00 | Mtr |  | 6622.00 | 529760.00 | 6732.00 | 538560.00 | 6348.00 | 507840.00 | 507840.00 | PROJENIX PRIVATE LIMITED
2.20 | 200 mm dia. | 50.00 | Mtr |  | 3865.00 | 193250.00 | 3861.00 | 193050.00 | 3795.00 | 189750.00 | 189750.00 | PROJENIX PRIVATE LIMITED
2.30 | 150 mm dia. | 18.00 | Mtr |  | 2502.00 | 45036.00 | 2544.00 | 45792.00 | 2547.00 | 45846.00 | 45036.00 | Blue Star Limited
2.40 | 100 mm dia. | 72.00 | Mtr |  | 1697.00 | 122184.00 | 1725.00 | 124200.00 | 1722.00 | 123984.00 | 122184.00 | Blue Star Limited
2.50 | 80 mm dia. | 9.00 | Mtr |  | 1191.00 | 10719.00 | 1194.00 | 10746.00 | 1220.00 | 10980.00 | 10719.00 | Blue Star Limited
2.60 | 50 mm dia. | 18.00 | Mtr |  | 757.00 | 13626.00 | 770.00 | 13860.00 | 775.00 | 13950.00 | 13626.00 | Blue Star Limited
3.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required.
3.10 | 100 mm dia. | 80.00 | Mtr |  | 1791.00 | 143280.00 | 1879.00 | 150320.00 | 746.00 | 59680.00 | 59680.00 | PROJENIX PRIVATE LIMITED
4.00 | Supply, Installation, Testing & Commissioning of following Valves, Strainers, in condenser water piping complete with companion flanges, nuts, bolts, gaskets, support etc and duly painted.
4.10 | Butterfly valves (CI body SS disc nitrile sheet & O ring & PN16 pressure rating as specified)
4.11 | 200mm dia. | 6.00 | Nos. |  | 10217.00 | 61302.00 | 15367.00 | 92202.00 | 10145.00 | 60870.00 | 60870.00 | PROJENIX PRIVATE LIMITED
4.12 | 100mm dia. | 3.00 | Nos. |  | 4364.00 | 13092.00 | 5280.00 | 15840.00 | 4334.00 | 13002.00 | 13002.00 | PROJENIX PRIVATE LIMITED
4.13 | 80mm dia. | 3.00 | Nos. |  | 3344.00 | 10032.00 | 4066.00 | 12198.00 | 3322.00 | 9966.00 | 9966.00 | PROJENIX PRIVATE LIMITED
4.14 | 50mm dia. | 3.00 | Nos. |  | 2628.00 | 7884.00 | 3122.00 | 9366.00 | 2614.00 | 7842.00 | 7842.00 | PROJENIX PRIVATE LIMITED
4.20 | Y strainer (Ductile CI body flanged ends with stainless steel strainer)
4.21 | 200mm dia. | 3.00 | Nos. |  | 24258.00 | 72774.00 | 27290.00 | 81870.00 | 23181.00 | 69543.00 | 69543.00 | PROJENIX PRIVATE LIMITED
5.00 | Supply of one number 3.5c x 25 sqmm armound aluminium PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade. | 500.00 | Mtr |  | 285.00 | 142500.00 | 185.00 | 92500.00 | 175.00 | 87500.00 | 87500.00 | PROJENIX PRIVATE LIMITED
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
6.10 | Upto 35 sq. mm | 165.00 | Mtr |  | 88.00 | 14520.00 | 138.00 | 22770.00 | 57.00 | 9405.00 | 9405.00 | PROJENIX PRIVATE LIMITED
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 180.00 | Mtr |  | 88.00 | 15840.00 | 138.00 | 24840.00 | 45.00 | 8100.00 | 8100.00 | PROJENIX PRIVATE LIMITED
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
8.10 | 3½ X 25 sq. mm (28mm) | 6.00 | Set |  | 1003.00 | 6018.00 | 1043.00 | 6258.00 | 735.00 | 4410.00 | 4410.00 | PROJENIX PRIVATE LIMITED
9.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
9.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 30.00 | Mtr |  | 482.00 | 14460.00 | 730.00 | 21900.00 | 441.00 | 13230.00 | 13230.00 | PROJENIX PRIVATE LIMITED
10.00 | Excavation of the trenches for pipe laying in hard rock / concrete road/ bitumine road not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 12.00 | Cum |  | 1253.00 | 15036.00 | 331.00 | 3972.00 | 5650.00 | 67800.00 | 3972.00 | VOLTAS LIMITED
11.00 | Providing and laying in position cement concrete of 1:2:4 (1 Cement: 2 coarse sand derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) including all cost for making concrete /bitumine road surface as required at site. | 10.00 | Cum |  | 6266.00 | 62660.00 | 14209.00 | 142090.00 | 5650.00 | 56500.00 | 56500.00 | PROJENIX PRIVATE LIMITED
12.00 | Supply & fixing of Iron support/re-inforcement bar for the cooling tower foundation & base frame fabrication as per OEM recomendation. | 3000.00 | Kg |  | 80.00 | 240000.00 | 126.70 | 380100.00 | 105.00 | 315000.00 | 240000.00 | Blue Star Limited
13.00 | Dismantling of old Euipments/Support/Accessories Dismantling of existing cooling towers pipe, valve, cable etc. and dump in AAI store yard. | 3.00 | Lot |  | 7519.00 | 22557.00 | 20654.00 | 61962.00 | 11300.00 | 33900.00 | 22557.00 | Blue Star Limited
14.00 | Providing and laying reinforced cement concrete 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) in foundation of cooling tower including shuttering, centering, funishing work etc complete as required (excluding reinforcement). | 15.00 | Cum |  | 7519.00 | 112785.00 | 10327.00 | 154905.00 | 11300.00 | 169500.00 | 112785.00 | Blue Star Limited
15.00 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material outside airport premises as per direction of Engineer - in- charge. | 12.00 | Cum |  | 1253.00 | 15036.00 | 11053.00 | 132636.00 | 1356.00 | 16272.00 | 15036.00 | Blue Star Limited
16.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 6266.00 | 25064.00 | 10288.00 | 41152.00 | 6215.00 | 24860.00 | 24860.00 | PROJENIX PRIVATE LIMITED
17.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 3.00 | Set |  | 4386.00 | 13158.00 | 9438.00 | 28314.00 | 5085.00 | 15255.00 | 13158.00 | Blue Star Limited
18.00 | Providing and fixing 25 mm X 5 mm G.I.strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 18.00 | Mtr |  | 514.00 | 9252.00 | 2136.00 | 38448.00 | 147.00 | 2646.00 | 2646.00 | PROJENIX PRIVATE LIMITED
19.00 | Providing and fixing 25 mm X5 mm G.I. strip on surface or in recess for connections etc. as required. | 18.00 | Mtr |  | 75.00 | 1350.00 | 247.00 | 4446.00 | 40.00 | 720.00 | 720.00 | PROJENIX PRIVATE LIMITED
| Total in Figures |  |  |  |  | 4782152.00 |  | 5191205.00 |  | 4264908.00
Lowest Amount Quoted BY: PROJENIX PRIVATE LIMITED(4264908.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply and Replacement of cooling Tower for 300 TR chiller plant at Amritsar Airport Tender ID: 2023_AAI_170143_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PROJENIX PRIVATE LIMITED | 4264908.00 | L1
| 2 | Blue Star Limited | 4782152.00 | L2
| 3 | VOLTAS LIMITED | 5191205.00 | L3