## BoQ1
Government eProcurement System Created By: KASI R Created Date/Time: 15-Dec-2023 11:43 AM Tender Title: Provision of power supply and bore well pumps for new bore wells at Coimbatore International Airport. Tender ID: 2023_AAI_172917_1
Tender Inviting Authority: Asst.Gen.Manager (E-E), Airports Authority of India, Coimbatore International Airport, Coimbatore - 641014.
Name of Work: Provision of power supply & bore well pumps for new bore wells at Coimbatore International Airport.
Tender ID: 2023_AAI_172917_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | C P MONCHESTER ELECTRICALS(GSTN-33AJOPP7842E1ZY) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Energy efficient Submersible borewell multi stage pump IP 68 class suitable to handle clear water for operation on S/D starter. Pump should be completely made of stainless Steel construction for pump, motor & impeller to avoid the corrosion formation & with motor diameter 6 inch or less. All bearings are water lubricated and suitably shaped bearings for sand flush, inlet strainer for prevents entering of particles , in-built non return valve for preventing back flow and reduce the water hammer, stop ring for prevents damage of the pump due to up-thrust load. Pump should coupled with high efficiency oil cooled/water cooled submersible motor with bearing for smooth operation. Motor should be re-windable type and shall be with temperature sensor for motor protection. Pump flow and head min: 12000 LPH / 250 LPM / 4.17 LPS @ 150 meter head. (9.2KW 3 phase or suitable capacity) Make:- Grundfos SP17-17 or as per list of approved make | 1.00 | Each |  | 77220.00 | 77220.00 | 485000.00 | 485000.00 | 77220.00 | C P MONCHESTER ELECTRICALS
2.00 | Supply of Energy efficient Submersible borewell multi stage pump IP 68 class suitable to handle clear water for operation on DOL starter. Pump should be completely made of stainless Steel construction for pump, motor & impeller to avoid the corrosion formation & with motor diameter 5 inch or less. All bearings are water lubricated and suitably shaped bearings for sand flush, inlet strainer for prevents entering of particles , in-built non return valve for preventing back flow and reduce the water hammer, stop ring for prevents damage of the pump due to up-thrust load. Pump should coupled with high efficiency oil cooled/water cooled submersible motor with bearing for smooth operation. Motor should be re-windable type and shall be with temperature sensor for motor protection. Pump flow and head min: 2000 LPH / 33 LPM / 0.56 LPS @ 125 meter head. (1.5 KW 3 phase or suitable capacity) Make:- Grundfos SP3A-25 1.5kW 380-415V 50Hz or as per list of approved make. | 1.00 | Each |  | 45000.00 | 45000.00 | 108000.00 | 108000.00 | 45000.00 | C P MONCHESTER ELECTRICALS
3.00 | Supply of Energy efficient Submersible borewell multi stage pump IP 68 class suitable to handle clear water for operation on DOL starter. Pump should be completely made of stainless Steel construction for pump, motor & impeller to avoid the corrosion formation & with motor diameter 5 inch or less. All bearings are water lubricated and suitably shaped bearings for sand flush, inlet strainer for prevents entering of particles , in-built non return valve for preventing back flow and reduce the water hammer, stop ring for prevents damage of the pump due to up-thrust load. Pump should coupled with high efficiency oil cooled/water cooled submersible motor with bearing for smooth operation. Motor should be re-windable type and shall be with temperature sensor for motor protection. Pump flow and head min: 7000 LPH / 116.4 LPM / 1.94 LPS @ 125 meter head. (1.5 KW 3 phase or suitable capacity) Make:- Grundfos SP9-21 4.0kW or as per list of approved make. | 2.00 | Each |  | 45000.00 | 90000.00 | 235000.00 | 470000.00 | 90000.00 | C P MONCHESTER ELECTRICALS
4.00 | Supply of Energy efficient Submersible borewell multi stage pump IP 68 class suitable to handle clear water for operation on DOL starter. Pump should be completely made of stainless Steel construction for pump, motor & impeller to avoid the corrosion formation & with motor diameter 5 inch or less. All bearings are water lubricated and suitably shaped bearings for sand flush, inlet strainer for prevents entering of particles , in-built non return valve for preventing back flow and reduce the water hammer, stop ring for prevents damage of the pump due to up-thrust load. Pump should coupled with high efficiency oil cooled/water cooled submersible motor with bearing for smooth operation. Motor should be re-windable type and shall be with temperature sensor for motor protection. Pump flow and head min: 2000 LPH / 33 LPM / 0.56 LPS @ 150 meter head. (2.2 KW 3 phase or suitable capacity) Make:- Grundfos SP3A-29 Rp 1 1/4 4" 50Hz or as per list of approved make. | 1.00 | Each |  | 45000.00 | 45000.00 | 65000.00 | 65000.00 | 45000.00 | C P MONCHESTER ELECTRICALS
5.00 | Supplying of following sizes of 1.1 KV grade, XLPE insulated, Aluminium conductor armoured Power Cable conforming to IS 7098 Part-I with up to date amendments complete as required as per specifications. 3.5 core, 70 sq.mm | 1435.00 | Meter |  | 450.00 | 645750.00 | 325.00 | 466375.00 | 466375.00 | Awasthi Electric Works
6.00 | Supply of 1.1KV grade, flat type three core PVC insulated & PVC sheathed industrial cable for submersible pump motors conforming to IS 694 with up to date amendments complete as required as per specifications. 3 core 2.5 sqmm | 880.00 | Meter |  | 120.00 | 105600.00 | 85.00 | 74800.00 | 74800.00 | Awasthi Electric Works
7.00 | Supply and lowering of uPVC borewell column pipe of following size, lead free and heavy metal free, threaded ends for each pipe to enable connection with suitable coupler, O rings as required in to the borewell along with already supplied flat cable tied to bore well column pipe & already supplied nylon rope for binding the motor pump set complete as required and as per instructions of Engineer-in-Charge Nominal dia -50mm, mini 17kg/cm2 (Make:- Astral pipe, M071300306, Crystal or equivalent from List of approved makes) | 540.00 | Meter |  | 300.00 | 162000.00 | 240.00 | 129600.00 | 129600.00 | Awasthi Electric Works
8.00 | Installation testing commissioning of borewell motor pump set into the borewell column pipe of required size with top and bottom adapter set, bracket connector, top metal clamp of suitable size for column pipe support etc complete as required as per instructions of Engineer-in-Charge. | 4.00 | Job |  | 27000.00 | 108000.00 | 25000.00 | 100000.00 | 100000.00 | Awasthi Electric Works
9.00 | Supply & installation uPVC Ball Valve Plastic 50mm size, including providing & installing required size Tee joint in the delivery pipe line from borewell complete as required. Make:- Supreme AqauaGold or equivalent from List of Approved makes. | 4.00 | Job |  | 2700.00 | 10800.00 | 1500.00 | 6000.00 | 6000.00 | Awasthi Electric Works
10.00 | Supply & installation of Check Valve (NRV) (Size - 50mm, Material - Bronze, Make- Zoloto or equivalent) with required MTA, 50mm size union on the pipe line complete as required. | 4.00 | Job |  | 7200.00 | 28800.00 | 3500.00 | 14000.00 | 14000.00 | Awasthi Electric Works
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 35sq.mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 1172.00 | Meter |  | 120.00 | 140640.00 | 125.00 | 146500.00 | 140640.00 | C P MONCHESTER ELECTRICALS
12.00 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 113.00 | Cum |  | 450.00 | 50850.00 | 900.00 | 101700.00 | 50850.00 | C P MONCHESTER ELECTRICALS
13.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part Il complete with fitting and cutting, jointing etc. in the existing trench, complete as required. 75 mm dia (OD-75 mm & ID-63 mm nominal) | 350.00 | Meter |  | 140.00 | 49000.00 | 145.00 | 50750.00 | 49000.00 | C P MONCHESTER ELECTRICALS
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required. Above 35sq.mm and upto 95sq.Mm | 280.00 | Meter |  | 90.00 | 25200.00 | 40.00 | 11200.00 | 11200.00 | Awasthi Electric Works
15.00 | Dismantling bituminous road by manually/ mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 meters lead as per direction of Engineer-in-charge and Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) excluding the cost of centering and shuttering - All work up to plinth level including form work etc as required. | 1.00 | Cum |  | 12000.00 | 12000.00 | 9000.00 | 9000.00 | 9000.00 | Awasthi Electric Works
16.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required 80 mm dia | 12.00 | Meter |  | 1800.00 | 21600.00 | 1020.00 | 12240.00 | 12240.00 | Awasthi Electric Works
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 70sq. mm (38mm) | 8.00 | Set |  | 2500.00 | 20000.00 | 495.00 | 3960.00 | 3960.00 | Awasthi Electric Works
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 300 sq. mm (70mm) | 1.00 | Set |  | 3500.00 | 3500.00 | 1395.00 | 1395.00 | 1395.00 | Awasthi Electric Works
19.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Set |  | 9000.00 | 90000.00 | 8500.00 | 85000.00 | 85000.00 | Awasthi Electric Works
20.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 40.00 | Meter |  | 45.00 | 1800.00 | 35.00 | 1400.00 | 1400.00 | Awasthi Electric Works
21.00 | Supply of nylon rope of high strength, shock resistant, having resistance to abrasion and deterioration due to UV light, minimal elongation, unaffected by hard water of size 20 mm, suitable for binding the borewell motor pump set. | 530.00 | Meter |  | 45.00 | 23850.00 | 90.00 | 47700.00 | 23850.00 | C P MONCHESTER ELECTRICALS
22.00 | Supply of Class-B Woltmann type water meter , size- 50mm, Cast Iron Body, flanged type, suitable for water temperature upto 50 degree Celsius, capable of withstanding pressure upto 16 bar, designed for measuring bulk flows of cold potable water complete as required. Make:- Kranti 50 mm Kflow Cast Iron Body or equivalent | 5.00 | Each |  | 9000.00 | 45000.00 | 10500.00 | 52500.00 | 45000.00 | C P MONCHESTER ELECTRICALS
23.00 | Installation of water meter in the existing PVC/metal pipe line at the delivery side of the pumping system with adequate support, flanges, MTA, bend, minor welding cutting works as per requirement at site complete as per instructions of Engineer-in-Charge. | 4.00 | Each |  | 2700.00 | 10800.00 | 3000.00 | 12000.00 | 10800.00 | C P MONCHESTER ELECTRICALS
24.00 | Supply and installation of DOL submersible pump starter suitable to connect 10 HP (7.5 KW) motor pump set having relay range of 20-32 amps, with protection features such as single phasing, over load, phase reversal, phase un-balance, coil voltage of 415V, push button for start & stop, power ON-OFF indications, with volt meter & ammeter for monitoring purpose, having auto re-start feature, enclosure protection of IP 54, complete as required. Make:- L&T, model:- MU-G10H (Heavy Duty), Cat No:- SS95974DOEO or equivalent. | 2.00 | Each |  | 18000.00 | 36000.00 | 10200.00 | 20400.00 | 20400.00 | Awasthi Electric Works
25.00 | Supply & installation of digital hour meter with LED/LCD display, contact / Voltage input selectable, self powered in suitable enclosure in the LT panel/over the LT panel as per site requirement and as per instructions of Engineer-in-Charge. Make:-SELEC LTC9A or equivalent | 6.00 | Each |  | 3600.00 | 21600.00 | 920.00 | 5520.00 | 5520.00 | Awasthi Electric Works
26.00 | Supply of DOL submersible pump starter suitable to connect 05 HP motor pump set having relay range of 06-10 amps, with protection features such as single phasing, over load, phase reversal, phase un-balance, coil voltage of 415V, push button for start & stop, power ON-OFF indications, with volt meter & ammeter for monitoring purpose, enclosure protection of IP 54, complete as required. Make:- L&T, model:- MU-G6 DOL, Cat No:- SS97756COVO or equivalent. | 1.00 | Each |  | 12000.00 | 12000.00 | 7200.00 | 7200.00 | 7200.00 | Awasthi Electric Works
27.00 | Supply of AE make, 100/5 A, 15VA, class 1 Resin Cast type Current Transformer conforming to IS 2705/1992 complete as required | 20.00 | Each |  | 2500.00 | 50000.00 | 1575.00 | 31500.00 | 31500.00 | Awasthi Electric Works
28.00 | Supply of 0.5 HP self priming mono block, Single phase, suction upto 7.5 m, copper winding with class F insulation, High-quality Extruded aluminium body for motor and Cast iron for pump casing, Forged brass impeller, of discharge capacity 1900 L / h. Make:- Havells, Model:- Hydrant 2 or equivalent in the list of approved makes | 1.00 | Each |  | 6000.00 | 6000.00 | 27000.00 | 27000.00 | 6000.00 | C P MONCHESTER ELECTRICALS
29.00 | Supply of UPVC pipe of size 3 inch and laying in the existing trench along with required couplers, unions at start and end, reducer, elbow etc for connecting to the existing line at both ends complete as required. | 50.00 | Meter |  | 900.00 | 45000.00 | 250.00 | 12500.00 | 12500.00 | Awasthi Electric Works
30.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required. Upto 35 sq. Mm | 77.00 | Meter |  | 45.00 | 3465.00 | 40.00 | 3080.00 | 3080.00 | Awasthi Electric Works
31.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 10.00 | Cum |  | 9000.00 | 90000.00 | 9000.00 | 90000.00 | 90000.00 | C P MONCHESTER ELECTRICALS, Awasthi Electric Works
32.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of double door, outdoor LT power supply Feeder Pillar of IP 54 protection minimum, made out of 2mm CRCA sheet, 3 mm thick for gland plates, dust & vermin proof, cubical type, compartmentalized, with aluminium bus bar having 400 amps current rating (same rating for phase and neutral), suitable for operation at 415V, 3phase, 4 wire, 50Hz, AC system complete with accessories, making connections and interconnections, mechanical interlocking for incomers & bus coupler (3 lock 2 key system), terminal blocks for termination of cables with bottom entry as per site conditions, locking arrangement, suitable earth bus, painting. etc. including the following accessories as per technical specifications and drawing as approved by engineer-in- charge . Incomer: 320 Amps, 4 Pole MCCB, 50 kA breaking capacity, Microprocessor release type, Ics = 100% Icu, having adjustable overload setting and short circuit setting, spreader bars, with rotary handle and LED indications for RYB, ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 02 Nos. Bus Coupler: 320 Amps, 4 Pole MCCB, 50 kA breaking capacity, Microprocessor release type, Ics = 100% Icu, having adjustable overload setting and short circuit setting, spreader bars, with rotary handle and LED indications for ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 01 No. Outgoings: 1) 200 Amps, 4 Pole MCCB, >=35 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase - 02 Nos 2) 160 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase -02 Nos 3) 100 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase -02 Nos 4) 32 Amps, 4 Pole MCB, C curve - 02 Nos 5) 16 Amps, 2 Pole MCB, C curve - 03 Nos | 1.00 | Job |  | 475000.00 | 475000.00 | 525000.00 | 525000.00 | 475000.00 | C P MONCHESTER ELECTRICALS
33.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of double door, outdoor LT power supply Feeder Pillar of IP 54 protection minimum, made out of 2mm CRCA sheet, 3 mm thick for gland plates, dust & vermin proof, cubical type, compartmentalized, with aluminium bus bar having 300 amps current rating (same rating for phase and neutral), suitable for operation at 415V, 3phase, 4 wire, 50Hz, AC system complete with accessories, making connections and interconnections, mechanical interlocking for incomers & bus coupler (3 lock 2 key system), terminal blocks for termination of cables with bottom entry as per site conditions, locking arrangement, painting. etc. including the following accessories as per technical specifications and drawing as approved by engineer-in- charge . Incomer: 200 Amps, 4 Pole MCCB,>=35 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, with rotary handle and LED indications for RYB, ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 02 Nos. Bus Coupler: 200 Amps, 4 Pole MCCB, >=35 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, with rotary handle and LED indications for ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 01 No. Outgoings: 1) 160 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase - 04 Nos 2) 100 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase -02 Nos 3) 32 Amps, 4 Pole MCB, C curve - 02 Nos 4) 16 Amps, 2 Pole MCB, C curve - 03 Nos | 1.00 | Job |  | 410000.00 | 410000.00 | 395000.00 | 395000.00 | 395000.00 | Awasthi Electric Works
34.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of double door, outdoor LT power supply Feeder Pillar of IP 54 protection minimum, made out of 2mm CRCA sheet, 3 mm thick for gland plates, dust & vermin proof, cubical type, compartmentalized, with aluminium bus bar having 200 amps current rating (same rating for phase and neutral), suitable for operation at 415V, 3phase, 4 wire, 50Hz, AC system complete with accessories, making connections and interconnections, terminal blocks for termination of cables with bottom entry as per site conditions, locking arrangement, painting. etc. including the following accessories as per technical specifications and drawing as approved by engineer-in- charge . Incomer: 125 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED indications for RYB, ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 01 Nos. Outgoings: 1) 125 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase -01 Nos 2) 63 Amps, 4 Pole MCB controlled motor control centre (MCC) having DOL starter with required contactors, OLR, Dry run protection, single phase preventor, start & stop push buttons, suitable for 5 HP borewell motor pump set, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase, digital hour meter for showing pump running hours -01 Nos (The panel should have empty cubicle to accomodate the OEM supplied starter (S/D or DOL as the case may be) incase of OEM of the borewell pump set recommends so). 3) 32 Amps, 4 Pole MCB, C curve - 02 Nos 4) 16 Amps, 2 Pole MCB, C curve - 03 Nos | 3.00 | Job |  | 162000.00 | 486000.00 | 168000.00 | 504000.00 | 486000.00 | C P MONCHESTER ELECTRICALS
35.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of double door, outdoor LT power supply Feeder Pillar of IP 54 protection minimum, made out of 2mm CRCA sheet, 3 mm thick for gland plates, dust & vermin proof, cubical type, compartmentalized, with aluminium bus bar having 200 amps current rating (same rating for phase and neutral), suitable for operation at 415V, 3phase, 4 wire, 50Hz, AC system complete with accessories, making connections and interconnections, terminal blocks for termination of cables with bottom entry as per site conditions, locking arrangement, painting. etc. including the following accessories as per technical specifications and drawing as approved by engineer-in- charge . Incomer: 125 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED indications for RYB, ON, OFF indications, suitable resin cast/wire wound CT's with digital multifunction meter - 01 Nos. Outgoings: 1) 125 Amps, 4 Pole MCCB, >=20 kA breaking capacity, TMR type, Ics = 100% Icu, spreader bars, rotary handle, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase -01 Nos 2) 63 Amps, 4 Pole MCB controlled motor control centre (MCC) having DOL starter with required contactors, OLR, Dry run protection, single phase preventor, start & stop push buttons, suitable for 5 HP borewell motor pump set, LED type ON & OFF Indications, LED type basic Ammeter of class 1 accuracy having inbuilt selector switch suitable for 3 phase, digital hour meter for showing pump running hours -01 Nos (The panel should have empty cubicle to accomodate the OEM supplied starter (S/D or DOL as the case may be) incase of OEM of the borewell pump set recommends so). 3) 32 Amps, 4 Pole MCB, C curve - 02 Nos 4) 16 Amps, 2 Pole MCB, C curve - 03 Nos | 1.00 | Job |  | 165000.00 | 165000.00 | 175000.00 | 175000.00 | 165000.00 | C P MONCHESTER ELECTRICALS
36.00 | Supply of borewell motor lifting machine, designed with suitable size square pipe and L angles, electrically operated with suitable capacity 3 phase motor from reputed brands such as havells, crompton Kirloskar etc along with forward and reverse switch with gears for speed reduction, having mast of height more than 12 feet and drum for winding the rope (combined type), having wheels for transportation purpose, suitable to lift borewell from upto 150 meter depth, including painting, supply of 4 number suitable die, etc complete as required. | 1.00 | Each |  | 135000.00 | 135000.00 | 325000.00 | 325000.00 | 135000.00 | C P MONCHESTER ELECTRICALS
| Total in Figures |  |  |  |  | 3747475.00 |  | 4575320.00
Lowest Amount Quoted BY: C P MONCHESTER ELECTRICALS(3747475.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of power supply and bore well pumps for new bore wells at Coimbatore International Airport. Tender ID: 2023_AAI_172917_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | C P MONCHESTER ELECTRICALS | 3747475.00 | L1
| 2 | Awasthi Electric Works | 4575320.00 | L2