## BoQ1
Government eProcurement System Created By: Arun Kumar Majhi Created Date/Time: 22-Dec-2023 11:52 AM Tender Title: Replacement of HT Lt Cable and Transformer Tender ID: 2023_AAI_173899_1
Tender Inviting Authority: <AIRPORTS AUTHORITY OF INDIA>
Name of Work: <Replacement/Relocation of HT/LT cables and replacement of 400KVA oil type transformer inside Operational Area, NSCBI Airport, Kolkata>
Contract No: <2023_AAI_173899_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | SAHA COMMERCIAL CONSTRUCTION(GSTN-19AASFS6288A1ZN) |  | SHREE GOURI ELECTRIC ENTERPRISE(GSTN-19ADDPB4683J1ZE) |  | M/s J.K. Electric Engineering Works(GSTN-19AAHFJ4404E1ZL) |  | Shahi Electric Engg Co Pvt Ltd(GSTN-19AAECS3962N1ZP) |  | The Indian Overseas Trading Company(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Fabrication, Supply & ITC including civil foundation work of 12.0 KV, 21kA for 3 sec, SF6 insulated extendable outdoor type 5 way Ring Main Unit. Consisting of 02 Nos. 630 A capacity Load Break Switches (LBS) for incomers and 03 Nos. 630 A capacity VCB switches for Outgoings suitable for termination of 3c x 300 sq.mm., XLPE, Al, Armoured 11KV grade HT cable, housed in suitable SF6 insulated enclosure with all types of protection relays & metering (as specified below) and necessary accessories etc. as required. The operation of the switches shall be spring charged and motorised. RMU shall be suitable for outdoor operation in highly corosive atmosphere and shall be with suitable IP protection.
1.01 | A. Load Break Switch (LBS) each comprising of the following: 12KV, 630A, 21kA motorized Load break switch with built in earth switch Mechanical position indicator (On/off/earthed) Live cable indicator Cable termination bushing suitable for upto 2 RUN 3Cx300 Sq mm, XLPE cable Cable termination cover boots Fault passage indicator (FPI) with in-built Overcurrent, Short Circuit and earth fault indication (in one LBS) B. Vacuum circuit breaker (VCB) each comprising of the following: 12KV, 630A, 21kA VCB with motorized spring charging mechanism and tripping/closing coil. Motor operator 630A disconnector with built in earth switch Mechanical position indicator (On/off/earthed) Live cable indicator Self powered O/C+ E/F relay Multifunctional energy meter Class 1.0. Suitable ratio CT --/1-1A, Class - 1.0, 2.5VA for metering and Class 10P10, 2.5VA for protection Cable termination bushing suitable for upto 1 RUN 3Cx300 Sq mm, XLPE cable Cable termination cover boots (Push on type) C. Air Insulated Bus Connected Metering Unit (M) comprising the following Air Insulated enclosure with necessary bus connection PT 6KV/Rt 3/110V/Rt3, 25VA, class-1.0 Voltmeter with selector switch R/Y/B indicating lamps 11KV/230V AC, 1KVA control transformer Battery and battery charger, 7Ah, (I/P-230V AC, O/P - 24V DC) RMU degree of protection shall be IP54 for outer enclosure and IP67 for SF6 tank The RMU shall be provided with potential free contacts at the multi core terminal blocks for SCADA compatibility. | 1.00 | JOB |  | 1600000.00 | 1600000.00 | 1649800.00 | 1649800.00 | 1150000.00 | 1150000.00 | 2450000.00 | 2450000.00 | 1570399.00 | 1570399.00 | 1929448.00 | 1929448.00 | 1150000.00 | SHREE GOURI ELECTRIC ENTERPRISE
2.00 | Supplying, installation, testing and commissioning of 400 KVA, 6-11/0.415 KV dual core, 3 Phase, 50 Hz, Dyn 11, indoor ONAN type, copper wound transformer with OFF load tap changing arrangement on HV side in steps of +/- 2.5% & -7.5%, having cable end boxes on HV side suitable for 3 x 300 sqmm XLPE cable of 11 KV grade and 800 Amp. bus for Cable Termination on LV side complete with all accessories i/c first filling of filtered dehydrated oil and confirming to IS 2026 (Part 1 to Part 5) & as per specification attached complete in all respects as required at site. | 1.00 | Job |  | 1450000.00 | 1450000.00 | 1348500.00 | 1348500.00 | 1400000.00 | 1400000.00 | 2175000.00 | 2175000.00 | 2633626.00 | 2633626.00 | 1889167.00 | 1889167.00 | 1348500.00 | SAHA COMMERCIAL CONSTRUCTION
3.00 | Supply of following sizes of Aluminium Power Cables, multi stranded conductor, XLPE Insulated, Armoured, FRLSH at outer sheathed,11kV (E) grade as per IS 7098(Part II) with up to date amendments. 3 core 120 Sq.mm. | 5000.00 | Meter |  | 755.00 | 3775000.00 | 750.00 | 3750000.00 | 1000.00 | 5000000.00 | 900.00 | 4500000.00 | 843.00 | 4215000.00 | 951.00 | 4755000.00 | 3750000.00 | SAHA COMMERCIAL CONSTRUCTION
4.00 | Supply of following sizes of Aluminium Power Cables, multi stranded conductor, XLPE Insulated, Armoured, FRLSH at outer sheathed,1.1kV (E) grade as per IS 7098(Part I) with up to date amendments. 3.5 core 185 Sq.mm. | 2000.00 | Meter |  | 705.00 | 1410000.00 | 725.00 | 1450000.00 | 875.00 | 1750000.00 | 810.00 | 1620000.00 | 781.00 | 1562000.00 | 865.00 | 1730000.00 | 1410000.00 | Youngmen Traders
5.00 | Supply of 160 mm outer dia HDPE (high density polyethylene) pipe confirming to IS 4984: 2016 and uptodate ammendments along with its necessary accessories like coupler, end plugs etc. PE-80, PN-6. | 2300.00 | Meter |  | 725.00 | 1667500.00 | 975.00 | 2242500.00 | 650.00 | 1495000.00 | 650.00 | 1495000.00 | 778.00 | 1789400.00 | 985.00 | 2265500.00 | 1495000.00 | SHREE GOURI ELECTRIC ENTERPRISE, M/s J.K. Electric Engineering Works
6.00 | Laying of 160 mm outer dia HDPE (high density polyethylene) pipe confirming to IS 4984: 2016 and uptodate ammendments along with its necessary accessories like coupler, end plugs etc. below the ground (i/c road crossing, cement concrete drain area, etc) at a depth of min 1.5 m through HDD method with fusion welding of HDPE pipes as per site requirement. | 2300.00 | Meter |  | 400.00 | 920000.00 | 350.00 | 805000.00 | 50.00 | 115000.00 | 370.00 | 851000.00 | 605.00 | 1391500.00 | 649.00 | 1492700.00 | 115000.00 | SHREE GOURI ELECTRIC ENTERPRISE
7.00 | Supply of DWC HDPE pipe ISI marked of 160mm outer dia conforming to IS 16205, Part 24 : 2018 and uptodate ammendments along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc. as required. | 3300.00 | Meter |  | 260.00 | 858000.00 | 225.00 | 742500.00 | 200.00 | 660000.00 | 295.00 | 973500.00 | 220.00 | 726000.00 | 299.00 | 986700.00 | 660000.00 | SHREE GOURI ELECTRIC ENTERPRISE
8.00 | Laying of DWC HDPE pipe along with all accessories like socket, bend, couplers etc. with fitting and cutting, jointing etc.direct in ground (upto120 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 3300.00 | Meter |  | 175.00 | 577500.00 | 275.00 | 907500.00 | 50.00 | 165000.00 | 125.00 | 412500.00 | 363.00 | 1197900.00 | 225.00 | 742500.00 | 165000.00 | SHREE GOURI ELECTRIC ENTERPRISE
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. Upto 120 sq. mm | 75.00 | Meter |  | 325.00 | 24375.00 | 475.00 | 35625.00 | 400.00 | 30000.00 | 300.00 | 22500.00 | 363.00 | 27225.00 | 273.00 | 20475.00 | 20475.00 | The Indian Overseas Trading Company
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/HUME/ METAL pipe as required. Upto 120 sq. mm | 4100.00 | Meter |  | 60.00 | 246000.00 | 150.00 | 615000.00 | 20.00 | 82000.00 | 33.50 | 137350.00 | 73.00 | 299300.00 | 234.00 | 959400.00 | 82000.00 | SHREE GOURI ELECTRIC ENTERPRISE
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required. Upto 120 sq. mm | 50.00 | Meter |  | 30.00 | 1500.00 | 125.00 | 6250.00 | 100.00 | 5000.00 | 33.50 | 1675.00 | 61.00 | 3050.00 | 169.00 | 8450.00 | 1500.00 | Youngmen Traders
12.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
12.01 | Above 95 sq. mm and upto 185 sq. mm | 50.00 | Meter |  | 300.00 | 15000.00 | 250.00 | 12500.00 | 400.00 | 20000.00 | 140.00 | 7000.00 | 242.00 | 12100.00 | 222.00 | 11100.00 | 7000.00 | M/s J.K. Electric Engineering Works
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required.
13.01 | Above 95 sq. mm and upto 185 sq. mm | 1500.00 | Meter |  | 45.00 | 67500.00 | 125.00 | 187500.00 | 20.00 | 30000.00 | 30.00 | 45000.00 | 73.00 | 109500.00 | 169.00 | 253500.00 | 30000.00 | SHREE GOURI ELECTRIC ENTERPRISE
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
14.01 | Above 95 sq. mm and upto 185 sq. mm | 25.00 | Meter |  | 20.00 | 500.00 | 95.00 | 2375.00 | 100.00 | 2500.00 | 30.00 | 750.00 | 61.00 | 1525.00 | 150.00 | 3750.00 | 500.00 | Youngmen Traders
15.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required : 120 sq.mm. | 10.00 | Each |  | 3000.00 | 30000.00 | 7500.00 | 75000.00 | 4500.00 | 45000.00 | 4800.00 | 48000.00 | 3648.00 | 36480.00 | 6066.00 | 60660.00 | 30000.00 | Youngmen Traders
16.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. 3½ X 150 sq. mm (50mm) | 2.00 | Each |  | 1800.00 | 3600.00 | 950.00 | 1900.00 | 1000.00 | 2000.00 | 700.00 | 1400.00 | 1519.00 | 3038.00 | 1730.00 | 3460.00 | 1400.00 | M/s J.K. Electric Engineering Works
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm (57mm) | 2.00 | Each |  | 1500.00 | 3000.00 | 1150.00 | 2300.00 | 4000.00 | 8000.00 | 700.00 | 1400.00 | 1641.00 | 3282.00 | 1453.00 | 2906.00 | 1400.00 | M/s J.K. Electric Engineering Works
18.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required : 120 sq. mm. | 10.00 | Each |  | 7500.00 | 75000.00 | 11500.00 | 115000.00 | 8000.00 | 80000.00 | 9800.00 | 98000.00 | 10975.00 | 109750.00 | 11002.00 | 110020.00 | 75000.00 | Youngmen Traders
19.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm | 4.00 | Each |  | 4000.00 | 16000.00 | 4750.00 | 19000.00 | 8000.00 | 32000.00 | 3000.00 | 12000.00 | 5481.00 | 21924.00 | 6893.00 | 27572.00 | 12000.00 | M/s J.K. Electric Engineering Works
20.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (upto 120 cm deep)and re-filling etc as required
20.01 | 100 mm | 24.00 | Meter |  | 1500.00 | 36000.00 | 1275.00 | 30600.00 | 2000.00 | 48000.00 | 1300.00 | 31200.00 | 1588.00 | 38112.00 | 1592.00 | 38208.00 | 30600.00 | SAHA COMMERCIAL CONSTRUCTION
20.02 | 150 mm | 36.00 | Meter |  | 2300.00 | 82800.00 | 1825.00 | 65700.00 | 3000.00 | 108000.00 | 1650.00 | 59400.00 | 2321.00 | 83556.00 | 2214.00 | 79704.00 | 59400.00 | M/s J.K. Electric Engineering Works
21.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. (but without charcoal/ coke and salt ) as required. | 4.00 | Each |  | 5500.00 | 22000.00 | 6500.00 | 26000.00 | 7000.00 | 28000.00 | 5500.00 | 22000.00 | 9136.00 | 36544.00 | 8870.00 | 35480.00 | 22000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
22.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. | 50.00 | Meter |  | 140.00 | 7000.00 | 195.00 | 9750.00 | 150.00 | 7500.00 | 140.00 | 7000.00 | 159.00 | 7950.00 | 336.00 | 16800.00 | 7000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 75.00 | Meter |  | 450.00 | 33750.00 | 525.00 | 39375.00 | 500.00 | 37500.00 | 600.00 | 45000.00 | 732.00 | 54900.00 | 545.00 | 40875.00 | 33750.00 | Youngmen Traders
24.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Meter |  | 105.00 | 3150.00 | 190.00 | 5700.00 | 150.00 | 4500.00 | 135.00 | 4050.00 | 159.00 | 4770.00 | 210.00 | 6300.00 | 3150.00 | Youngmen Traders
25.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 15000.00 | 30000.00 | 10500.00 | 21000.00 | 18000.00 | 36000.00 | 11500.00 | 23000.00 | 15246.00 | 30492.00 | 16297.00 | 32594.00 | 21000.00 | SAHA COMMERCIAL CONSTRUCTION
26.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. | 35.00 | Meter |  | 925.00 | 32375.00 | 995.00 | 34825.00 | 1300.00 | 45500.00 | 1050.00 | 36750.00 | 1341.00 | 46935.00 | 1325.00 | 46375.00 | 32375.00 | Youngmen Traders
27.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter |  | 1225.00 | 36750.00 | 1325.00 | 39750.00 | 1600.00 | 48000.00 | 1450.00 | 43500.00 | 1526.00 | 45780.00 | 1526.00 | 45780.00 | 36750.00 | Youngmen Traders
28.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 35.00 | Meter |  | 890.00 | 31150.00 | 985.00 | 34475.00 | 1200.00 | 42000.00 | 1015.00 | 35525.00 | 1314.00 | 45990.00 | 1300.00 | 45500.00 | 31150.00 | Youngmen Traders
29.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 20.00 | Cum |  | 7500.00 | 150000.00 | 8500.00 | 170000.00 | 5000.00 | 100000.00 | 6000.00 | 120000.00 | 7260.00 | 145200.00 | 7437.00 | 148740.00 | 100000.00 | SHREE GOURI ELECTRIC ENTERPRISE
30.00 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels finished with a floating coat of neat cement. | 90.00 | Sq.m |  | 325.00 | 29250.00 | 200.00 | 18000.00 | 350.00 | 31500.00 | 150.00 | 13500.00 | 242.00 | 21780.00 | 344.00 | 30960.00 | 13500.00 | M/s J.K. Electric Engineering Works
31.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation etc including form work etc as required. | 20.00 | Cum |  | 8500.00 | 170000.00 | 9500.00 | 190000.00 | 7000.00 | 140000.00 | 5800.00 | 116000.00 | 7865.00 | 157300.00 | 8006.00 | 160120.00 | 116000.00 | M/s J.K. Electric Engineering Works
32.00 | Excavation and refilling in soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 100.00 | Cum |  | 175.00 | 17500.00 | 350.00 | 35000.00 | 250.00 | 25000.00 | 250.00 | 25000.00 | 424.00 | 42400.00 | 415.00 | 41500.00 | 17500.00 | Youngmen Traders
33.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 20.00 | Cum |  | 1500.00 | 30000.00 | 550.00 | 11000.00 | 1000.00 | 20000.00 | 500.00 | 10000.00 | 1815.00 | 36300.00 | 467.00 | 9340.00 | 9340.00 | The Indian Overseas Trading Company
34.00 | Dismantling of HT/LT power cable upto 185 sq.mm. from existing Masonary Duct/HUME pipe/HDPE pipes. | 100.00 | Meter |  | 20.00 | 2000.00 | 50.00 | 5000.00 | 300.00 | 30000.00 | 30.00 | 3000.00 | 30.00 | 3000.00 | 180.00 | 18000.00 | 2000.00 | Youngmen Traders
35.00 | Dismantling of existing 400 KVA oil Type Tranformer with all its accessories and removal all cable termination etc. as complete carefully without damaging the existing and facility and transportation of panel to the AAI Store with in a distance of 3 Km inside operational area. | 1.00 | Job |  | 3000.00 | 3000.00 | 5484.00 | 5484.00 | 25000.00 | 25000.00 | 4000.00 | 4000.00 | 12100.00 | 12100.00 | 38940.00 | 38940.00 | 3000.00 | Youngmen Traders
36.00 | Underground survey using ground penetrating Radar (GPR) to detect existing utilities up to 5 meter depth along with 5 meter wide corridor, underground survey using EPL to detect existing preparation of route diagram for the above. | 800.00 | Meter |  | 38.00 | 30400.00 | 250.00 | 200000.00 | 350.00 | 280000.00 | 35.00 | 28000.00 | 157.00 | 125600.00 | 130.00 | 104000.00 | 28000.00 | M/s J.K. Electric Engineering Works
| Total in Figures |  |  |  |  | 13487600.00 |  | 14909909.00 |  | 13128000.00 |  | 15479000.00 |  | 16651708.00 |  | 18191524.00
Lowest Amount Quoted BY: SHREE GOURI ELECTRIC ENTERPRISE(13128000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of HT Lt Cable and Transformer Tender ID: 2023_AAI_173899_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHREE GOURI ELECTRIC ENTERPRISE | 13128000.00 | L1
| 2 | Youngmen Traders | 13487600.00 | L2
| 3 | SAHA COMMERCIAL CONSTRUCTION | 14909909.00 | L3
| 4 | M/s J.K. Electric Engineering Works | 15479000.00 | L4
| 5 | Shahi Electric Engg Co Pvt Ltd | 16651708.00 | L5
| 6 | The Indian Overseas Trading Company | 18191524.00 | L6