## BoQ1
Government eProcurement System Created By: Ravindra Nandurkar Created Date/Time: 31-Jan-2024 12:10 PM Tender Title: Structural rehabilitation of existing 03 Nos. of RCC Sumps and 01 No. RCC Overhead tank at New Airport Colony, Mumbai. SH Electrical Works Tender ID: 2023_AAI_174670_1
Tender Inviting Authority: Asstt.G.M.(E-E)
Name of Work: Structural rehabilitation of existing 03 nos. of R.C.C. Sumps and 01 No. of R.C.C. Overhead tank at New Airport Colony, Mumbai. Sub-Head: -Electrical works.
Contract No: 2023_AAI_174670_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Ramesh Electrical and Mechanical Works(GSTN-27ACKPS7682J1ZQ) |  | PERFECT TECH ENGINEERS(GSTN-27AAEPK2522K1ZT)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | MOTOR CONTROL PANEL (E-LINE & A-LINE) (15HP (11KW) Submersible Pump Set
1.01 | Design, Supply, Installation, Testing and Commissioning of Floor Mounted Motor Control Stater Panel of suitable size with mounting frame 50mm x 50mm x 5 mm thick MS Angle and 0.5 m long legs of same size, for 04 nos. 15 HP (11KW) Submersible Pump sets operating on 415 V, 50 Hz AC power supply, cubicle indoor type, made out of 14 SWG CRCA sheet steel, totally enclosed, dust and vermin proof, IP 54, powder coated in approved shade, removeable 3mm thick gland plate for bottom cable entry (incoming and outgoings) and to be mounted on CC base foundation of suitable size, panel shall also have common Al strip of 25 mm x 5 mm size at the rear with two numbers of earth studs and including the following switch gears and pump protection relays, wiring complete as required. INCOMER : - (a) Four Pole MCCB 250 A, Microprocessor release (Ics=50 KA upto 433 V)- 2 Nos. with 4 X 300 Amp copper busbar (R,Y,B,N) (b) Manual Changeover Switch, 250 A-1 No. (c) Digital Multifuntion Meter -2 Nos. with set of 250/5 A of CTs. (d) Phase indication LED lamps with suitable SPMCB - 3 Nos OUTGOING : - 1. Suitable capcacity of Star/Delta Starter Contactor & relay for 15 HP submersible pump set , along with dry run protection, single phase preventor, over load protection, under & over voltage protection , manual ON/OFF push button, Motor ON/OFF LED type indication (01 Set)-4 No. with following accessories: ( a ) TP MPCB, 100 A, Thermal magnetic release (Ics=36 KA upto 433 V)-4 Nos. ( b )Motor Selection Switch - 02 Nos. ( for sumercible pump selection purpose) (d) Power supply LED indication lamp (R,Y,B) with control MCBs 2. TPN MCCB, 100 Amp, Thermal magnetic release (Ics=36 KA upto 433 V)- 1 No. (Spare) with following accessories: (a) Power supply LED indication lamp (R,Y,B) with control MCBs | 2.00 | Job |  | 278000.00 | 556000.00 | 450000.00 | 900000.00 | 556000.00 | Ramesh Electrical and Mechanical Works
2.00 | MOTOR CONTROL PANEL (O-LINE) (15 HP (11KW) Submersible Pump Set)
2.01 | Design, Supply, Installation, Testing and Commissioning of Wall mounted Motor Control Stater Panel for 02 nos. 15 HP (11KW) Submersible Pump sets operating on 415 V, 50 Hz AC power cubicle indoor type, made out of 14 SWG CRCA sheet steel, totally enclosed, dust and vermin proof, IP 54, powder coated in approved shade, removeable 3mm thick for gland plate for bottom cable entry (incoming and outgoings), panel shall also have common Al strip of 25 mm x 5 mm size at the rear with two numbers of earth studs and including the following switch gears and pump protection relays, wiring complete as required. INCOMER : - (a) Four Pole MCCB 100 A, Thermal magnetic release (Ics=36 KA upto 433 V) - 2 No., with 4 X 150 Amp copper busbar (R,Y,B,N) (b) Manual Changeover Switch, 100 A-1 No. (c) Digital Multifuntion Meter -2 Nos. with set of 100/5A of CTs. (d) Phase indication LED lamps with suitable SPMCB - 3 Nos OUTGOING : - 1. Suitable capcacity of Star/Delta Starter Contactor & relay for 15 HP submersible pump set , along with dry run protection, single phase preventor, over load protection, under & over voltage protection , manual ON/OFF push button, Motor ON/OFF LED type indication (01 Set)-2 No. with following accessories: (b) TP MPCB 63 Amps, Thermal magnetic release (Ics=36 KA upto 433 V)-2 Nos. (c) Motor Selection Switch - 01 Nos. ( for sumercible pump selection purpose) 2. TPN MCCB, 63 Amp, Thermal magnetic release (Ics=36 KA upto 433 V)- 1 No. (Spare) with following accessories: (a) Power supply LED indication lamp (R,Y,B) with control MCBs | 1.00 | Job |  | 256000.00 | 256000.00 | 432000.00 | 432000.00 | 256000.00 | Ramesh Electrical and Mechanical Works
3.00 | Supply, Installation, Testing and Commissioning of 3 phase 15 HP horizontal Submersible Fresh water pumpset, suitable for operation on 415V, 50 Hz power supply. The pump shall have Stainless Steel Shaft, Cast Iron Body & Impeller with water delivery capacity range from 1080 to 1980 LPM (approx.) for 24 mtr to 30 mtr head, IP 68 rating etc as specificied in Technical Specifications complete as required. | 10.00 | Job |  | 120450.00 | 1204500.00 | 69300.00 | 693000.00 | 693000.00 | PERFECT TECH ENGINEERS
4.00 | Supply of following size of 1.1 KV grade,XLPE insulated PVC sheated armoured Aluminium conductor cable confirming to IS 7098 part -II amended upto date. 3.5 x 150 Sq.mm | 70.00 | Mtr |  | 893.00 | 62510.00 | 1530.00 | 107100.00 | 62510.00 | Ramesh Electrical and Mechanical Works
5.00 | Supply of following size of 1.1 KV grade,XLPE insulated PVC sheated armoured Aluminium conductor cable confirming to IS 7098 part -II amended upto date. 3.5 x 50 Sq.mm | 370.00 | Mtr |  | 381.00 | 140970.00 | 711.00 | 263070.00 | 140970.00 | Ramesh Electrical and Mechanical Works
6.00 | Supply of 1100 V voltage grade , PVC insulated and PVC sheathed Industrial 3 core flat Submersible cable with bare bunched copper conductor cable confirming to IS :694/1990 . 3 x 10sq.mm | 240.00 | Mtr |  | 476.00 | 114240.00 | 900.00 | 216000.00 | 114240.00 | Ramesh Electrical and Mechanical Works
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. - Upto 35 sq. mm (clamped with 1mm thick saddle) | 220.00 | Mtr |  | 200.00 | 44000.00 | 1242.00 | 273240.00 | 44000.00 | Ramesh Electrical and Mechanical Works
8.00 | Supply of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II .
8.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 350.00 | Mtr |  | 241.00 | 84350.00 | 207.00 | 72450.00 | 72450.00 | PERFECT TECH ENGINEERS
8.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 60.00 | Mtr |  | 357.00 | 21420.00 | 306.00 | 18360.00 | 18360.00 | PERFECT TECH ENGINEERS
9.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
9.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 350.00 | Mtr |  | 200.00 | 70000.00 | 54.00 | 18900.00 | 18900.00 | PERFECT TECH ENGINEERS
9.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 60.00 | Mtr |  | 175.00 | 10500.00 | 54.00 | 3240.00 | 3240.00 | PERFECT TECH ENGINEERS
10.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/Metal/HDPE/PVC pipe as required.
10.01 | Above 35 sq. mm and upto 95 sq. mm | 350.00 | Mtr |  | 250.00 | 87500.00 | 27.00 | 9450.00 | 9450.00 | PERFECT TECH ENGINEERS
10.02 | Above 95 sq. mm and upto 185 sq. mm | 60.00 | Mtr |  | 350.00 | 21000.00 | 54.00 | 3240.00 | 3240.00 | PERFECT TECH ENGINEERS
11.00 | Supply and making End termination with Brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1KV grade as required.
11.01 | 3½ X 50 sq. mm | 4.00 | Each |  | 700.00 | 2800.00 | 540.00 | 2160.00 | 2160.00 | PERFECT TECH ENGINEERS
11.02 | 3½ X 150 sq. mm | 2.00 | Each |  | 800.00 | 1600.00 | 900.00 | 1800.00 | 1600.00 | Ramesh Electrical and Mechanical Works
12.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 3.00 | Each |  | 18000.00 | 54000.00 | 14400.00 | 43200.00 | 43200.00 | PERFECT TECH ENGINEERS
13.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 500.00 | Mtr |  | 30.00 | 15000.00 | 27.00 | 13500.00 | 13500.00 | PERFECT TECH ENGINEERS
14.00 | Providing & Fixing of 100 mm dia . Heavy duty " C " class GI pipe for connection of Submersible pumpset (15 HP) from pumpset to delivery line in pump room along with long bend, coupler, Tee, pipe supports, weilding, cutting , making threading complete as required. | 80.00 | Mtr |  | 2950.00 | 236000.00 | 1260.00 | 100800.00 | 100800.00 | PERFECT TECH ENGINEERS
15.00 | Providing & Fixing of 65 mm dia . Heavy duty " C " class GI pipe for connection of Submersible pumpset (15HP) from pumpset to delivery line in pump room along with long bend, coupler, Tee, pipe supports, weilding, cutting , making threading complete as required. | 20.00 | Mtr |  | 2450.00 | 49000.00 | 630.00 | 12600.00 | 12600.00 | PERFECT TECH ENGINEERS
16.00 | Supply, Installation, Testing & Commissioning of 100 mm dia. butterfly valve made of cast iron body confirming to IS 13095, PN 16 complete with flange, rubber gasket, GI bolts, nuts washers etc complete as required. | 8.00 | Each |  | 6500.00 | 52000.00 | 4500.00 | 36000.00 | 36000.00 | PERFECT TECH ENGINEERS
17.00 | Supply, Installation, Testing & Commissioning of 65 mm dia. butterfly valve made of cast iron body confirming to IS 13095, PN 16 complete with flange, rubber gasket, GI bolts, nuts washers etc complete as required. | 2.00 | Each |  | 4500.00 | 9000.00 | 3600.00 | 7200.00 | 7200.00 | PERFECT TECH ENGINEERS
18.00 | Supply, Installation, Testing & Commissioning of 100 mm dia. Gun Metal/Bronze Vertical Lift type Non-Return valve (NRV) complete as required. | 8.00 | Each |  | 18200.00 | 145600.00 | 12600.00 | 100800.00 | 100800.00 | PERFECT TECH ENGINEERS
19.00 | Supply, Installation, Testing & Commissioning of 65 mm dia. Gun Metal/Bronze Vertical Lift type Non-Return valve (NRV) complete as required. | 2.00 | Each |  | 14200.00 | 28400.00 | 6300.00 | 12600.00 | 12600.00 | PERFECT TECH ENGINEERS
20.00 | Design, Supply, Installation, Testing and Commissioning of Floor Mounted Junction Box of size suitable size with mounting frame 50mm x 50mm x 5 mm thick MS Angle and 0.5 m long legs of same size, for one no. incomer of cable size 3.5 x 240 sqmm and three nos. outgoing of cable size 3.5 x 150 sqmm having 4 X 300 Amp aluminium busbar (R,Y,B,N), cubicle outdoor type, made out of 14 SWG CRCA sheet steel, totally enclosed, dust and vermin proof, IP 65, powder coated in approved shade, removeable 3 mm thick gland plate for bottom cable entry (incoming and outgoings) and to be mounted on CC base foundation of suitable size, panel shall also have common Al strip of 25 mm x 5 mm size at the rear with two numbers of earth studs complete as required. | 2.00 | Job |  | 2500.00 | 5000.00 | 12600.00 | 25200.00 | 5000.00 | Ramesh Electrical and Mechanical Works
21.00 | Dismantling and shifting of existing split casing pump sets at E Line Pump Room (40 HP each), E Line Pump Room (10 HP each) & A line Pump Room (40 HP Each.) with motor, Valves, pipes etc. to AAI store and closing of existing pipe with flange, etc. complete as required. | 3.00 | Job |  | 5000.00 | 15000.00 | 3000.00 | 9000.00 | 9000.00 | PERFECT TECH ENGINEERS
22.00 | Dismantling of existing motor control panel of existing old 40HP & 10 HP pump sets including disconnection of LT cable, termination from LT panel and remained all unused cable from E line pump room and shifting to power house of New Airport colony (approx. 4OO mtr from pump room as per direction E.I.C. complete as required. | 3.00 | Job |  | 5000.00 | 15000.00 | 3000.00 | 9000.00 | 9000.00 | PERFECT TECH ENGINEERS
| Total in Figures |  |  |  |  | 3301390.00 |  | 3383910.00
Lowest Amount Quoted BY: Ramesh Electrical and Mechanical Works(3301390.00)

## BOQ Summary
BOQ Summary Details Tender Title: Structural rehabilitation of existing 03 Nos. of RCC Sumps and 01 No. RCC Overhead tank at New Airport Colony, Mumbai. SH Electrical Works Tender ID: 2023_AAI_174670_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ramesh Electrical and Mechanical Works | 3301390.00 | L1
| 2 | PERFECT TECH ENGINEERS | 3383910.00 | L2