## BoQ1
Government eProcurement System Created By: ABHIJIT DATTA Created Date/Time: 28-May-2024 01:45 PM Tender Title: Design, Supply, Installation, Testing and Commissioning of Facade Lighting of New Integrated Terminal Building at NSCBI Airport, Kolkata. Tender ID: 2023_AAI_174782_1
Tender Inviting Authority: Airports Authority of India
Name of Work:-Design, Supply, Installation, Testing and Commissioning of Façade lighting of New Integrated Terminal Building at NSCBI Airport, Kolkata.
Contract No: AAI, NSCBI Airport, Kolkata.
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bajaj Electricals Limited (GSTN-27AAACB2484Q1Z8) BID ID -641941 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -648688 |  | Surya Roshni Limited(GSTN-NA)--647477
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I - SITC WORKS Supply, Installation, Testing & Commissioning of following Luminaries: Supply Installation testing & commissioning of 300W to 350W RGBW surface mounted Narrow to Medium beam luminaire suitable for outdoor applications of Facade Lighting as per AAI requirement. Luminaire luminous flux range shall be more than 12000 lm, CRI of 80 (for only white colour), overall surge protection of ≥ 10kV & IP ≥ 66. Luminaire should be provided with suitable power supply unit and controllable on DMX protocol. High pressure die cast aluminium alloy housing with adjustable base bracket for angle adjustment so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, ingress protected cable connectors, mounting arrangements, etc. as complete as required. LOCATION : NIPTB T2 Terminal Building Departure Canopy Roof & side edge of the terminal building - Working height 5m. | 84.00 | Each | 121736.00 | 53283.00 | 4475772.00 | 62000.00 | 5208000.00 | 74500.00 | 6258000.00 | 4475772.00 | Bajaj Electricals Limited
2.00 | Supply, Testing, Installation & Commissioning of 1 meter length 24W to 30W RGBW surface mounted Wide - Elliptical beam linear continuous luminaire, suitable for outdoor applications of Facade Lighting as per AAI requirement. Luminaire luminous flux range shall be more than 960 lm, CRI of 80 (for only white colour), overall surge protection of ≥ 10kV & IP ≥ 66. Luminaire should be provided with suitable power supply unit and integral part of DMX protocol & the same is controllable. Housing should have suitable mounting arrangements with complete accessories, so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, ingress protected cable connectors, mounting channels, etc. as complete as required. The erection & fabrication of GI mounting supporting structure & clamping arrangements set with SS nut & bolts at the top roof of terminal building to be considered abiding all AAI measures of safety mentioned in ANNEXURE-II. LOCATION : NIPTB T2 Terminal Building Roof Top - Working height 30m from Departure floor level. | 500.00 | Each | 29077.00 | 9378.00 | 4689000.00 | 9250.00 | 4625000.00 | 7250.00 | 3625000.00 | 3625000.00 | Surya Roshni Limited
3.00 | Supply, Testing, Installation & Commissioning of 1 meter length 24W to 30W RGBW surface mounted Wide - Elliptical beam linear continuous luminaire, suitable for outdoor applications of Facade Lighting as per AAI requirement. Luminaire luminous flux range shall be more than 960 lm, CRI of 80 (for only white colour), overall surge protection of ≥ 10kV & IP ≥ 66. Luminaire should be provided with suitable power supply unit and integral part of DMX protocol & the same is controllable. Housing should have suitable mounting arrangements in existing structure with complete accessories, so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, ingress protected cable connectors, mounting channels, etc. as complete as required. LOCATION : NIPTB T2 Terminal Building departure glass canopy - Working height 5m from Departure level. | 750.00 | Each | 24784.00 | 7035.00 | 5276250.00 | 9250.00 | 6937500.00 | 7250.00 | 5437500.00 | 5276250.00 | Bajaj Electricals Limited
4.00 | Supply, Testing, Installation & Commissioning of static warm white 9W to 12W (3000K) surface mounted Medium / Wide beam cylindrical down projector luminaire suitable for outdoor applications of Facade Lighting. Luminaire luminous efficacy ≥ 70 lm/w, CRI of 80 (for only white colour), overall surge protection of ≥ 10kV & IP ≥ 66. The luminaire should have powder coating pressure die cast aluminium housing with minimum 3-4mm thick safety glass. Luminaire shall have suitable power supply unit and mounting accessories as complete as required so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, power connectors etc. LOCATION : NIPTB T2 Terminal Building Departure Canopy Pillar - Working height 3m. | 110.00 | Each | 3744.00 | 4110.00 | 452100.00 | 7935.00 | 872850.00 | 3200.00 | 352000.00 | 352000.00 | Surya Roshni Limited
5.00 | Supply, Testing, Installation & Commissioning of 50W to 55W RGBW surface mounted Round/square projector luminaire with Narrow / Medium / Wide beam or Round/square projector luminaire with Beam Angle 10/15/30/45/60 deg, suitable for outdoor applications of Facade Lighting as per AAI requirement. Luminaire luminous flux range shall be more than 2000 lm, CRI of 80 (for only white colour), overall surge protection of ≥ 10kV & IP ≥ 66. Luminaire should be provided with suitable power supply unit and DMX Decoder integral part of DMX protocol & the same is controllable. High pressure die cast aluminium alloy housing with adjustable base bracket for angle adjustment so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, ingress protected cable connectors, mounting arrangements, etc. as complete as required. LOCATION : NIPTB T2 Terminal Building Arrival Pillar - Working height 10m. | 360.00 | Each | 42420.00 | 12610.00 | 4539600.00 | 16545.00 | 5956200.00 | 15700.00 | 5652000.00 | 4539600.00 | Bajaj Electricals Limited
6.00 | Supply, Testing, Installation & Commissioning of static warm white 100W to 120W (2700K / 3000K) warm surface mounted Medium / Wide beam round/square projector luminaire suitable for outdoor applications of Facade Lighting as per AAI requirement. Luminaire efficacy shall be more than 100 lm/W, overall surge protection of ≥ 10kV & IP ≥ 66. Luminaire should be provided with suitable power supply unit. High pressure die cast aluminium alloy housing with adjustable base bracket for angle adjustment so that the light direction can be adjusted to illuminate desired structural elements including LED drivers, decoders, anchor fastners, ingress protected cable connectors, mounting arrangements, etc. as complete as required. LOCATION : NIPTB T2 Garden area Netaji, national flag & MIG - Working at ground level. | 24.00 | Each | 22220.00 | 20949.00 | 502776.00 | 34500.00 | 828000.00 | 18800.00 | 451200.00 | 451200.00 | Surya Roshni Limited
7.00 | Lighting Panel: Supply, installation, testing & commissioning of 3 Phase, 415V wall mounted, single door Lighting panel with lockable arrangement made from polycarbonate material, 1 no. earth stud on each side face, LED indicating lamps for incomer, copper bus bars and having following: Incomer: 63A 4P MCCB (25kA) - 1no., respective rating 4P 63A contactor -1no., SPD: 40 kV -1 no. Digital Time Switch having following facilities: Precise time programming for - Daily / Weekly, Pulse switching, Simple Reset feature, Weekend programming, Red LED for relay ON Indication, 24 Hr display (Military), Manual Override. Supply Voltage & Frequency: 110 - 240 VAC, +10% / -20 %, 50 / 60 Hz; Memory Locations: 8 On / Off operations, 16 memory locations; Minimum Switching Time: 1 min; Housing: Flame Retardant UL94V0 Outgoing: 10A 3P 'C" Curve MCB (10kA) - 9 nos. | 2.00 | Each | 98728.00 | 117999.00 | 235998.00 | 78760.00 | 157520.00 | 210000.00 | 420000.00 | 157520.00 | Instapower Ltd
8.00 | Supply, Installation testing & commissioning of 3 Phase, 415V Lighting panel, outdoor type with canopy, free standing, double door with lockable arrangement made from polycarbonate material, 1 no. earth stud on each side face, LED indicating lamps for incomer, copper bus bars and having following: Incomer: 63A 4P MCCB (25kA) - 1no., respective rating 4P 63A contactor -1no., SPD: 40 kV -1 no. Digital Time Switch having following facilities: Precise time programming for - Daily / Weekly, Pulse switching, Simple Reset feature, Weekend programming, Red LED for relay ON Indication, 24 Hr display (Military), Manual Override. Supply Voltage & Frequency: 110 - 240 VAC, +10% / -20 %, 50 / 60 Hz; Memory Locations: 8 On / Off operations, 16 memory locations; Minimum Switching Time: 1 min; Housing: Flame Retardant UL94V0 Outgoing:10A 3P MCB (10kA) - 4 nos. | 2.00 | Each | 72215.00 | 143704.00 | 287408.00 | 114380.00 | 228760.00 | 147000.00 | 294000.00 | 228760.00 | Instapower Ltd
9.00 | Supply, Installation testing & commissioning of 3 Phase, 415V Lighting panel, outdoor type with canopy, free standing, double door with lockable arrangement made from polycarbonate material, 1 no. earth stud on each side face, LED indicating lamps for incomer, copper bus bars and having following: Incomer: 63A 4P MCCB (25kA) - 1no., respective rating 4P 63A contactor -1no., SPD: 40 kV -1 no. Digital Time Switch having following facilities: Precise time programming for - Daily / Weekly, Pulse switching, Simple Reset feature, Weekend programming, Red LED for relay ON Indication, 24 Hr display (Military), Manual Override. Supply Voltage & Frequency: 110 - 240 VAC, +10% / -20 %, 50 / 60 Hz; Memory Locations: 8 On / Off operations, 16 memory locations; Minimum Switching Time: 1 min; Housing: Flame Retardant UL94V0 Outgoing: 32A 3P 'C" Curve MCB (10kA) - 2 no. Outgoing: 10A 3P 'C" Curve MCB (10kA) - 4 nos. | 2.00 | Each | 66660.00 | 146685.00 | 293370.00 | 119860.00 | 239720.00 | 165000.00 | 330000.00 | 239720.00 | Instapower Ltd
10.00 | Earthing Materials: Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 6145.00 | 26511.00 | 106044.00 | 4920.00 | 19680.00 | 30000.00 | 120000.00 | 19680.00 | Instapower Ltd
11.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 240.00 | Meter | 49.00 | 43.00 | 10320.00 | 50.30 | 12072.00 | 38.00 | 9120.00 | 9120.00 | Surya Roshni Limited
12.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection / terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 240.00 | Meter | 127.00 | 116.00 | 27840.00 | 134.00 | 32160.00 | 68.00 | 16320.00 | 16320.00 | Surya Roshni Limited
13.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface / recessed conduit / submain wiring / cable as required. | 6100.00 | Meter | 40.00 | 30.00 | 183000.00 | 50.30 | 306830.00 | 48.00 | 292800.00 | 183000.00 | Bajaj Electricals Limited
14.00 | CONTROLLERS- Supply, Installation, Testing and Commissioning of following DMX CONTROL SYSTEM: Supply, Installation, Testing and Commissioning of DMX Controller System with Standalone interfaces. Controller should deliver 3072 DMX channels. The controller should have new Nicolaudie Stand Alone engine (NSA) offering some great possibilities (multi-zone, extended triggers, 16-bit channels management). the controller should offer multiple possibilities to trigger your lighting scenes: time / date, input ports, TCP/UDP commands. The controller should have LS Cloud (Future: activation required) as an optional feature to manage lighting controller from anywhere in the world, at any time using internet connectivity. PC DMX Should have IN triggers, Standalone DMX IN triggers with 512 interfaces, x8 nos. dry (5V) External trigger contacts, Internal calendar, internal clock with power backup of 3 weeks, 4GB minimum micro SD Memory card, input power voltage: 8-15V DC with power adapter via USB (USB power supply included). Trigger lighting scenes using calendar triggers and conditional rules with New Stand-Alone engine, contact ports, RS232 or over Ethernet. Provision of Stand Alone mode with 2000 scenes across 20 zones & Buttons with rotary switch for scene selection. iPhone/iPad/Android remote and programming apps. Temperature: 0 to +50 C°, DMX Compatibility: 8- and 16-bit DMX fixtures, System Compatibility: Windows 10, 11, MAC OS X (10.6 and +), Linux." | 1.00 | Each | 212851.00 | 346906.00 | 346906.00 | 200000.00 | 200000.00 | 49000.00 | 49000.00 | 49000.00 | Surya Roshni Limited
15.00 | Supply, Installation, commissioning, and Testing of 22 AWG DMX cable of single pair stranded (7x30) tinned copper conductors having Datalene (FHDPE) insulation, twisted pairs, overall Beldfoil shield (100% coverage) with tinned copper braid & PVC jacket Cable in PVC conduit alongwith Water proof (IP 66 rating) 3 pin DMX Connector set of flame resistance / anti - UV nylon shell material for connecting DMX cables as complete as required. | 9200.00 | Meter | 253.00 | 157.00 | 1444400.00 | 219.75 | 2021700.00 | 150.00 | 1380000.00 | 1380000.00 | Surya Roshni Limited
16.00 | Supply, installation, Testing and commissioning of Splitter, is a 6-output DMX splitter with capacity of DMX signal boosting. This unit takes the incoming DMX signal and splits the signal into six separate output channels allowing for expanding the number of connecting devices upto 6 x 32 nos. (32 nos/out put). The output terminals are optically isolated from the input and share a common ground reference. All six output ports have an independent output driver and ELV transformer to boost the DMX signal with enclosure (Protection Rating ≥ IP 66) Box for splitter including Water proof 3 pin DMX Connector (IP 66 rating) set of flame resistance / anti - UV nylon shell material for connecting DMX cables as complete as required. | 9.00 | Each | 79176.00 | 52808.00 | 475272.00 | 58500.00 | 526500.00 | 7200.00 | 64800.00 | 64800.00 | Surya Roshni Limited
17.00 | Supply, installation, Testing and commissioning of Splitter, is a -6 output DMX splitter with capacity of DMX signal boosting. This unit takes the incoming DMX signal and splits the signal into six separate output channels allowing for expanding the number of connecting devices upto 6 x 32 nos. (32 nos/out put). The output terminals are optically isolated from the input and share a common ground reference. All two output ports have an independent output driver and ELV transformer to boost the DMX signal with enclosure (Protection Rating ≥ IP 66) Box including Water proof 3 pin DMX Connector (IP 66 rating) set of flame resistance / anti - UV nylon shell material for connecting DMX cables as complete as required. | 9.00 | Each | 51793.00 | 52808.00 | 475272.00 | 58500.00 | 526500.00 | 7200.00 | 64800.00 | 64800.00 | Surya Roshni Limited
18.00 | Supply, installation, Testing and commissioning of Signal Amplifier, Should be specially design for signal shaping & amplification of DMX Master controller's signal which attenuated after a long‐distance transmission, realizing extending the signal transmission distance. DMX Signal amplifier shall increase & distribute multi-channel control. Amplifier shall have optical isolation between input and output terminal, & the same can operate on 220V AC/24V DC. Working temperature shall be (‐10 to 50 Deg Cel). Protection Rating ≥ IP 66 with enclosure (≥ IP 66, ≥ IK 08) Box including Water proof ( ≥ IP 66 rating) 3 pin DMX Connector set of flame resistance / anti - UV nylon shell material for connecting DMX cables as complete as required. | 6.00 | Each | 18685.00 | 6799.00 | 40794.00 | 58500.00 | 351000.00 | 7200.00 | 43200.00 | 40794.00 | Bajaj Electricals Limited
19.00 | Programming charges to complete the Installation, testing and commissioning of complete Façade lighting System as per the simulation decided by AAI as & when required till upto completion of DLP and AMC period with full satisfaction of EIC. | 1.00 | Job | 181800.00 | 158108.00 | 158108.00 | 200000.00 | 200000.00 | 800000.00 | 800000.00 | 158108.00 | Bajaj Electricals Limited
20.00 | Supply of new laptop with specification min. RAM 16GB, min. 512GB SSD, min. intel i5/Ryzen 5 processor, screen size 15.6'', Charger unit, pre loaded original operating windows profocessional software, MS office professional, screen resolution 1920 x 1080 pixel light weight including essential laptop Backpack. Laptop shall be suitable for connecting with DMX controller system & necessary DMX programming software platform to run the entire facade light. make: DELL / HP / IBM / LENOVO. | 1.00 | Each | 42916.00 | 64824.00 | 64824.00 | 44500.00 | 44500.00 | 156000.00 | 156000.00 | 44500.00 | Instapower Ltd
21.00 | LT Cables: Supplying and Laying of one number PVC / XLPE insulated and PVC sheathed armoured power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
21.01 | (a) 4C x 10 sq.mm armoured Copper conductor cable | 200.00 | Meter | 1096.00 | 1033.00 | 206600.00 | 570.04 | 114008.00 | 735.00 | 147000.00 | 114008.00 | Instapower Ltd
21.02 | (b) 3.5C x 70 sq.mm armoured Aluminium conductor cable | 100.00 | Meter | 845.00 | 331.00 | 33100.00 | 453.84 | 45384.00 | 550.00 | 55000.00 | 33100.00 | Bajaj Electricals Limited
22.00 | Supplying and Laying of one number PVC / XLPE insulated and PVC sheathed armoured power cable of 1.1 KV grade of following size on wall surface as required.
22.01 | (a) 4C x 10 sq.mm armoured Copper conductor cable (clamped with 1mm thick saddle) | 2200.00 | Meter | 1102.00 | 661.00 | 1454200.00 | 596.04 | 1311288.00 | 735.00 | 1617000.00 | 1311288.00 | Instapower Ltd
22.02 | (b) 3.5C x 50 sq.mm armoured Aluminium conductor cable (clamped with 25x3mm MS flat clamp) | 100.00 | Meter | 692.00 | 696.00 | 69600.00 | 368.97 | 36897.00 | 400.00 | 40000.00 | 36897.00 | Instapower Ltd
22.03 | (c) 3.5C x 70 sq.mm armoured Aluminium conductor cable (clamped with 25x3mm MS flat clamp) | 300.00 | Meter | 898.00 | 578.00 | 173400.00 | 480.38 | 144114.00 | 550.00 | 165000.00 | 144114.00 | Instapower Ltd
23.00 | Supplying and Laying of one number PVC / XLPE insulated and PVC sheathed armoured power cable of 1.1 KV grade of following size on cable tray as required.
23.01 | (a) 4C x 10 sq.mm armoured Copper conductor cable (clamped with 1mm thick saddle) | 300.00 | Meter | 1096.00 | 440.00 | 132000.00 | 596.04 | 178812.00 | 735.00 | 220500.00 | 132000.00 | Bajaj Electricals Limited
23.02 | (b) 3.5C x 50 sq.mm armoured Aluminium conductor cable (clamped with 25x3mm MS flat clamp) | 100.00 | Meter | 665.00 | 257.00 | 25700.00 | 368.97 | 36897.00 | 405.00 | 40500.00 | 25700.00 | Bajaj Electricals Limited
23.03 | (c) 3.5C x 70 sq.mm armoured Aluminium conductor cable (clamped with 25x3mm MS flat clamp) | 1000.00 | Meter | 870.00 | 342.00 | 342000.00 | 480.38 | 480380.00 | 550.00 | 550000.00 | 342000.00 | Bajaj Electricals Limited
24.00 | Supplying and Laying of one number PVC / XLPE insulated and PVC sheathed armoured power cable of 1.1 KV grade of following size in the existing G.I. trunking with necessary accessories as complete as required.
24.01 | (a) 4C x 10 sq. mm armoured Copper conductor cable | 2200.00 | Meter | 1087.00 | 466.00 | 1025200.00 | 596.04 | 1311288.00 | 735.00 | 1617000.00 | 1025200.00 | Bajaj Electricals Limited
24.02 | (b) 4C x 16 sq. mm armoured Aluminium conductor cable | 600.00 | Meter | 334.00 | 102.00 | 61200.00 | 610.00 | 366000.00 | 212.00 | 127200.00 | 61200.00 | Bajaj Electricals Limited
25.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi core cable in surface / recessed with PVC solid conduit as required.
25.01 | (a) 3C x 1.5 sq. mm | 2250.00 | Meter | 228.00 | 102.00 | 229500.00 | 164.46 | 370035.00 | 75.00 | 168750.00 | 168750.00 | Surya Roshni Limited
25.02 | (b) 3C x 2.5 sq. mm | 200.00 | Meter | 280.00 | 136.00 | 27200.00 | 214.56 | 42912.00 | 120.00 | 24000.00 | 24000.00 | Surya Roshni Limited
26.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi core cable in surface / recessed with GI flexible conduit with PVC coating as required.
26.01 | (a) 3C x 1.5 sq. mm | 2300.00 | Meter | 272.00 | 180.00 | 414000.00 | 269.46 | 619758.00 | 75.00 | 172500.00 | 172500.00 | Surya Roshni Limited
27.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi core cable in surface / recessed with PVC flexible conduit as required.
27.01 | (a) 3C x 1.5 sq. mm | 1660.00 | Meter | 273.00 | 91.00 | 151060.00 | 269.46 | 447303.60 | 75.00 | 124500.00 | 124500.00 | Surya Roshni Limited
27.02 | (b) 3C x 2.5 sq. mm | 200.00 | Meter | 325.00 | 125.00 | 25000.00 | 319.56 | 63912.00 | 120.00 | 24000.00 | 24000.00 | Surya Roshni Limited
28.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi core cable in surface / recessed in the existing G.I. trunking with necessary accessories as complete as required.
28.01 | (a) 3C x 1.5 sq. mm | 850.00 | Meter | 145.00 | 83.00 | 70550.00 | 199.46 | 169541.00 | 75.00 | 63750.00 | 63750.00 | Surya Roshni Limited
28.02 | (b) 3C x 2.5 sq. mm | 500.00 | Meter | 198.00 | 506.00 | 253000.00 | 249.56 | 124780.00 | 120.00 | 60000.00 | 60000.00 | Surya Roshni Limited
29.00 | Supply & termination of following sizes of cables using polyamide glands & Aluminium/ copper lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
29.01 | (a) 3½ X 50 sq. mm (35mm) | 4.00 | Each | 353.00 | 3162.00 | 12648.00 | 790.35 | 3161.40 | 86.00 | 344.00 | 344.00 | Surya Roshni Limited
29.02 | (b) 3½ X 70 sq. mm (38mm) | 8.00 | Each | 387.00 | 1050.00 | 8400.00 | 995.75 | 7966.00 | 114.00 | 912.00 | 912.00 | Surya Roshni Limited
30.00 | Supply & installation of Other Miscellaneous Items. Providing, laying and fixing of 100 mm dia G.I. pipe (medium class) in ground including making suitable trench by cutting of road / drain / pavement, concrete etc. with necessary G.I. fittings, accessories and re-filling etc. as complete as required. | 80.00 | Meter | 1867.00 | 525.00 | 42000.00 | 2078.38 | 166270.40 | 1125.00 | 90000.00 | 42000.00 | Bajaj Electricals Limited
31.00 | Supply, fixing, Testing & Commissioning of 7 mtrs. High octagonal Aluminium pole with bracket suitable for mounting of luminaires for MIG aircraft including exavation, civil foundation & electrical connection etc. as complete as required. | 4.00 | Each | 30300.00 | 24453.00 | 97812.00 | 13838.60 | 55354.40 | 13250.00 | 53000.00 | 53000.00 | Surya Roshni Limited
32.00 | Providing & installing of GI Hot dipped galvanized Maxi trunking of size 75 x 50 mm for laying of cable with necessary fixing arrangements as complete as required. | 1550.00 | Meter | 1677.00 | 116.00 | 179800.00 | 1013.70 | 1571235.00 | 1800.00 | 2790000.00 | 179800.00 | Bajaj Electricals Limited
33.00 | Supply, Installation, Testing and Commissioning of one Polycarbonate weatherproof junction box suitable for outdoor installation with ingress protection 65 or above, with knokouts for cable entry and exit of following sizes with stud type terminal suitable for terminating XLPE insulated armoured aluminium cables in & out and along with 1 no. breather, gland socket etc. with necessary accessories as complete as required.
33.01 | (a) 155 x 210 x 92 mm | 240.00 | Each | 2729.00 | 1553.00 | 372720.00 | 2714.30 | 651432.00 | 630.00 | 151200.00 | 151200.00 | Surya Roshni Limited
33.02 | (b) 225 x 295 x 122 mm | 100.00 | Each | 13850.00 | 2118.00 | 211800.00 | 8695.00 | 869500.00 | 1050.00 | 105000.00 | 105000.00 | Surya Roshni Limited
34.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
34.01 | (a) 150 mm width X 50 mm depth X 1.6 mm thickness | 1200.00 | Meter | 535.00 | 893.00 | 1071600.00 | 517.45 | 620940.00 | 412.00 | 494400.00 | 494400.00 | Surya Roshni Limited
34.02 | (b) 300 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Meter | 615.00 | 1133.00 | 113300.00 | 816.00 | 81600.00 | 650.00 | 65000.00 | 65000.00 | Surya Roshni Limited
35.00 | Providing service of air conditioned 7 seater capacity four wheeler vehicle not more than two years old with Valid Commercial license, in good running condition either petrol or diesel driven (Bolero/Sumo) etc. with Driver and fuel, mobil oil etc for movement of engineering AAI officials for supervision of site work & other official work, all complete as per direction and satisfaction of Engg-In-Charge.(Average running per month is estimated as 1000 Km including all-expense paid for 10 hours a day any time including Saturday, Sunday, Public Holidays as per site work requirement). Any difference in monthly running will be compenseted/deducted on pro-rata basis.Log book for daily use to be maintained.). The rate includes all charges Nothing extra shall be paid for ADP and operational area permit etc. | 6.00 | Month | 44440.00 | 86960.00 | 521760.00 | 80000.00 | 480000.00 | 7946.25 | 47677.50 | 47677.50 | Surya Roshni Limited
36.00 | SH: II - AICMC Charge for All inclusive Comprehensive maintenance of above systems including periodic maintenance (once per quarter) for 5 years after defect liability period of 2 years with manpower and material.
36.01 | a) For First year after DLP period of 2 years (1.01% of SITC Cost) | 12.00 | Month | 66621.33 | 317243.06 | 317243.06 | 400619.13 | 400619.13 | 351782.73 | 351782.73 | 317243.06 | Bajaj Electricals Limited
36.02 | b) For Second year (1.52% of SITC Cost) | 12.00 | Month | 100261.75 | 477435.10 | 477435.10 | 602911.96 | 602911.96 | 529415.60 | 529415.60 | 477435.10 | Bajaj Electricals Limited
36.03 | c) For Third year (2.02% of SITC Cost) | 12.00 | Month | 133242.58 | 634486.12 | 634486.12 | 801238.27 | 801238.27 | 703565.46 | 703565.46 | 634486.12 | Bajaj Electricals Limited
36.04 | d) For Forth year (2.53% of SITC Cost) | 12.00 | Month | 166883.08 | 794678.16 | 794678.16 | 1003531.10 | 1003531.10 | 881198.33 | 881198.33 | 794678.16 | Bajaj Electricals Limited
36.05 | e) For Fifth year (3.03% of SITC Cost) | 12.00 | Month | 199863.92 | 951729.18 | 951729.18 | 1201857.40 | 1201857.40 | 1055348.20 | 1055348.20 | 951729.18 | Bajaj Electricals Limited
| Total in Figures |  |  |  |  | 34585775.62 |  | 43675418.66 |  | 38351283.82
Lowest Amount Quoted BY: Bajaj Electricals Limited(34585775.62)

## BOQ Summary
BOQ Summary Details Tender Title: Design, Supply, Installation, Testing and Commissioning of Facade Lighting of New Integrated Terminal Building at NSCBI Airport, Kolkata. Tender ID: 2023_AAI_174782_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Bajaj Electricals Limited | 34585775.62 | L1
| 2 | Surya Roshni Limited | 38351283.82 | L2
| 3 | Instapower Ltd | 43675418.66 | L3