## BoQ1
Government eProcurement System Created By: MD Sadrul Huda Created Date/Time: 27-Dec-2023 03:37 PM Tender Title: Reconfiguration of Existing Terminal Building at C.E. Bhuj. SH- SITC of 400 KVA DG Sets and associated electrical works at Bhuj Airport Tender ID: 2023_AAI_175332_1
Tender Inviting Authority: Asst.General Manager (E-E)
Name of Work:“ Reconfiguration of Existing Terminal Building at C.E. Bhuj.SH: SITC of 400 KVA DG Sets and associated electrical works at Bhuj Airport."
Tender ID: 2023_AAI_175332_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | EVERCREST PROJECTS PVT LTD(GSTN-24AADCE7826L1ZE) |  | HINDUSTAN ELECTRIC COMPANY(GSTN-24AABFH3759C1ZQ) |  | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | Patel Electricals(GSTN-NA) |  | girnar electricals(GSTN-NA) |  | Virtus Techno(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Diesel Generating Sets Providing, Installing, Testing and Commissiong of 'Silent Type' Diesel Generating set (CPCB4+ complaint) alongwith having Prime Power Rating 400 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor and consisting of the followings: a) Diesel Engine: Diesel engine 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 45 degree C, 50% RH & at 1000 meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continous operation. The engine will be fitted complete with all the required accessories. b) Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low lub. Oil trip indication (ix) Engine Hours indication c) Alternator: Synchronous alternator rated at 400 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 45 Degree C, 50% RH & at 1000 meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self excited and self regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical condiitions and with class -F/H insulation. | 2.00 | Job |  | 4093140.00 | 8186280.00 | 4740708.00 | 9481416.00 | 4500000.00 | 9000000.00 | 3945205.00 | 7890410.00 | 3800000.00 | 7600000.00 | 3755000.00 | 7510000.00 | 4070000.00 | 8140000.00 | 7510000.00 | girnar electricals
1.01 | d) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. e) Exhaust System: Dry exhaust mainfold with Residential exhaust silencer and catalytic convertor. f) Starting System: 24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand (25 plates, 180 Amp. Hour capacity lead acid type) as required as per specifications. g) Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. The work should be as per Central Electrical Authority / Pollution control board standards & as per tender condition.
2.00 | AMF Panel Fabricating, Supply, Installation, Testing and Commissioning of MV Switch Panel board - Automatic Mains Failure (AMF) Control Panel made of 14 SWG CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, suitable for 400 KVA DG Set, 3 phase, 4 wire, 50 Hz, AC system complete with all accessories, control cabling from AMF panel to diesel engine and elsewhere if required, interconnection, connection, earthing, painting etc. as required and comprising of following: a) 02 Nos. of 630 A, 50KA, 4P MCCBs with microprocessor based releases for OC/SC/EF Protection, C.T. operated Digital Meter [EM 6400 of Conzerve/Equivalent], each for EB Supply and Gen Set Supply, ON/OFF/TRIP Indication, and Phase Indication Lamps. b) 02 Nos. of 630 A, 4P Power Contactors each for EB Supply and Gen Set Supply. c) 02 Nos. of 630 A, 4P Change Over Switches for Bye-Pass Arrangements each for EB Supply and Gen Set Supply. d) 24 V Battery Charger consisting of transformer, rectifier, DC Ammeter, DC Volt Meter and charge rate selector switch with position ON/Trickle/OFF/Boost for charging capacity of suitable for 24 Volts , 180 AH lead acid batteries etc. e) 01 Set of Timers and Contactors/AMF Relay for Start with Condition to take load within 15 Sec. in 3 Attempts/Stop/Delay Time of DG Set with Selector Switch for Time Delay, Contactors for Auto/Manual/Interlock/Time Delay etc.as required f) 01 Set of Selector Swiches for Auto/Manual/Test/Off Operation, One Set of LVM, One Set of Push Button for Start/Stop/Reset etc. g) One Set of 5 mm, 3 LED Display for Performance of DG Set. h) One Hooter to alarm the abnormality of DG Set and Annunciation Windows for Performance and Operation of DG Set etc. i) 01 set of 800 A TPN Aluminium Bus bar j) 02 Nos. out goings of 400 A, 36KA, 4P MCCBs with microprocessor based releases for OC/SC Protection, C.T. operated Digital ammeter for each outgoing of MCCB , ON/OFF Indication Lamps. k) 01 No. out going of 250 A, 36KA, 4P MCCBs with microprocessor based releases for OC/SC Protection, C.T. operated Digital ammeter for each outgoing of MCCB , ON/OFF Indication Lamps. | 2.00 | set |  | 772700.00 | 1545400.00 | 450000.00 | 900000.00 | 700000.00 | 1400000.00 | 880000.00 | 1760000.00 | 343000.00 | 686000.00 | 477000.00 | 954000.00 | 687500.00 | 1375000.00 | 686000.00 | Patel Electricals
2.01 | l) Audio/Video annunciation for: (i) High water temperature (ii) Low lubricating oil pressure (iii) Engine over speed (iv) Engine fails to start (v) Full load/maximum load warning m) Space for spare compartments. All accessories such as fuses, auxillary contactors, auxillary switches etc.
3.00 | Supplying and fixing exhaust gas piping for 400 kVA D.G. set with 150mm dia. (or as per OEM) welded black MS pipe (Class-B) conforming to IS:1239 (part-I, 2004) cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, SS Expansion Joints, insulation of exhaust system with mineral wool/Rockwool, 50 mm thick wiremesh & aluminum cladding etc., complete as required as per specifications. | 25.00 | metre |  | 5173.00 | 129325.00 | 4500.00 | 112500.00 | 4000.00 | 100000.00 | 7000.00 | 175000.00 | 1500.00 | 37500.00 | 2700.00 | 67500.00 | 12880.00 | 322000.00 | 37500.00 | Patel Electricals
4.00 | Supplying and Laying of fuel piping between fuel tank and each diesel engine with MS class ‘C’ pipes of 25mm dia. (or as per OEM) on floors complete with valves, flanges, gaskets, joints , nutbolts, unions, level indications on Fuel tank & all accessories etc complete as required as per the site condition. | 20.00 | metre |  | 759.00 | 15180.00 | 100.00 | 2000.00 | 500.00 | 10000.00 | 1000.00 | 20000.00 | 500.00 | 10000.00 | 325.00 | 6500.00 | 952.00 | 19040.00 | 2000.00 | HINDUSTAN ELECTRIC COMPANY
5.00 | Dismantling of Exisitng 160 KVA acoustic enclosure type DG sets along with AMF panels, removing terminations, cable connections, Diesel Tanks including shifting to store or as directed by E-I-C complete as required. | 2.00 | Job |  | 30000.00 | 60000.00 | 3600.00 | 7200.00 | 15000.00 | 30000.00 | 50000.00 | 100000.00 | 30000.00 | 60000.00 | 9000.00 | 18000.00 | 16800.00 | 33600.00 | 7200.00 | HINDUSTAN ELECTRIC COMPANY
6.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 4.00 | cum |  | 9200.00 | 36800.00 | 3366.00 | 13464.00 | 7000.00 | 28000.00 | 6800.00 | 27200.00 | 100000.00 | 400000.00 | 8500.00 | 34000.00 | 7280.00 | 29120.00 | 13464.00 | HINDUSTAN ELECTRIC COMPANY
7.00 | SITC of LT Panel (Essential) Supplying, installation, testing & commissioning of cubical, floor mounted, indoor type, dust and verming proof and having IP 42 protection LT panel suitable for 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in totally enclosed and compartmentalized design from CRCA sheet steel of 2 mm thick for load bearing members & 1.6 mm thick for doors, 3 mm thick for gland plates i/c cleaning & finishing complete with powder coating in approved shade, TPN Aluminium Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, suitable angle /channels frame in the bottom. Fabrication shall be done in transportable sections, connections from main bus bars to switch gears with required size of copper/aluminium solid conductors/bus bars and control wiring with 2.5 sq. mm PVC insulated copper conductor , cable alleys, cable gland plates in two half , Control MCBs etc. as required as per technical specifications i/c providing following switch gears and accessories: Incomer and Bus coupler (2+1) 630 Amp 4 pole (50 KA, lcs = 100% lcu) MCCB with Microprocessor release, Overcurrent/Short circuit/ Earth Fault protection, shunt trip coil, Auxilary contact, Extended Direct Rotary Handle, Spreaders, etc - 3 sets which shall be mutually mechanical & electrically interlocked by control key system between Two incomers and Bus coupler for safe operation. Bus Bars 800 Amp. TPN bus bars of aluminium alloy of suitable size as per technical specifications. Outgoings A) 400 Amp. 4 Pole, 50 KA, (lcs=100%lcu) MCCB with spreaders, ROH -1 Nos. B) 250 Amp. 4 Pole, 50 KA, (lcs=100%lcu) MCCB with spreaders, ROH -3 Nos C) 160 Amp. 4 Pole, 50 KA, (lcs=100%lcu) MCCB with spreaders, ROH -2 Nos D) 100 Amp. 4 Pole, 35 KA, (lcs=100%lcu) MCCB with spreaders, ROH -8 Nos. Instrumentation A) 2 Nos. VAF + PF Meter having class 0.5 Accuracy with suitable CTs/PTs, Class 0.5 accuracy. B) 12 Nos. Three phase Digital Ammeter having class 0.5 Accuracy with suitable CTs, Class 0.5 accuracy. C) 03 nos LED phase indicating lights (RYB) with protection MCB/fuses for each incomer. D) 03 nos ON/OFF/TRIP LED indicating lamps for each I/C and Buscoupler; & 01 no ON indicating lamp for each O/G MCCB. | 1.00 | set |  | 1107775.00 | 1107775.00 | 740000.00 | 740000.00 | 700000.00 | 700000.00 | 675000.00 | 675000.00 | 480000.00 | 480000.00 | 860000.00 | 860000.00 | 1057100.00 | 1057100.00 | 480000.00 | Patel Electricals
8.00 | Supply of heavy duty XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098, Part-I 1988 with up to date amendments of following size and confirm to technical specifications enclosed.
8.10 | 3.5C X 400 Sq.mm | 270.00 | metre |  | 1573.00 | 424710.00 | 900.00 | 243000.00 | 1400.00 | 378000.00 | 1537.00 | 414990.00 | 1800.00 | 486000.00 | 1800.00 | 486000.00 | 1425.87 | 384984.90 | 243000.00 | HINDUSTAN ELECTRIC COMPANY
8.20 | 3.5C X 240 Sq.mm | 60.00 | metre |  | 1007.00 | 60420.00 | 630.00 | 37800.00 | 950.00 | 57000.00 | 985.00 | 59100.00 | 1150.00 | 69000.00 | 1150.00 | 69000.00 | 912.80 | 54768.00 | 37800.00 | HINDUSTAN ELECTRIC COMPANY
9.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
9.10 | 750 mm width X 62.5 mm depth X 2.0 mm thickness. | 65.00 | metre |  | 1816.00 | 118040.00 | 720.00 | 46800.00 | 2000.00 | 130000.00 | 2180.00 | 141700.00 | 2000.00 | 130000.00 | 1450.00 | 94250.00 | 1680.00 | 109200.00 | 46800.00 | HINDUSTAN ELECTRIC COMPANY
9.20 | 375 mm width X 62.5 mm depth X 2.0 mm thickness. | 65.00 | metre |  | 1054.00 | 68510.00 | 540.00 | 35100.00 | 1500.00 | 97500.00 | 1800.00 | 117000.00 | 690.00 | 44850.00 | 900.00 | 58500.00 | 980.00 | 63700.00 | 35100.00 | HINDUSTAN ELECTRIC COMPANY
10.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “bends“ (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
10.10 | 750 mm width X 62.5 mm depth X 2.0 mm thickness | 4.00 | each |  | 4301.00 | 17204.00 | 180.00 | 720.00 | 3000.00 | 12000.00 | 4400.00 | 17600.00 | 2500.00 | 10000.00 | 1450.00 | 5800.00 | 3360.00 | 13440.00 | 720.00 | HINDUSTAN ELECTRIC COMPANY
10.20 | 375 mm width X 62.5 mm depth X 2.0 mm thickness | 2.00 | each |  | 2478.00 | 4956.00 | 180.00 | 360.00 | 1800.00 | 3600.00 | 2700.00 | 5400.00 | 1000.00 | 2000.00 | 900.00 | 1800.00 | 1960.00 | 3920.00 | 360.00 | HINDUSTAN ELECTRIC COMPANY
11.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “Tee” (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 750 mm width X 62.5 mm depth X 2.0 mm thickness. | 4.00 | each |  | 5147.00 | 20588.00 | 144.00 | 576.00 | 10000.00 | 40000.00 | 5600.00 | 22400.00 | 3000.00 | 12000.00 | 1450.00 | 5800.00 | 4200.00 | 16800.00 | 576.00 | HINDUSTAN ELECTRIC COMPANY
12.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “Reducer” (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 750 mm width X 62.5 mm depth X 2.0 mm thickness | 4.00 | each |  | 6837.00 | 27348.00 | 144.00 | 576.00 | 1500.00 | 6000.00 | 5600.00 | 22400.00 | 4420.00 | 17680.00 | 1450.00 | 5800.00 | 3360.00 | 13440.00 | 576.00 | HINDUSTAN ELECTRIC COMPANY
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 185 Sq. mm and upto 400 Sq. mm (clamped with 40 x 3 mm MS flat clamp). | 270.00 | metre |  | 168.00 | 45360.00 | 108.00 | 29160.00 | 150.00 | 40500.00 | 150.00 | 40500.00 | 150.00 | 40500.00 | 120.00 | 32400.00 | 168.00 | 45360.00 | 29160.00 | HINDUSTAN ELECTRIC COMPANY
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed aluminium conductor cable of 1.1 KV grade as required.
14.10 | 3.5C X 400 sq. mm (82mm) | 12.00 | set |  | 3709.00 | 44508.00 | 18.00 | 216.00 | 1200.00 | 14400.00 | 3600.00 | 43200.00 | 1800.00 | 21600.00 | 900.00 | 10800.00 | 1512.00 | 18144.00 | 216.00 | HINDUSTAN ELECTRIC COMPANY
14.20 | 3.5C X 240 sq. mm (62mm) | 4.00 | set |  | 2515.00 | 10060.00 | 18.00 | 72.00 | 800.00 | 3200.00 | 2400.00 | 9600.00 | 1300.00 | 5200.00 | 750.00 | 3000.00 | 1344.00 | 5376.00 | 72.00 | HINDUSTAN ELECTRIC COMPANY
15.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | set |  | 19546.00 | 78184.00 | 18000.00 | 72000.00 | 18000.00 | 72000.00 | 13500.00 | 54000.00 | 20000.00 | 80000.00 | 11000.00 | 44000.00 | 12432.00 | 49728.00 | 44000.00 | girnar electricals
16.00 | Earthing with G.I.earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | set |  | 10238.00 | 40952.00 | 4500.00 | 18000.00 | 7500.00 | 30000.00 | 6500.00 | 26000.00 | 8500.00 | 34000.00 | 8000.00 | 32000.00 | 5264.00 | 21056.00 | 18000.00 | HINDUSTAN ELECTRIC COMPANY
17.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | metre |  | 1820.00 | 54600.00 | 1008.00 | 30240.00 | 1500.00 | 45000.00 | 1310.00 | 39300.00 | 2400.00 | 72000.00 | 1350.00 | 40500.00 | 1069.60 | 32088.00 | 30240.00 | HINDUSTAN ELECTRIC COMPANY
18.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | metre |  | 707.00 | 14140.00 | 270.00 | 5400.00 | 750.00 | 15000.00 | 490.00 | 9800.00 | 450.00 | 9000.00 | 450.00 | 9000.00 | 106.40 | 2128.00 | 2128.00 | Virtus Techno
19.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | metre |  | 1259.00 | 25180.00 | 810.00 | 16200.00 | 1100.00 | 22000.00 | 950.00 | 19000.00 | 2400.00 | 48000.00 | 950.00 | 19000.00 | 1069.60 | 21392.00 | 16200.00 | HINDUSTAN ELECTRIC COMPANY
20.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 80.00 | metre |  | 146.00 | 11680.00 | 90.00 | 7200.00 | 200.00 | 16000.00 | 130.00 | 10400.00 | 450.00 | 36000.00 | 175.00 | 14000.00 | 106.41 | 8512.80 | 7200.00 | HINDUSTAN ELECTRIC COMPANY
| Total in Figures |  |  |  |  | 12147200.00 |  | 11800000.00 |  | 12250200.00 |  | 11700000.00 |  | 10391330.00 |  | 10381650.00 |  | 11839897.70
Lowest Amount Quoted BY: girnar electricals(10381650.00)

## BOQ Summary
BOQ Summary Details Tender Title: Reconfiguration of Existing Terminal Building at C.E. Bhuj. SH- SITC of 400 KVA DG Sets and associated electrical works at Bhuj Airport Tender ID: 2023_AAI_175332_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | girnar electricals | 10381650.00 | L1
| 2 | Patel Electricals | 10391330.00 | L2
| 3 | Mona Generator Services Pvt. Ltd. | 11700000.00 | L3
| 4 | HINDUSTAN ELECTRIC COMPANY | 11800000.00 | L4
| 5 | Virtus Techno | 11839897.70 | L5
| 6 | EVERCREST PROJECTS PVT LTD | 12147200.00 | L6
| 7 | DOSHI ELECTRIC ENGG. CO. | 12250200.00 | L7