## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 29-Nov-2024 12:07 PM Tender Title: Provision of Ring main Power Supply System for NAV-AIDS at Dibrugarh Airport Tender ID: 2023_AAI_175583_1
Tender Inviting Authority: AAI, Dibrugarh Airport
Name of Work: Provision of Ring main Power Supply System for NAV-AIDS at Dibrugarh Airport
Contract No: 2023_AAI_175583_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -646349
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 3.5CX 240 sq.mm size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. (Make: As per AAI list of approved makes) | 7320.00 | Mtr |  | 1300.00 | 9516000.00 | 9516000.00 | REWINDER TECHNO ELECTRICALS
2.00 | Supply of 3.5CX 70 sq.mm size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. (Make: As per AAI list of approved makes) | 200.00 | Mtr |  | 400.00 | 80000.00 | 80000.00 | REWINDER TECHNO ELECTRICALS
3.00 | Supply of 160 mm dia HDPE pipe, lSI marked along with all accessories like socket, couplers etc. conforming to IS 4984-1995, PN6 grade, PE63 etc | 450.00 | Mtr |  | 700.00 | 315000.00 | 315000.00 | REWINDER TECHNO ELECTRICALS
4.00 | Supply of 110 mm dia HDPE pipe, lSI marked along with all accessories like socket, couplers etc. conforming to IS 4984-1995, PN4 grade, PE63 etc | 6460.00 | Mtr |  | 350.00 | 2261000.00 | 2261000.00 | REWINDER TECHNO ELECTRICALS
5.00 | Supply of 63 mm dia HDPE pipe, lSI marked along with all accessories like socket, couplers etc. conforming to IS 4984-1995, PN4 grade, PE63 etc | 150.00 | Mtr |  | 200.00 | 30000.00 | 30000.00 | REWINDER TECHNO ELECTRICALS
6.00 | Laying of HDPE/ DWC pipe of 63 mm dia size complete with fitting and cutting, jointing or including butt joint welding wherever required etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 150.00 | Mtr |  | 50.00 | 7500.00 | 7500.00 | REWINDER TECHNO ELECTRICALS
7.00 | Laying of HDPE/ DWC of pipe 110mm dia size complete with fitting and cutting, jointing or including butt joint welding wherever required etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 6460.00 | Mtr |  | 30.00 | 193800.00 | 193800.00 | REWINDER TECHNO ELECTRICALS
8.00 | Laying of one number HDPE pipe of size 160 mm dia by making Horizontal boring using suitable mechanical arrangement, Sensor operated, Min. 2 Mtr Depth including butt joint welding of HDPE pipe, inserting of HDPE Pipes in bore well hole etc., complete is required. | 450.00 | Mtr |  | 200.00 | 90000.00 | 90000.00 | REWINDER TECHNO ELECTRICALS
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required Above 35 sq. mm and upto 95 sq. mm | 150.00 | Mtr |  | 5.00 | 750.00 | 750.00 | REWINDER TECHNO ELECTRICALS
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required Above 185 sq. mm and upto 400 sq. mm | 6860.00 | Mtr |  | 8.00 | 54880.00 | 54880.00 | REWINDER TECHNO ELECTRICALS
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KVgrade of size in the existing masonry open duct as required Above 35 sqmm and upto 95 sqmm | 50.00 | mtr |  | 5.00 | 250.00 | 250.00 | REWINDER TECHNO ELECTRICALS
12.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KVgrade of size in the existing masonry open duct as required Above 185 sq. mm and upto 400 sq. mm | 250.00 | Mtr |  | 5.00 | 1250.00 | 1250.00 | REWINDER TECHNO ELECTRICALS
13.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3.5X 240 sq.mm PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 9.00 | Each |  | 2000.00 | 18000.00 | 18000.00 | REWINDER TECHNO ELECTRICALS
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5X 70 sq. mm (38mm) | 4.00 | Set |  | 200.00 | 800.00 | 800.00 | REWINDER TECHNO ELECTRICALS
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 X 240 sq. mm (62mm) | 10.00 | Set |  | 200.00 | 2000.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
16.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meter in width, and lift upto 1.5 meter, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meter. | 5.00 | Cum |  | 200.00 | 1000.00 | 1000.00 | REWINDER TECHNO ELECTRICALS
17.00 | Supply, Installation, Testing and Commissioning of 415V, 50Hz, AC supply totally enclosed with self standing floor mounting, cubicle type, dust and vermin proof , indoor compartmentalized, Double door , IP65, outdoor type, sloped roof LT panel fabricated from 2mm thick CRCA sheet with Bus bars, earth bar connections including internal wiring with suitable sizes wire/cable, interconnection, duly powder coated, painting etc,. The panel shall have provision for bottom cable entry, including supply and installations of following switchgears, metering instruments and accessories in the LT Panel and as per technical specifications. INCOMMER MCCB a) 160 Amps, Four Pole Moulded Case Circuit Breaker having adjustable Thermal ( 80% - 100% ) with Rotary handle and the Breaking capacity Icu at 415 V, 36 kA - 2 No. b) Set of indication lamps, LED type for R, Y, B, with HRC control fuse- 2 set c) Digital type 3 phase multi function meter - 2 No d)Bus coupler : 160 Amps, Four Pole Moulded Case Circuit Breaker having adjustable Thermal ( 80% - 100% ) and Fixed Magnetic Release with Rotary handle and the Breaking capacity Icu at 415 V, 36 kA - 1 No. with 2 keys systems mechanical interlocking arrangement with two incomers - 1Set. e) One set of 200 Amp. TPN copper bus bars of suitable rupturing capacity OUT GOINGS a) 160 Amps, Four Pole Moulded Case Circuit Breaker having adjustable Thermal ( 80% - 100% ) with Rotary handle and the Breaking capacity Icu at 415 V, 36 kA - 2 No. b) 100 Amps, Four Pole Moulded Case Circuit Breaker having adjustable Thermal ( 80% - 100% ) with Rotary handle and the Breaking capacity Icu at 415 V, 25 kA - 3 No. Note : Each MCCB outgoings shall be provided with ON/OFF/TRIP indication | 4.00 | Job |  | 50000.00 | 200000.00 | 200000.00 | REWINDER TECHNO ELECTRICALS
18.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 8.00 | Set |  | 3000.00 | 24000.00 | 24000.00 | REWINDER TECHNO ELECTRICALS
19.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Mtr |  | 200.00 | 10000.00 | 10000.00 | REWINDER TECHNO ELECTRICALS
20.00 | Constructing masonry Chamber 120x120x100 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 M sand) , with RCC top slab 1:2:4 mix (1 cement : 2 M sand : 4 graded stone aggregate 20 mm nominal size ), i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 M sand : 10 graded stone aggregate 40 mm nominal size ) and inside plastering with cement mortar 1:3 (1 cement : 3M sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design : | 8.00 | Each |  | 3000.00 | 24000.00 | 24000.00 | REWINDER TECHNO ELECTRICALS
21.00 | Supply, Installation, Testing and Commissioning of smart RFID based electronic cable marker 220 mm dia, 1.5 m depth range 10 digit hexadecimal ID code as per direction of Engineer-in-charge. | 100.00 | Each |  | 1000.00 | 100000.00 | 100000.00 | REWINDER TECHNO ELECTRICALS
22.00 | Supply and Fixing of Outdoor type (IP65) Junction Box suityable for termination of 3.5C X 240 sqmm cable( 2 nos- 1 incoming & 1 outgoing) along with suitable Aluminum busbars, suitable support insulators etc.,and MS stand for fixing with excavation, making foundation with PCC completely as per direction of Engineer In Charge. | 3.00 | Each |  | 2000.00 | 6000.00 | 6000.00 | REWINDER TECHNO ELECTRICALS
23.00 | Providing and laying in position cement concrete of specified grade 1:2:4(1 Cement:2Coarse sand :4 graded stone aggregate 20mm nominal size) at all levels for damaged portion of wall/road/paver block portion etc., complete as required. | 5.00 | Cumtr |  | 2006.00 | 10030.00 | 10030.00 | REWINDER TECHNO ELECTRICALS
| Total in Figures |  |  |  |  | 12946260.00
Lowest Amount Quoted BY: REWINDER TECHNO ELECTRICALS(12946260.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Ring main Power Supply System for NAV-AIDS at Dibrugarh Airport Tender ID: 2023_AAI_175583_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | REWINDER TECHNO ELECTRICALS (BID ID -646349) | 12946260.00 | L1