## BoQ1
Government eProcurement System Created By: Sateesh Kr Kanaujiya Created Date/Time: 15-Dec-2023 04:02 PM Tender Title: Reconfiguration of Existing Terminal building at Aurangabad Airport. SH Internal Electrical work, fire work, building signages work and Fountain type water cooler. Tender ID: 2023_AAI_175870_1
Tender Inviting Authority: Senior Manager (Engg.-Electrical), Airports Authority of India, Aurangabad Airport, Aurangabad- 431007.
Name of Work: Reconfiguration of Existing Terminal building at Aurangabad Airport. SH: Internal Electrical work ,fire work, building signages work & Fountain type water cooler.
Tender ID : 2023_AAI_175870_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RAJSON ELECTRONS(GSTN-27ABIPW2620D1ZR) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | A K TECHNOCRATS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 175.00 | Point |  | 1700.00 | 297500.00 | 1400.00 | 245000.00 | 1500.00 | 262500.00 | 245000.00 | Awasthi Electric Works
2.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 110.00 | Point |  | 950.00 | 104500.00 | 750.00 | 82500.00 | 925.00 | 101750.00 | 82500.00 | Awasthi Electric Works
3.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 2000.00 | Meter |  | 450.00 | 900000.00 | 370.00 | 740000.00 | 430.00 | 860000.00 | 740000.00 | Awasthi Electric Works
4.01 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in existing surface/ recessed steel conduit/raceway as required. 2 X 1.5 sq. mm +1 X 1.5 sq. mm earth wire | 300.00 | Meter |  | 200.00 | 60000.00 | 280.00 | 84000.00 | 175.00 | 52500.00 | 52500.00 | A K TECHNOCRATS
4.02 | 2 X 2.5 sq. mm +1 X 2.5 sq. mm earth wire | 2570.00 | Meter |  | 200.00 | 514000.00 | 300.00 | 771000.00 | 140.00 | 359800.00 | 359800.00 | A K TECHNOCRATS
4.03 | 2 X 4 sq. mm +1 X 4 sq. mm earth wire | 4980.00 | Meter |  | 300.00 | 1494000.00 | 315.00 | 1568700.00 | 210.00 | 1045800.00 | 1045800.00 | A K TECHNOCRATS
4.04 | 2 X 6 sq. mm +1 X 6 sq. mm earth wire | 480.00 | Meter |  | 300.00 | 144000.00 | 360.00 | 172800.00 | 300.00 | 144000.00 | 144000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
5.01 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 20 mm | 300.00 | Meter |  | 350.00 | 105000.00 | 200.00 | 60000.00 | 310.00 | 93000.00 | 60000.00 | Awasthi Electric Works
5.02 | 25 mm | 2190.00 | Meter |  | 230.00 | 503700.00 | 240.00 | 525600.00 | 210.00 | 459900.00 | 459900.00 | A K TECHNOCRATS
5.03 | 32 mm | 200.00 | Meter |  | 550.00 | 110000.00 | 300.00 | 60000.00 | 510.00 | 102000.00 | 60000.00 | Awasthi Electric Works
6.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 20.00 | Each |  | 910.00 | 18200.00 | 380.00 | 7600.00 | 900.00 | 18000.00 | 7600.00 | Awasthi Electric Works
7.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 50.00 | Each |  | 1500.00 | 75000.00 | 480.00 | 24000.00 | 1500.00 | 75000.00 | 24000.00 | Awasthi Electric Works
8.01 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. 1 or 2 Module (75mm X 75mm) | 20.00 | Each |  | 400.00 | 8000.00 | 190.00 | 3800.00 | 350.00 | 7000.00 | 3800.00 | Awasthi Electric Works
8.02 | 6 Module (200mm X 75mm) | 85.00 | Each |  | 550.00 | 46750.00 | 335.00 | 28475.00 | 510.00 | 43350.00 | 28475.00 | Awasthi Electric Works
8.03 | 8 Module (125mm X 125mm) | 30.00 | Each |  | 650.00 | 19500.00 | 380.00 | 11400.00 | 650.00 | 19500.00 | 11400.00 | Awasthi Electric Works
8.04 | 12 Module (200mm X 150mm) | 30.00 | Each |  | 950.00 | 28500.00 | 477.00 | 14310.00 | 930.00 | 27900.00 | 14310.00 | Awasthi Electric Works
9.01 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 5/6 A switch | 40.00 | Each |  | 200.00 | 8000.00 | 90.00 | 3600.00 | 175.00 | 7000.00 | 3600.00 | Awasthi Electric Works
9.02 | 15/16 A switch | 100.00 | Each |  | 300.00 | 30000.00 | 115.00 | 11500.00 | 275.00 | 27500.00 | 11500.00 | Awasthi Electric Works
9.03 | 6 pin 15/16 A socket outlet | 100.00 | Each |  | 375.00 | 37500.00 | 155.00 | 15500.00 | 375.00 | 37500.00 | 15500.00 | Awasthi Electric Works
9.04 | Telephone socket outlet | 5.00 | Each |  | 3300.00 | 16500.00 | 115.00 | 575.00 | 275.00 | 1375.00 | 575.00 | Awasthi Electric Works
10.01 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 6 way (2+4), Double Door | 6.00 | Each |  | 1800.00 | 10800.00 | 2400.00 | 14400.00 | 1800.00 | 10800.00 | 10800.00 | A K TECHNOCRATS, RAJSON ELECTRONS
10.02 | 8 way (2+6), Double Door | 8.00 | Each |  | 2000.00 | 16000.00 | 2850.00 | 22800.00 | 1900.00 | 15200.00 | 15200.00 | A K TECHNOCRATS
10.03 | 12 way (2+10), Double Door | 3.00 | Each |  | 2500.00 | 7500.00 | 3400.00 | 10200.00 | 2500.00 | 7500.00 | 7500.00 | A K TECHNOCRATS, RAJSON ELECTRONS
11.00 | Supplying and fixing of 6 way (8 +18), double door , metal, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing, blanking plates etc. as required. (But without MCB/RCCB/Isolator).(Make : L&T ; Model : 8537; 6 way (8 + 18) TPN DB Metal Door or Equivalent). | 3.00 | Each |  | 4900.00 | 14700.00 | 4800.00 | 14400.00 | 4600.00 | 13800.00 | 13800.00 | A K TECHNOCRATS
12.00 | Supplying and fixing of 8 way (8 +24), double door , metal, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing, blanking plates etc. as required. (But without MCB/RCCB/Isolator).(Make : L&T ; Model : 8537; 8 way (8 + 24) TPN DB Metal Door or Equivalent). | 3.00 | Each |  | 5400.00 | 16200.00 | 7350.00 | 22050.00 | 5400.00 | 16200.00 | 16200.00 | A K TECHNOCRATS, RAJSON ELECTRONS
13.01 | Providing and fixing following rating and breaking capacity and pole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. 125 A,36KA,FPMCCB | 2.00 | Each |  | 15000.00 | 30000.00 | 12000.00 | 24000.00 | 15000.00 | 30000.00 | 24000.00 | Awasthi Electric Works
14.01 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 6.00 | Each |  | 3100.00 | 18600.00 | 3000.00 | 18000.00 | 3020.00 | 18120.00 | 18000.00 | Awasthi Electric Works
15.01 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 6.00 | Each |  | 3400.00 | 20400.00 | 3300.00 | 19800.00 | 3300.00 | 19800.00 | 19800.00 | A K TECHNOCRATS, Awasthi Electric Works
16.00 | Supplying and fixing 63A rating, 415 V, 10 kA, Four Pole MCB suitable for inductive load in the existing TPN MCB DB complete with connections, testing and commissioning etc. as required. | 6.00 | Each |  | 1800.00 | 10800.00 | 1900.00 | 11400.00 | 1800.00 | 10800.00 | 10800.00 | A K TECHNOCRATS, RAJSON ELECTRONS
17.00 | Supplying and fixing 63A rating, 240/415 V, 10 kA, "C" curve, DP miniature circuit breaker suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 6.00 | Each |  | 1000.00 | 6000.00 | 1050.00 | 6300.00 | 1000.00 | 6000.00 | 6000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
18.00 | Supplying and fixing of 32 Amp rating, Two pole, (one phase and neutral), 415/240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each |  | 3500.00 | 10500.00 | 4350.00 | 13050.00 | 3400.00 | 10200.00 | 10200.00 | A K TECHNOCRATS
19.00 | Supplying and fixing of 32 Amp rating, Two pole, (one phase and neutral), 415/240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each |  | 3300.00 | 9900.00 | 4500.00 | 13500.00 | 3330.00 | 9990.00 | 9900.00 | RAJSON ELECTRONS
20.00 | Supplying and fixing of 63 Amp rating, Four Pole, 415/240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each |  | 4700.00 | 14100.00 | 5350.00 | 16050.00 | 4700.00 | 14100.00 | 14100.00 | A K TECHNOCRATS, RAJSON ELECTRONS
21.00 | Supplying and fixing of 63 Amp rating, Four Pole, 415/240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each |  | 4500.00 | 13500.00 | 5600.00 | 16800.00 | 4400.00 | 13200.00 | 13200.00 | A K TECHNOCRATS
22.01 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required. 4 way (4 + 12), Double door | 1.00 | Each |  | 5000.00 | 5000.00 | 9250.00 | 9250.00 | 5000.00 | 5000.00 | 5000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
22.02 | 8 way (4 + 24), Double door | 1.00 | Each |  | 6000.00 | 6000.00 | 11500.00 | 11500.00 | 6000.00 | 6000.00 | 6000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
23.01 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 250.00 | Each |  | 300.00 | 75000.00 | 175.00 | 43750.00 | 250.00 | 62500.00 | 43750.00 | Awasthi Electric Works
23.02 | Double pole | 20.00 | Each |  | 800.00 | 16000.00 | 625.00 | 12500.00 | 775.00 | 15500.00 | 12500.00 | Awasthi Electric Works
23.03 | Triple pole | 10.00 | Each |  | 1200.00 | 12000.00 | 925.00 | 9250.00 | 1200.00 | 12000.00 | 9250.00 | Awasthi Electric Works
23.04 | Triple pole and Nutral | 20.00 | Each |  | 1500.00 | 30000.00 | 1275.00 | 25500.00 | 1500.00 | 30000.00 | 25500.00 | Awasthi Electric Works
24.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 50.00 | Each |  | 30.00 | 1500.00 | 35.00 | 1750.00 | 40.00 | 2000.00 | 1500.00 | RAJSON ELECTRONS
25.00 | Supply of recessed mounted LED downlighter 18W with pressure die-cast aluminium housing Lighting system comprising of LED of approved make ,having luminaire efficacy of not less than 100 lm/W. etc as per specifications and complete as required. | 80.00 | Each |  | 1500.00 | 120000.00 | 1100.00 | 88000.00 | 1000.00 | 80000.00 | 80000.00 | A K TECHNOCRATS
26.00 | Supply of LED 36W luminaire suitable for recess mounting in modular false ceiling system powder coated CRCA housing with acrilic diffuser size 2 ft x 2 ft ,comprising of LED’s of approved make with Constant current output driver, having luminaire efficacy of not less than 100 lm/W. etc as per specifications and complete as required. | 80.00 | Each |  | 2300.00 | 184000.00 | 1500.00 | 120000.00 | 1100.00 | 88000.00 | 88000.00 | A K TECHNOCRATS
27.00 | SITC of 3W LED Double sided Exit Signage (Green/Red) Light with inbuilt 2 hours battery back up etc as per specifications and complete as required . | 10.00 | Each |  | 1500.00 | 15000.00 | 7500.00 | 75000.00 | 1400.00 | 14000.00 | 14000.00 | A K TECHNOCRATS
28.00 | Supply of flexible LED light strip 10W per running meter strip in transparent unit with approx. 120Nos of LEDs per meter (IP:65) complete with driver complete as required. | 80.00 | RM |  | 550.00 | 44000.00 | 800.00 | 64000.00 | 540.00 | 43200.00 | 43200.00 | A K TECHNOCRATS
29.00 | Installation, testing and commissioning of pre-wired, LED fitting with driver/ fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall/ surface, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 160.00 | Each |  | 140.00 | 22400.00 | 175.00 | 28000.00 | 140.00 | 22400.00 | 22400.00 | A K TECHNOCRATS, RAJSON ELECTRONS
30.01 | Supply of following sizes of Power Cables , multi stranded copper conductor, XLPE Insulated, cores laid up, PVC tape / Extruded Inner sheathed , Armoured, FRLS at outer sheathed,1100V grade as per IS 7098(Part 1) 1988 4CORE 10 sq.mm. CU Ar. XLPE cable | 150.00 | RM |  | 700.00 | 105000.00 | 490.00 | 73500.00 | 700.00 | 105000.00 | 73500.00 | Awasthi Electric Works
30.02 | 4CORE 16 sq.mm. CU Ar. XLPE cable | 350.00 | RM |  | 900.00 | 315000.00 | 725.00 | 253750.00 | 900.00 | 315000.00 | 253750.00 | Awasthi Electric Works
30.03 | 4CORE 25 sq.mm. CU Ar. XLPE cable | 200.00 | RM |  | 1500.00 | 300000.00 | 1050.00 | 210000.00 | 1300.00 | 260000.00 | 210000.00 | Awasthi Electric Works
31.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size onsurface / cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 700.00 | Meter |  | 55.00 | 38500.00 | 65.00 | 45500.00 | 60.00 | 42000.00 | 38500.00 | RAJSON ELECTRONS
32.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 500.00 | Meter |  | 250.00 | 125000.00 | 30.00 | 15000.00 | 240.00 | 120000.00 | 15000.00 | Awasthi Electric Works
33.01 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. 4C X 10 sq. mm | 10.00 | Each |  | 450.00 | 4500.00 | 300.00 | 3000.00 | 470.00 | 4700.00 | 3000.00 | Awasthi Electric Works
33.02 | 4C X 16 sq. mm | 20.00 | Each |  | 550.00 | 11000.00 | 400.00 | 8000.00 | 500.00 | 10000.00 | 8000.00 | Awasthi Electric Works
33.03 | 4C X 25 sq. mm | 20.00 | Each |  | 600.00 | 12000.00 | 500.00 | 10000.00 | 550.00 | 11000.00 | 10000.00 | Awasthi Electric Works
34.00 | Supply of 3.5CX 150 sq.mm size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. (Make: As per AAI list of preffered makes) | 300.00 | Meter |  | 1200.00 | 360000.00 | 675.00 | 202500.00 | 970.00 | 291000.00 | 202500.00 | Awasthi Electric Works
35.01 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 90 mm dia (OD-90 mm & ID-76 mm nominal) | 300.00 | Meter |  | 500.00 | 150000.00 | 200.00 | 60000.00 | 455.00 | 136500.00 | 60000.00 | Awasthi Electric Works
36.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required Above 95 sq. mm and upto 185 sq. mm | 300.00 | Meter |  | 200.00 | 60000.00 | 50.00 | 15000.00 | 150.00 | 45000.00 | 15000.00 | Awasthi Electric Works
37.01 | Supplying and making end termination with brass compression gland and aluminium/copper lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 150 sq. mm (50mm) | 2.00 | Each |  | 1400.00 | 2800.00 | 450.00 | 900.00 | 1300.00 | 2600.00 | 900.00 | Awasthi Electric Works
38.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 7500.00 | 30000.00 | 10000.00 | 40000.00 | 7500.00 | 30000.00 | 30000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
39.01 | Supply & Fixing of factory fabricated pre-galvanized G.I. sheet steel raceway in 1.6mm thickness for bottom & sides and 2mm thick top Cover including juction boxes with 2mm cover plate and as called for including necessary civil work such as chase cutting in screed, fixing/ jamming the raceway, aligning & levelling and finishing with sand cement plaster & chicken wire mesh. 150mm x 38mm (2mm top Cover) | 550.00 | Meter |  | 775.00 | 426250.00 | 1050.00 | 577500.00 | 610.00 | 335500.00 | 335500.00 | A K TECHNOCRATS
40.00 | Design, Supply, Installation, Testing & Commissioning of Outdoor Type, Floor Mounted compartmentalized cubical type Feeder Pillar of 415 Volt (Nominal), fabricated out of 2 mm thick CRCA Sheet, free standing and totally enclosed, IP65, Double Door Feeder pillar to cover incomers and outgoings confirming to IS: 61439, Weather proof / dust proof / vermin proof with bottom cable entries and cable alleys. The feeder pillar shall be suitable for operation on 3 Phase, 4 wire, 50 Hz AC supply and with suitable size busbar, earth bar and following switchgear instrumentation and protection devices etc. complete with connections, interconnection, earthing, painting and marking as per site conditions etc complete as required as per the specifications. Suuplier must take Feeder Pillar Design Approval from EIC before the supply. I: - Incomer : a) 160 A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 Nos. b) Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD/LED Display of size 96 x 96 mm. - 01 Nos. c) Indication Lamp R, Y & B (LED Type) -01 set II - Outgoing : a) 100 A, MCCB, 4P, 30 KA (Icu= 100% Ics) with extended rotary handle - 02 Nos. b) 64A, MCCB, 4P, 30 KA (Icu= 100% Ics) with extended rotary handle - 04 Nos. c) Indication Lamp R & G (LED type) - 06 Set Other : a) 300A Copper busbar, 3 Phase and Neutral c) Necessary CT & Control wiring arrangement | 1.00 | Each |  | 250000.00 | 250000.00 | 590000.00 | 590000.00 | 16000.00 | 16000.00 | 16000.00 | A K TECHNOCRATS
41.00 | Supply of Wall mounted SS Steel Hnad Drier with Air Purifier having suitable voltage ramge of 220-240 v , 50 Hz , Touch free infrared sensor activation , Brushless motor having 18000 RPM ,Noise level shoud not be more than 72 db (Make : Dolphy ; Model : DAHD0063 or Eqquivalent) | 6.00 | Each |  | 35000.00 | 210000.00 | 27500.00 | 165000.00 | 15000.00 | 90000.00 | 90000.00 | A K TECHNOCRATS
42.00 | Dismantling of existing conduit piping ,wiring , light fixture , switch borad , MCBDB etc as per the site requirement. | 1.00 | Job |  | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 5000.00 | 5000.00 | 5000.00 | A K TECHNOCRATS
43.00 | Supply of portable Airport mobile charging station compatible of 240 V, 50 Hz, having capacity of 7 Mobile chargers and 5 USB ports. (Design approval should be taken form EIC before the supply) | 6.00 | Each |  | 66500.00 | 399000.00 | 22000.00 | 132000.00 | 5000.00 | 30000.00 | 30000.00 | A K TECHNOCRATS
44.00 | Supply installation, testing and commissioning of recessed bi level drinking water fountain with double chrome plated brass bubblers & one recess type sport bottle filling station with sensor and mechanical operation. Drinking water fountain having min. 8 GPH cooling capacity, stainless steel body , SS finish frame , suitable for operation min. range 50 to 90 PSI, chilling unit suitable for R134a refrigerant with suitable to operate on 220V +/- 5% Volt , 50 Hz. AC Single phase supply complete , adjustable thermo state,with all accessories etc as required . The system shall comply with ANSI 117.1 and ADA,UL listed , ANSI/NSF 61 complied . The recess type seperate mechanical activation botter filler shall have silver ion antimicrobial protection with SS finish frame exerior . The unit shall be installed at standard height to meet the standard requirement as per direction and satisfaction of Engineer‐Incharge.(Model- M8CRSBF Make:Oasis/Model:H1011.8 with 1900 Make:Haws/ equivalent approved make & model ) NOTE: 1) Item to be executed by a specialized agency approved by Engineer‐In‐Charge. 2) Item to be executed as per shop drawing to be submitted by agency duly approved by Engineer‐In‐Charge. | 5.00 | Each |  | 95000.00 | 475000.00 | 125000.00 | 625000.00 | 10000.00 | 50000.00 | 50000.00 | A K TECHNOCRATS
45.00 | Supply, Installation, Testing & Commissioning of Reverse Osmosis System (RO) having min. capacity 50 LPH RO system along with five stage filteration along with media and carbon filter , RO membrane , UV filteration & TDS meter and pressure gauge with 60 ltrs. HTP pressure tank to generate the adequate pressure for meeeting the operation for above "SOQ Item No. 16 drinking fountain" . All the system will be enclosed in the powder coated M.S body with suitable mounting/fixing arrangment as per site requirement complete etc as required upto the satisfaction of Engg. In Charge. (Make:Danfrost Model RO 50L /Make: Oasis/equivalent approved make). NOTE:1) Item to be executed by a specialized agency approved by Engineer‐In‐Charge. 2) Item to be executed as per shop drawing submitted by agency duly approved by Engineer‐In‐Charge. | 5.00 | Each |  | 120000.00 | 600000.00 | 115000.00 | 575000.00 | 10000.00 | 50000.00 | 50000.00 | A K TECHNOCRATS
46.01 | Design, supply, installation, testing & commissioning of wall/ celing mounted internally illuminated pictographs. The signage board shall be fabricated board by making "C" shaped 3 mm thick Aluminum profile sign board with inbuilt light proof ventilating system. The signage panel shall be fabricated from 2 mm aluminum sheet of approved make and shade having laser cut logo/ lettering in Marathi, Hindi & English. 3 mm poly carbonate sheet shall fixed at inner side of the panel sheet board so as the lettering will glow white as per the design approved by the Engineer-In-Charge. Boards shall be designed, fabricated and installed as per the detailed specification. The signage shall have system for easygraphic changes and easy access for maintenance. The illumination source shall be of LED's (2400 lumens/ SQMT) as light source with individual current regulator for every signage complete with all internal wiring , connectors etc. (Make of LED Modules and power supply driver module of make requivalent of OSRAM/ PHILIPS/ NICHIA) of minimum 5 years guarantee. The signboard can be either suspended fromceiling/ wall mounted with necessary Aluminum powdercoated pipe of 38 x 2 mm pipe on the top or side for fixing the same on the desired location as per conditions including wiring up to 5 meters in casing, capping, as required. The entire signage shall be powder coated in required shade as per direction of EIC. Single Side - 1700mm x 400mm X 75mm deep | 13.00 | No. |  | 20000.00 | 260000.00 | 42500.00 | 552500.00 | 2000.00 | 26000.00 | 26000.00 | A K TECHNOCRATS
46.02 | Double Side - 1700mm x 400mm X 75mm deep | 2.00 | No. |  | 5000.00 | 10000.00 | 55000.00 | 110000.00 | 5000.00 | 10000.00 | 10000.00 | A K TECHNOCRATS, RAJSON ELECTRONS
46.03 | Single Side - 400mm x 400mm X 75mm deep | 15.00 | No. |  | 6500.00 | 97500.00 | 17500.00 | 262500.00 | 5000.00 | 75000.00 | 75000.00 | A K TECHNOCRATS
47.00 | Dismantling and re-installation of existing signages board as per site condition including accessories like supporting piping etc as required. | 1.00 | Job |  | 5000.00 | 5000.00 | 15000.00 | 15000.00 | 1000.00 | 1000.00 | 1000.00 | A K TECHNOCRATS
48.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) Intelligent addressable smoke detector with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications ,complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors). | 50.00 | Each |  | 5000.00 | 250000.00 | 2500.00 | 125000.00 | 3600.00 | 180000.00 | 125000.00 | Awasthi Electric Works
49.00 | Supplying, Installation, testing & commissioning of UL / EN listed (latest version) intelligent addressable manual call station (Resetable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test reset lock, electronic or ratary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire control panel. Cover shall be made out of LEXAN (or poly carbonate equivalent) with clear operating instruction and the word fire appearing on the front complete with connections etc. as required and as per enclosed specifications. | 10.00 | Each |  | 4500.00 | 45000.00 | 3000.00 | 30000.00 | 4500.00 | 45000.00 | 30000.00 | Awasthi Electric Works
50.00 | Supply, installation, testing and commissioning of UL / EN listed (latest version) loop powered addressable Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 10.00 | Each |  | 5000.00 | 50000.00 | 6250.00 | 62500.00 | 4501.00 | 45010.00 | 45010.00 | A K TECHNOCRATS
51.00 | Supply and laying of 2 core , 1.5 sq. mm . Fire Survival cable, armoured copper conductor of 600/1000 V grade, insulated with specially formulated PVC , coated with special fire resistance materials and overall sheathed with special PVC, with special properties as Zero Halogen Low Smoke insulation Basic construction as per BS 7846 -2009 & cuircuit integrity as per BS 6387 C.W.Z/BS EN 50200. | 400.00 | Meter |  | 300.00 | 120000.00 | 160.00 | 64000.00 | 240.00 | 96000.00 | 64000.00 | Awasthi Electric Works
52.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Modular Microprocessor based expandable expandable intellegent Addressable type Fire Alarm Control panel of 05 (Five) loops, with minimum 320 character graphics/ LCD display with tuch screen or other keypad and minimum 4000 events history long in the non volatile memory (EPROM), The panel should be equiped with loop capacity to take minimum 240 intellegent addressable detectors/ devices (In any combination with minimum 120 detector per loop) in one loop. Four access levels, capable of taking Protocol Devices, Graphical Display, sufficient numbers of programmable relay controls for controlling ventilation fan, fire pump room, monitoring of fire sprinkler and fire hydrant pump, 230 volts, 50 Hz AC power supply, inbuilt automatic battery charger, 24 volts sealed maintenance free lead acid batteries sufficient for 2 hourse normal working and then be capable of operating the system for 30 minutes during and emergency/ fault conditions along with battery stand as required. The panel shall have facility for seamless integration with PA system in case of fire) The panel shall be compatible for Building Management System with open protocol BACNET/MODBUS etc. as per specifiction, complete as required. The panel should be compatible with the existing fire alarm system inclung re-addressing, re-programming, re-commissioning of existing fire devices in fire alarm control panel etc. as required. ( smoke detectors, multi criteria detectors , MCPs). EST3 fire panel shall be suitable for existing fire system. a) 5 Loop. Note: 1). Prior site inspection by OEM of the fire panel is mandatory before the delivery of panel. 2). All the re programmig of installed fire devices a | 1.00 | Job |  | 150000.00 | 150000.00 | 175000.00 | 175000.00 | 20000.00 | 20000.00 | 20000.00 | A K TECHNOCRATS
53.01 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. 80 mm dia | 2.00 | Each |  | 5000.00 | 10000.00 | 4250.00 | 8500.00 | 4500.00 | 9000.00 | 8500.00 | Awasthi Electric Works
53.02 | 100 mm dia | 4.00 | Each |  | 6500.00 | 26000.00 | 5750.00 | 23000.00 | 5500.00 | 22000.00 | 22000.00 | A K TECHNOCRATS
53.03 | 150 mm dia | 4.00 | Each |  | 9000.00 | 36000.00 | 8500.00 | 34000.00 | 8500.00 | 34000.00 | 34000.00 | A K TECHNOCRATS, Awasthi Electric Works
54.01 | Providing, laying /erection, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling or with proper hanging arrangements (in case of sprinkler line with proper welding) with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. 25 mm dia | 150.00 | Meter |  | 500.00 | 75000.00 | 350.00 | 52500.00 | 450.00 | 67500.00 | 52500.00 | Awasthi Electric Works
54.02 | 32 mm dia | 80.00 | Meter |  | 600.00 | 48000.00 | 400.00 | 32000.00 | 550.00 | 44000.00 | 32000.00 | Awasthi Electric Works
54.03 | 65 mm dia | 50.00 | Meter |  | 900.00 | 45000.00 | 750.00 | 37500.00 | 850.00 | 42500.00 | 37500.00 | Awasthi Electric Works
54.04 | 80 mm dia | 80.00 | Meter |  | 1100.00 | 88000.00 | 1000.00 | 80000.00 | 975.00 | 78000.00 | 78000.00 | A K TECHNOCRATS
54.05 | 100 mm dia | 100.00 | Meter |  | 1400.00 | 140000.00 | 1200.00 | 120000.00 | 1250.00 | 125000.00 | 120000.00 | Awasthi Electric Works
55.00 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes i/c quartzoid bulb complete as required after removing existing MS sprinkler drop (if it is required) or making arrangements for fixing of sprinkler flexible pipe in case of new sprinkler line. a) 1500 mm | 25.00 | Each |  | 2500.00 | 62500.00 | 1500.00 | 37500.00 | 2000.00 | 50000.00 | 37500.00 | Awasthi Electric Works
56.00 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 10.00 | Nos. |  | 3000.00 | 30000.00 | 4000.00 | 40000.00 | 2500.00 | 25000.00 | 25000.00 | A K TECHNOCRATS
57.00 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) female coupling suitable for connection with existing fire hydrant to the 63 mm dia hose pipe conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 20.00 | Nos. |  | 9000.00 | 180000.00 | 9500.00 | 190000.00 | 5500.00 | 110000.00 | 110000.00 | A K TECHNOCRATS
58.00 | Supplying and Fixing of M.S. Hose cabinet Wall mounted type fabricated out of S.S. sheet with glass fronted door and size of the cabinet shall be 600mm x 750 mm x 250 mm cabinet. | 3.00 | Nos. |  | 7000.00 | 21000.00 | 5500.00 | 16500.00 | 8000.00 | 24000.00 | 16500.00 | Awasthi Electric Works
59.00 | Supplying and Fixing of First Aid Hose Reel, wall mounting swinging type complete with drum & bracket of MS construction, spray painted in Post office Red, confirming to IS 884/1995 with upto date amendments, complete with the following as required. 30 Meter long 20 mm dia water hose Thermoplastic (Textile reinforced) Type - 2 as per IS : 12585 25 mm dia ball valve & nozzle.Drum and rackets for fixing the equipments on wall.Connection from riser with stop valve (gun metal) & M.S. Pipe | 3.00 | Nos. |  | 9000.00 | 27000.00 | 10000.00 | 30000.00 | 7500.00 | 22500.00 | 22500.00 | A K TECHNOCRATS
60.00 | Providing and fixing pre fabricated 4 mm thick glass door (with SS frame) of size 2.1 m x 0.9 m with centre opening for fire hose cabinet suitably marked on the outside with letters “Fire Hose’’ including locking arrangement suitable to accommodate 1 no Hydrant landing valves, 1 no fire hose reel, 2 nos. 15m long 63 mm dia hose pipe , 1 no branch pipe, 1 no fire man’s axe and 2 nos fire extinguishers. All SS work to be in Red P.O Colour over appropriate primer. | 3.00 | Nos. |  | 9000.00 | 27000.00 | 35000.00 | 105000.00 | 6500.00 | 19500.00 | 19500.00 | A K TECHNOCRATS
61.00 | Dismantling and re-installation of existing fire fighting drop pipe as per site condition including accessories like socket, rozzar plate and cap etc as required. | 10.00 | Each |  | 25000.00 | 250000.00 | 3000.00 | 30000.00 | 245.00 | 2450.00 | 2450.00 | A K TECHNOCRATS
| Total in Figures |  |  |  |  | 11187600.00 |  | 10991260.00 |  | 7444445.00
Lowest Amount Quoted BY: A K TECHNOCRATS(7444445.00)

## BOQ Summary
BOQ Summary Details Tender Title: Reconfiguration of Existing Terminal building at Aurangabad Airport. SH Internal Electrical work, fire work, building signages work and Fountain type water cooler. Tender ID: 2023_AAI_175870_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | A K TECHNOCRATS | 7444445.00 | L1
| 2 | Awasthi Electric Works | 10991260.00 | L2
| 3 | RAJSON ELECTRONS | 11187600.00 | L3