## BoQ1
Government eProcurement System Created By: Ravindra singh Mehrok Created Date/Time: 10-Jan-2024 06:05 PM Tender Title: Provision of Lighting on walking track of park, replacement of LT Panel of old colony and other miscellaneous works at Vadodara Airport. Tender ID: 2023_AAI_175937_1
Tender Inviting Authority: Asst.Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work :- Provision of Lighting on walking track of park, replacement of LT Panel of old colony and other miscellaneous works at Vadodara Airport.
Contract No: AAI/BO/E-E/NIT- 4/ Lighting_Panel_Misc.work / 2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Instapower Ltd(GSTN-05AAACI9712L1ZG) |  | Messers Rajesh Gawde(GSTN-23AFHPG7133A1Z4) |  | Ascent Electrification Engineers(GSTN-24AAOFA2574R1ZU) |  | Variant Infratech Private Limited(GSTN-NA) |  | MITESH R HAPANI(GSTN-NA) |  | GAYATRI ELECTRICAL(GSTN-NA) |  | girnar electricals(GSTN-NA) |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd(GSTN-NA) |  | Edge Telecom Pvt Ltd(GSTN-NA) |  | Patel Electricals(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of LED Highbay light with housing material - Al. die cast, fixture should have minimum net efficacy at System level (Not Chip Level) >= 150 lumens/watt, minimum luminous flux of 12000 lumen, Life of fixture 50000 hrs (minimum), CCT up to 6500K, CRI >70, PF >0.94, IP 65, IK06 and suitable for 150V- 270V AC, 50Hz. supply, Internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79 report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum). (Make- Bajaj, Model- BGHBM PRO B 120L WH NB SD or or Equivalent as per AAI preferred make list) | 202.00 | Each |  | 4100.00 | 828200.00 | 3000.00 | 606000.00 | 3996.00 | 807192.00 | 4464.00 | 901728.00 | 3175.00 | 641350.00 | 3950.00 | 797900.00 | 4000.00 | 808000.00 | 4680.00 | 945360.00 | 3000.00 | 606000.00 | 5000.00 | 1010000.00 | 4500.00 | 909000.00 | 606000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Instapower Ltd
2.00 | Supply of 2'x2' recessed type LED panel light with housing material - CRAC steel sheet, fixture should have minimum net efficacy at System level (Not Chip Level) >= 120 lumens/watt, luminous flux of 4200 lumen, Life of fixture 50000 hrs (minimum), CCT up to 6500K, CRI >80, PF >0.89, IP 20 and suitable for 180v- 270V AC, 50Hz. supply, Internal Surge Protection >= 3 KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79 report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- 113522 BZRSQL 43L XE WH OD SD or Equivalent as per AAI preferred make list ) | 55.00 | Each |  | 1800.00 | 99000.00 | 2100.00 | 115500.00 | 1936.95 | 106532.25 | 1887.00 | 103785.00 | 1671.00 | 91905.00 | 2200.00 | 121000.00 | 2050.00 | 112750.00 | 2080.00 | 114400.00 | 1500.00 | 82500.00 | 2000.00 | 110000.00 | 2000.00 | 110000.00 | 82500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
3.00 | Supply of 1'x4' recessed type LED panel light with housing material - steel, fixture should have minimum net efficacy at System level (Not Chip Level) >= 100 lumens/watt, luminous flux of 3600 lumen, Life of fixture 50000 hrs (minimum), CCT up to 4000K, CRI >70, PF >0.94, IP 20 and suitable for 180V-270V AC, 50Hz. supply, Internal Surge Protection >= 3KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79 report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- BZRSLL 36L LED GX WH SD or Equivalent as per AAI preferred make list ) | 45.00 | Each |  | 1875.00 | 84375.00 | 2625.00 | 118125.00 | 2097.90 | 94405.50 | 1887.00 | 84915.00 | 1760.00 | 79200.00 | 2200.00 | 99000.00 | 2050.00 | 92250.00 | 2184.00 | 98280.00 | 2000.00 | 90000.00 | 2000.00 | 90000.00 | 2100.00 | 94500.00 | 79200.00 | Variant Infratech Private Limited
4.00 | Supply of wide beam (minimum 60 degree) LED Flood Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 36000 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-08, and suitable for 150V-275V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- PRAZE F 360L WH NB-A5 TG SD or Equivalent as per AAI preferred make list) | 20.00 | Each |  | 11500.00 | 230000.00 | 12600.00 | 252000.00 | 13153.50 | 263070.00 | 10057.00 | 201140.00 | 9296.00 | 185920.00 | 11000.00 | 220000.00 | 11400.00 | 228000.00 | 13312.00 | 266240.00 | 8500.00 | 170000.00 | 12000.00 | 240000.00 | 13000.00 | 260000.00 | 170000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
5.00 | Supply of narrow beam (maximum 30 degree) LED Flood Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 42000 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-08, and suitable for 150V-275V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- PRAZE F 420L WH NB-A3 TG SD or Equivalent as per AAI preferred make list ) | 6.00 | Each |  | 13350.00 | 80100.00 | 14700.00 | 88200.00 | 14652.00 | 87912.00 | 13956.00 | 83736.00 | 9840.00 | 59040.00 | 13500.00 | 81000.00 | 13200.00 | 79200.00 | 15496.00 | 92976.00 | 9200.00 | 55200.00 | 12000.00 | 72000.00 | 15000.00 | 90000.00 | 55200.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.00 | Supply of wide beam (minimum 60 degree) LED Flood Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 9600 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-07, and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- PRAZE F 96L WH NB A5 TG SD or Equivalent as per AAI preferred make list ) | 22.00 | Each |  | 2900.00 | 63800.00 | 2940.00 | 64680.00 | 3507.60 | 77167.20 | 3831.00 | 84282.00 | 2855.00 | 62810.00 | 3200.00 | 70400.00 | 4080.00 | 89760.00 | 3432.00 | 75504.00 | 2700.00 | 59400.00 | 3600.00 | 79200.00 | 3300.00 | 72600.00 | 59400.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
7.00 | Supply of wide beam (minimum 60 degree) LED Flood Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=110lumens/watt & minimum luminous flux of 5500 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-07, and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- GLEAM 55L WH SY PC SD V2 or Equivalent as per AAI preferred make list ) | 10.00 | Each |  | 1800.00 | 18000.00 | 2100.00 | 21000.00 | 1720.50 | 17205.00 | 2271.00 | 22710.00 | 1785.00 | 17850.00 | 2300.00 | 23000.00 | 2520.00 | 25200.00 | 2132.00 | 21320.00 | 1700.00 | 17000.00 | 1760.00 | 17600.00 | 2100.00 | 21000.00 | 17000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.00 | Supply of wide beam (minimum 60 degree) LED Flood Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=110lumens/watt & minimum luminous flux of 3300 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-07, and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- GLEAM 33L WH SY PC SD V2 V2 or Equivalent as per AAI preferred make list ) | 10.00 | Each |  | 1300.00 | 13000.00 | 1260.00 | 12600.00 | 1243.20 | 12432.00 | 1243.00 | 12430.00 | 2566.00 | 25660.00 | 1500.00 | 15000.00 | 1450.00 | 14500.00 | 1560.00 | 15600.00 | 1150.00 | 11500.00 | 1760.00 | 17600.00 | 1600.00 | 16000.00 | 11500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
9.00 | Supply of LED street Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 10500 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-08, and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- ZELA P 108L WH PO TG SD or Equivalentas per AAI preferred make list ) | 10.00 | Each |  | 3156.00 | 31560.00 | 3780.00 | 37800.00 | 3174.60 | 31746.00 | 3164.00 | 31640.00 | 2433.00 | 24330.00 | 3100.00 | 31000.00 | 2850.00 | 28500.00 | 3640.00 | 36400.00 | 2800.00 | 28000.00 | 3600.00 | 36000.00 | 3600.00 | 36000.00 | 24330.00 | Variant Infratech Private Limited
10.00 | Supply of LED street Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 5400 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-08, and suitable for 150V-275V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- ENXT P 54 L WH PO PC SD MT or Equivalent as per AAI preferred make list ) | 20.00 | Each |  | 1765.00 | 35300.00 | 1890.00 | 37800.00 | 1709.40 | 34188.00 | 1752.00 | 35040.00 | 1607.00 | 32140.00 | 2200.00 | 44000.00 | 1980.00 | 39600.00 | 2080.00 | 41600.00 | 1290.00 | 25800.00 | 1760.00 | 35200.00 | 2000.00 | 40000.00 | 25800.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
11.00 | Supply of LED street Light fixture with housing material - Aluminum Alloy,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=120lumens/watt & minimum luminous flux of 8400 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 5700K, CRI >70, PF >=0.95, IP-66, IK-08, and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- ENXT P 84 L WH PO PC SD MT or Equivalent as per AAI preferred make list ) | 36.00 | Each |  | 2621.00 | 94356.00 | 2625.00 | 94500.00 | 2708.40 | 97502.40 | 2260.00 | 81360.00 | 2140.00 | 77040.00 | 2800.00 | 100800.00 | 2900.00 | 104400.00 | 3068.00 | 110448.00 | 2350.00 | 84600.00 | 2560.00 | 92160.00 | 3000.00 | 108000.00 | 77040.00 | Variant Infratech Private Limited
12.00 | Supply of 4 ft LED batten Tube Light fixture with housing material - Extruded aluminium housing,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=100 lumens/watt & minimum luminous flux of 2000 lumen, Life of fixture 25000hrs @ L70 Lumen maintenance, CCT upto 6500K, CRI >80, PF >=0.95, IP-22 and suitable for 150V-270V AC, 50Hz. supply minimum internal Surge Protection >= 3KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) | 260.00 | Each |  | 350.00 | 91000.00 | 294.00 | 76440.00 | 532.80 | 138528.00 | 237.00 | 61620.00 | 294.00 | 76440.00 | 600.00 | 156000.00 | 210.00 | 54600.00 | 328.00 | 85280.00 | 240.00 | 62400.00 | 360.00 | 93600.00 | 330.00 | 85800.00 | 54600.00 | GAYATRI ELECTRICAL
13.00 | Supply of round type LED Post top Light fixture with housing material - Extruded aluminium housing,Optic material - Polycarbonate with integrated electronic power supply unit, fixture should have minimum net efficacy at System level (Not Chip Level) >=85lumens/watt & minimum luminous flux of 3800 lumen, Life of fixture 50000hrs @ L70 Lumen maintenance, CCT upto 6500K IP-66, IK-08, and suitable for 150V-275V AC, 50Hz. supply minimum internal Surge Protection >= 4KV. The fixture should comply with the parameters as per IS10322 and IEC60598, EMC / EMI compliance, and LED driver shall be BIS registered & luminair manufacture shall provide LM79report from NABL accredited lab & LM80 report issued by LED manufacturer and warranty for 05 years (minimum) (Make- Bajaj, Model- Archner: Make-Philips, Model-BGP300 LED40 757 PSU PC IN S1, or sample from preferred make list approved by EIC) | 29.00 | Each |  | 7380.00 | 214020.00 | 4200.00 | 121800.00 | 4162.50 | 120712.50 | 4690.00 | 136010.00 | 2398.00 | 69542.00 | 7500.00 | 217500.00 | 4800.00 | 139200.00 | 8424.00 | 244296.00 | 4000.00 | 116000.00 | 6240.00 | 180960.00 | 650.00 | 18850.00 | 18850.00 | Patel Electricals
14.10 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured cable of 1.1 KV grade conforming to IS : 7098 (Part:-I) /1988 with upto date amendments etc.,as required.of following sizes : a) 4 X 16 Sq.mm | 500.00 | Meter |  | 126.00 | 63000.00 | 155.25 | 77625.00 | 144.30 | 72150.00 | 120.00 | 60000.00 | 120.00 | 60000.00 | 130.00 | 65000.00 | 160.00 | 80000.00 | 146.00 | 73000.00 | 153.00 | 76500.00 | 200.00 | 100000.00 | 180.00 | 90000.00 | 60000.00 | Variant Infratech Private Limited, Ascent Electrification Engineers
14.20 | b) 4 X 25 Sq.mm | 1500.00 | Meter |  | 160.00 | 240000.00 | 178.20 | 267300.00 | 166.50 | 249750.00 | 147.00 | 220500.00 | 135.00 | 202500.00 | 165.00 | 247500.00 | 195.00 | 292500.00 | 177.00 | 265500.00 | 168.00 | 252000.00 | 220.00 | 330000.00 | 210.00 | 315000.00 | 202500.00 | Variant Infratech Private Limited
15.10 | Supply of following sizes HDPE (High Density Polyethylene) duct of grade PE80, PN6 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:1995 with latest ammendments complete as required. 50mm dia.(O.D.) | 1400.00 | Meter |  | 79.00 | 110600.00 | 108.00 | 151200.00 | 49.95 | 69930.00 | 65.00 | 91000.00 | 35.00 | 49000.00 | 80.00 | 112000.00 | 105.00 | 147000.00 | 99.00 | 138600.00 | 90.00 | 126000.00 | 80.00 | 112000.00 | 100.00 | 140000.00 | 49000.00 | Variant Infratech Private Limited
15.20 | 90mm dia.(O.D.) | 300.00 | Meter |  | 207.00 | 62100.00 | 459.00 | 137700.00 | 133.20 | 39960.00 | 204.00 | 61200.00 | 65.00 | 19500.00 | 150.00 | 45000.00 | 245.00 | 73500.00 | 297.00 | 89100.00 | 280.00 | 84000.00 | 224.00 | 67200.00 | 120.00 | 36000.00 | 19500.00 | Variant Infratech Private Limited
16.10 | laying of following size HDPE pipe along with all accessories like socket, bend, couplers etc. with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 50mm dia.(O.D.) | 950.00 | Meter |  | 100.00 | 95000.00 | 65.00 | 61750.00 | 66.00 | 62700.00 | 69.00 | 65550.00 | 500.00 | 475000.00 | 150.00 | 142500.00 | 60.00 | 57000.00 | 136.00 | 129200.00 | 50.00 | 47500.00 | 56.00 | 53200.00 | 130.00 | 123500.00 | 47500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
16.20 | 90mm dia.(O.D.) | 215.00 | Meter |  | 110.00 | 23650.00 | 104.00 | 22360.00 | 111.00 | 23865.00 | 92.00 | 19780.00 | 500.00 | 107500.00 | 250.00 | 53750.00 | 60.00 | 12900.00 | 156.00 | 33540.00 | 55.00 | 11825.00 | 68.00 | 14620.00 | 150.00 | 32250.00 | 11825.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
17.00 | laying of 50 mm dia size HDPE pipe along with all accessories like socket, bend, couplers etc. with fitting and cutting, jointing etc. on wall with 25 x 3 mm GI flat clamp on 1.2 meter (max) interval etc., complete as per site requirement. | 120.00 | Meter |  | 50.00 | 6000.00 | 130.00 | 15600.00 | 77.70 | 9324.00 | 69.00 | 8280.00 | 450.00 | 54000.00 | 350.00 | 42000.00 | 100.00 | 12000.00 | 84.00 | 10080.00 | 70.00 | 8400.00 | 120.00 | 14400.00 | 70.00 | 8400.00 | 6000.00 | Techno Electricals
18.10 | laying of following size size HDPE pipe along with all accessories like socket, bend, couplers etc. with fitting and cutting, jointing etc. in ground (50 cm below ground level) under paver block/ hard rock including removal of paver block, breaking of hard rock, excavation, refilling the trench and fixing paver block (broken paver block shall be fixed with new one) or fixing as per previous site condition but excluding sand cushioning and protective covering etc.in complete as per site requirement. 50mm dia.(O.D.) | 330.00 | Meter |  | 250.00 | 82500.00 | 130.00 | 42900.00 | 99.90 | 32967.00 | 201.00 | 66330.00 | 450.00 | 148500.00 | 300.00 | 99000.00 | 180.00 | 59400.00 | 177.00 | 58410.00 | 80.00 | 26400.00 | 56.00 | 18480.00 | 70.00 | 23100.00 | 18480.00 | Edge Telecom Pvt Ltd
18.20 | 90mm dia.(O.D.) | 70.00 | Meter |  | 275.00 | 19250.00 | 195.00 | 13650.00 | 1254.30 | 87801.00 | 201.00 | 14070.00 | 450.00 | 31500.00 | 500.00 | 35000.00 | 180.00 | 12600.00 | 208.00 | 14560.00 | 90.00 | 6300.00 | 68.00 | 4760.00 | 80.00 | 5600.00 | 4760.00 | Edge Telecom Pvt Ltd
19.00 | Providing, laying and fixing 100 mm dia G.I. pipe (medium class) in concrete / bituminous road / paver block complete with G.I. fittings including trenching (50 cm deep) and re-filling and making the same as it is by providing concrete/ paver block etc complete as required | 80.00 | Meter |  | 1300.00 | 104000.00 | 1770.00 | 141600.00 | 44.40 | 3552.00 | 1150.00 | 92000.00 | 550.00 | 44000.00 | 1800.00 | 144000.00 | 1500.00 | 120000.00 | 1196.00 | 95680.00 | 1700.00 | 136000.00 | 1360.00 | 108800.00 | 750.00 | 60000.00 | 3552.00 | Messers Rajesh Gawde
20.10 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. Upto 35 sq. mm | 1445.00 | Meter |  | 30.00 | 43350.00 | 78.00 | 112710.00 | 66.60 | 96237.00 | 25.00 | 36125.00 | 80.00 | 115600.00 | 100.00 | 144500.00 | 30.00 | 43350.00 | 32.00 | 46240.00 | 15.00 | 21675.00 | 28.00 | 40460.00 | 70.00 | 101150.00 | 21675.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
20.20 | Above 35 sq. mm and upto 95 sq. mm | 20.00 | Meter |  | 35.00 | 700.00 | 91.00 | 1820.00 | 99.90 | 1998.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 200.00 | 4000.00 | 30.00 | 600.00 | 42.00 | 840.00 | 25.00 | 500.00 | 40.00 | 800.00 | 80.00 | 1600.00 | 500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Ascent Electrification Engineers
20.30 | Above 95 sq. mm and upto 185 sq. mm | 310.00 | Meter |  | 50.00 | 15500.00 | 156.00 | 48360.00 | 44.40 | 13764.00 | 25.00 | 7750.00 | 60.00 | 18600.00 | 300.00 | 93000.00 | 30.00 | 9300.00 | 52.00 | 16120.00 | 35.00 | 10850.00 | 56.00 | 17360.00 | 80.00 | 24800.00 | 7750.00 | Ascent Electrification Engineers
21.10 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Upto 35 sq. mm | 20.00 | Meter |  | 30.00 | 600.00 | 78.00 | 1560.00 | 66.60 | 1332.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 80.00 | 1600.00 | 30.00 | 600.00 | 32.00 | 640.00 | 15.00 | 300.00 | 20.00 | 400.00 | 50.00 | 1000.00 | 300.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
21.20 | Above 35 sq. mm and upto 95 sq. mm | 20.00 | Meter |  | 35.00 | 700.00 | 91.00 | 1820.00 | 99.90 | 1998.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 150.00 | 3000.00 | 30.00 | 600.00 | 42.00 | 840.00 | 30.00 | 600.00 | 48.00 | 960.00 | 50.00 | 1000.00 | 500.00 | Ascent Electrification Engineers
21.30 | Above 95 sq. mm and upto 185 sq. mm | 20.00 | Meter |  | 50.00 | 1000.00 | 156.00 | 3120.00 | 33.30 | 666.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 230.00 | 4600.00 | 30.00 | 600.00 | 52.00 | 1040.00 | 40.00 | 800.00 | 88.00 | 1760.00 | 60.00 | 1200.00 | 500.00 | Ascent Electrification Engineers
22.10 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 30.00 | Meter |  | 50.00 | 1500.00 | 78.00 | 2340.00 | 44.40 | 1332.00 | 25.00 | 750.00 | 60.00 | 1800.00 | 80.00 | 2400.00 | 30.00 | 900.00 | 52.00 | 1560.00 | 30.00 | 900.00 | 40.00 | 1200.00 | 70.00 | 2100.00 | 750.00 | Ascent Electrification Engineers
22.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 20.00 | Meter |  | 55.00 | 1100.00 | 91.00 | 1820.00 | 49.95 | 999.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 150.00 | 3000.00 | 30.00 | 600.00 | 73.00 | 1460.00 | 90.00 | 1800.00 | 96.00 | 1920.00 | 70.00 | 1400.00 | 500.00 | Ascent Electrification Engineers
22.30 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 20.00 | Meter |  | 65.00 | 1300.00 | 156.00 | 3120.00 | 49.95 | 999.00 | 25.00 | 500.00 | 60.00 | 1200.00 | 230.00 | 4600.00 | 30.00 | 600.00 | 104.00 | 2080.00 | 100.00 | 2000.00 | 120.00 | 2400.00 | 80.00 | 1600.00 | 500.00 | Ascent Electrification Engineers
23.00 | Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type Floor Mounted panel (with IP 54 protection) fabricated from 2mm thick CRCA sheet (Thickness of partition Minimum 1.6mm ) including making suitable size concreate foundation, suitable angle/ channels frame, providing suitable size of HDPE bend pipe in foundation for cable entry, supply and fixing of following switchgears and accessories complete with busbars,glande plates, neutral link, interconnections, earth connections, CT's, ammeter and voltmeter with selector switches and LED phase indicating lamps etc complete as required as per tender specifications, site requirement and approved make. (GEB LT PANEL) Incomer: 250A, MCCB, 4P, 50 kA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 Nos. Multi function meter (Shows Voltage, Current, Power, Energy & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 01 Nos. Indication Lamp R, Y & B (LED Type) -01 set Outgoing : 200A, MCCB, 4P, 50 kA (Icu= 100% Ics) with extended rotary handle - 03 Nos. Indication Lamp R & G (LED type) - 03 Set 63A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 01 Nos. Indication Lamp R & G (LED type) - 01 Set Other : 400A AL busbar, 4 Pole Mechanical key lock (1 Lock + 1 Key) Necessary CT & Control wiring arrangement Power terminal Block and other accessories Three Phase Surge Protection Device (SPD) having nominal dischage current (L-N/N-PE) =25 /100 kA (8/20 us) Lightning impulse current (L1 + L2 + L 3 + N -PE=100kA (10/350 us) & (L-N / N-PE = 25/100 kA) with voltage protection level <=1.5 kV (L-N/N-PE) including all accessories for installing on the mains power entry point at the busbar shall be of modular type. [ Make:-DEHN Model No. DV M TT 255 FM (951 315) or equivalent appproved make ] - 01 No. | 1.00 | Each |  | 175000.00 | 175000.00 | 264000.00 | 264000.00 | 382950.00 | 382950.00 | 281980.00 | 281980.00 | 188000.00 | 188000.00 | 322000.00 | 322000.00 | 306240.00 | 306240.00 | 348400.00 | 348400.00 | 310000.00 | 310000.00 | 172000.00 | 172000.00 | 200000.00 | 200000.00 | 172000.00 | Edge Telecom Pvt Ltd
24.00 | Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type Floor Mounted panel (with IP 54 protection) fabricated from 2mm thick CRCA sheet (Thickness of partition Minimum 1.6mm ) including making suitable size concreate foundation,suitable angle/ channels frame, providing suitable size of HDPE bend pipe in foundation for cable entry, supply and fixing of following switchgears and accessories complete with busbars,glande plates, neutral link, interconnections, earth connections, CT's, ammeter and voltmeter with selector switches and LED phase indicating lamps etc complete as required as per tender specifications, site requirement and approved make. (GEB LT PANEL) .( LT PANEL- LAL TANK PUMP ROOM) Incomer: 200A, MCCB, 4P, 50 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. Multi function meter (Shows Voltage, Current, Power, Energy & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 02 Nos. Indication Lamp R, Y & B (LED Type) -02 set Mechanical key lock (2 Lock + 1 Key) Outgoing : 125A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 01 Nos. Indication Lamp R & G (LED type) - 01 Set 63A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 06 Nos. Indication Lamp R & G (LED type) - 07 Set 40A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 02 Nos. Indication Lamp R & G (LED type) - 02 Set Digital Timer Current - 8A, Voltage- 240V AC, Opt. temp --10 to +55 Deg, multifunction Timer, Din rail Mount Contactor 3P, 63A - 01 Set Other : 400A Aluminimum busbar, 4 Pole Necessary CT & Control wiring arrangement Power terminal and other accessories | 1.00 | Each |  | 292000.00 | 292000.00 | 426135.00 | 426135.00 | 377400.00 | 377400.00 | 332465.00 | 332465.00 | 155000.00 | 155000.00 | 250000.00 | 250000.00 | 365000.00 | 365000.00 | 322400.00 | 322400.00 | 360000.00 | 360000.00 | 176000.00 | 176000.00 | 160000.00 | 160000.00 | 155000.00 | Variant Infratech Private Limited
25.00 | Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type Floor Mounted panel (with IP 54 protection) fabricated from 2mm thick CRCA sheet (Thickness of partition Minimum 1.6mm ) including making suitable size concreate foundation, suitable angle/ channels frame, providing suitable size of HDPE bend pipe in foundation for cable entry, supply and fixing of following switchgears and accessories complete with busbars,glande plates, neutral link, interconnections, earth connections, CT's, ammeter and voltmeter with selector switches and LED phase indicating lamps etc complete as required as per tender specifications, site requirement and approved make. ( LT PANEL- OLD COLONY) Incomer: 250A, MCCB, 4P, 50 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 02 Nos. Indication Lamp R, Y & B (LED Type) -02 set Mechanical key lock (2 Lock + 1 Key) Outgoing : 125A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 02 Nos. Indication Lamp R & G (LED type) - 01 Set 63A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 06 Nos. Indication Lamp R & G (LED type) - 06 Set 40A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 02 Nos. Indication Lamp R & G (LED type) - 02 Set Digital Timer [ Current - 8A, Voltage- 240V AC, Opt. temp --10 to +55 Deg, multifunction Timer, Din rail Mount Contactor 3P, 63A - 01 Set Other : 400A Aluminimum busbar, 4 Pole Necessary CT & Control wiring arrangement Power terminal and other accessories | 1.00 | Each |  | 350000.00 | 350000.00 | 48405.00 | 48405.00 | 416250.00 | 416250.00 | 337180.00 | 337180.00 | 145000.00 | 145000.00 | 350000.00 | 350000.00 | 370000.00 | 370000.00 | 348400.00 | 348400.00 | 360000.00 | 360000.00 | 260000.00 | 260000.00 | 190000.00 | 190000.00 | 48405.00 | Instapower Ltd
26.00 | Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, out door feeder pillar made out of 2mm thick CRCA sheet (Thickness of partition Minimum 1.6mm ) of size 1200mm x 800mm x 400mm, having four frangible legs of suitable length each of angle iron 35mm X 35mm x 5 mm size and canopy cover in hut shape (size- more than 3 cm from feeder from all 4 side) , 4 Pole aluminum busbars of rating 200A, Incomer 125A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) interconnected with busbars, painting and writing i/c danger plate, fixing with cement concrete (1:2:4) and also making the cement concrete bed (1:4:8) of radius one meter around the feeder pillar of 100mm thickness,providing suitable size of HDPE bend pipe in foundation for cable entry, etc. as per tender specification, site requirement.(Feeder panel -1 & 2) | 2.00 | Each |  | 15000.00 | 30000.00 | 45850.00 | 91700.00 | 66600.00 | 133200.00 | 46805.00 | 93610.00 | 31000.00 | 62000.00 | 50000.00 | 100000.00 | 55440.00 | 110880.00 | 43680.00 | 87360.00 | 55000.00 | 110000.00 | 48000.00 | 96000.00 | 100000.00 | 200000.00 | 30000.00 | Techno Electricals
27.00 | Supply, Installation & Erection of 5 Mtr height hot dip galvanized octagonal pole of top minimum dia 70mm & Bottom minimum dia 130mm and 3mm thickness, minimum base plate of size 200x200x12mm welded to bottom of the pole having hinged lockable Terminal box door along with 4 Nos. foundation bolts with single arm tilt bracket of length approx. 600 mm for mounting of fitting suitable to mount for street light fittings at top including supply of foundation bolts manufactured from special steel along with nuts, washers etc., providing bake lite sheet with stud type 4 pole connectors of suitable rating, DIN Rail for mounting of MCB in the terminal box, 5A-32A DP MCB, 3Cx1.5 sq mm cu cable from connector to fitting connector, etc. as required. Erecting the same on cement concrete foundation with a concrete mixture of 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation which also includes excavation and refilling, providing minimu 2 nos of L shape HDPE pipe in pole from bottom side etc. as required as site requirement and specification. | 30.00 | Each |  | 13137.00 | 394110.00 | 10695.00 | 320850.00 | 13875.00 | 416250.00 | 11500.00 | 345000.00 | 8600.00 | 258000.00 | 12500.00 | 375000.00 | 15400.00 | 462000.00 | 12480.00 | 374400.00 | 11000.00 | 330000.00 | 6000.00 | 180000.00 | 12000.00 | 360000.00 | 180000.00 | Edge Telecom Pvt Ltd
28.00 | Supply and fixing of single arm tilt bracket of length approx. 600 mm for mounting of fitting suitable to mount for street light fittings at top of existing street pole including providing bake lite sheet with stud type 4 pole connectors of suitable rating, DIN Rail for mounting of MCB in the terminal box, 5A-32A DP MCB, 3Cx1.5 sq mm cu cable from connector to fitting connector which also includes removal of paver bloack, breaking of hard rock, excavation, refilling same, fixing of paver block as same and providing & fixing minimum 2 nos of L shape HDPE pipe in pole from bottom side etc. as required as site requirement and specification. | 12.00 | Each |  | 2000.00 | 24000.00 | 3980.00 | 47760.00 | 5550.00 | 66600.00 | 173.00 | 2076.00 | 1650.00 | 19800.00 | 2500.00 | 30000.00 | 750.00 | 9000.00 | 2808.00 | 33696.00 | 3000.00 | 36000.00 | 2800.00 | 33600.00 | 1500.00 | 18000.00 | 2076.00 | Ascent Electrification Engineers
29.00 | Supply and fixing of round arm bracket of dia approx. 1200 mm for mounting of fitting suitable to mount for flood light fittings at top of existing street pole including providing bake lite sheet with stud type 4 pole connectors of suitable rating, DIN Rail for mounting of MCB in the terminal box, 5A-32A DP MCB, 3C x 2.5 sq mm cu cable from connector to fittings connector, termination with minimum 3 nos of fittings which also includes removal of paver bloack, breaking of hard rock, excavation, refilling same, fixing of paver block as same and providing & fixing minimum 2 nos of L shape HDPE pipe in pole from bottom side etc. as required as site requirement and specification. | 4.00 | Each |  | 3500.00 | 14000.00 | 4300.00 | 17200.00 | 6660.00 | 26640.00 | 173.00 | 692.00 | 2250.00 | 9000.00 | 8500.00 | 34000.00 | 4000.00 | 16000.00 | 3328.00 | 13312.00 | 5000.00 | 20000.00 | 960.00 | 3840.00 | 1800.00 | 7200.00 | 692.00 | Ascent Electrification Engineers
30.00 | Supply & fixing of 1Mtr wide & 2MM Thick, ISI marked Electrical Insulating Mats Confirming to IS: 15652 / 2006 with help of SR 998 Adhesives, Working voltage upto 3.3 KV. | 100.00 | Meter |  | 1200.00 | 120000.00 | 626.50 | 62650.00 | 666.00 | 66600.00 | 863.00 | 86300.00 | 1750.00 | 175000.00 | 1200.00 | 120000.00 | 800.00 | 80000.00 | 520.00 | 52000.00 | 500.00 | 50000.00 | 1440.00 | 144000.00 | 1200.00 | 120000.00 | 50000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
31.00 | Earthing with G.I. earth pipe (B- Class) 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required | 6.00 | Set |  | 6500.00 | 39000.00 | 6225.00 | 37350.00 | 8880.00 | 53280.00 | 5500.00 | 33000.00 | 1650.00 | 9900.00 | 8500.00 | 51000.00 | 3000.00 | 18000.00 | 4784.00 | 28704.00 | 5500.00 | 33000.00 | 4800.00 | 28800.00 | 7500.00 | 45000.00 | 9900.00 | Variant Infratech Private Limited
32.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with heavy duty cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 8000.00 | 48000.00 | 10775.00 | 64650.00 | 7770.00 | 46620.00 | 6500.00 | 39000.00 | 1850.00 | 11100.00 | 1500.00 | 9000.00 | 8000.00 | 48000.00 | 6760.00 | 40560.00 | 6000.00 | 36000.00 | 5600.00 | 33600.00 | 6500.00 | 39000.00 | 9000.00 | MITESH R HAPANI
33.00 | Supplying and laying 6 SWG G.I. wire at 0.50 meter below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 2775.00 | Meter |  | 75.00 | 208125.00 | 74.30 | 206182.50 | 36.63 | 101648.25 | 59.00 | 163725.00 | 130.00 | 360750.00 | 125.00 | 346875.00 | 30.00 | 83250.00 | 37.00 | 102675.00 | 25.00 | 69375.00 | 40.00 | 111000.00 | 60.00 | 166500.00 | 69375.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
34.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 20.00 | Meter |  | 30.00 | 600.00 | 74.30 | 1486.00 | 33.30 | 666.00 | 22.00 | 440.00 | 160.00 | 3200.00 | 50.00 | 1000.00 | 20.00 | 400.00 | 32.00 | 640.00 | 30.00 | 600.00 | 32.00 | 640.00 | 50.00 | 1000.00 | 400.00 | GAYATRI ELECTRICAL
35.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 10.00 | Meter |  | 300.00 | 3000.00 | 198.00 | 1980.00 | 144.30 | 1443.00 | 150.00 | 1500.00 | 190.00 | 1900.00 | 270.00 | 2700.00 | 180.00 | 1800.00 | 146.00 | 1460.00 | 125.00 | 1250.00 | 112.00 | 1120.00 | 170.00 | 1700.00 | 1120.00 | Edge Telecom Pvt Ltd
36.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 70.00 | Meter |  | 750.00 | 52500.00 | 198.00 | 13860.00 | 588.30 | 41181.00 | 577.00 | 40390.00 | 220.00 | 15400.00 | 1250.00 | 87500.00 | 315.00 | 22050.00 | 442.00 | 30940.00 | 600.00 | 42000.00 | 560.00 | 39200.00 | 250.00 | 17500.00 | 13860.00 | Instapower Ltd
37.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 25.00 | Meter |  | 250.00 | 6250.00 | 198.00 | 4950.00 | 133.20 | 3330.00 | 146.00 | 3650.00 | 190.00 | 4750.00 | 200.00 | 5000.00 | 145.00 | 3625.00 | 141.00 | 3525.00 | 190.00 | 4750.00 | 192.00 | 4800.00 | 150.00 | 3750.00 | 3330.00 | Messers Rajesh Gawde
38.10 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 4 X 16 sq. mm (28mm) | 5.00 | Each |  | 350.00 | 1750.00 | 348.40 | 1742.00 | 55.50 | 277.50 | 250.00 | 1250.00 | 120.00 | 600.00 | 250.00 | 1250.00 | 100.00 | 500.00 | 125.00 | 625.00 | 350.00 | 1750.00 | 232.00 | 1160.00 | 600.00 | 3000.00 | 277.50 | Messers Rajesh Gawde
38.20 | 4 X 25 sq. mm (28mm) | 24.00 | Each |  | 450.00 | 10800.00 | 453.45 | 10882.80 | 88.80 | 2131.20 | 250.00 | 6000.00 | 160.00 | 3840.00 | 350.00 | 8400.00 | 200.00 | 4800.00 | 136.00 | 3264.00 | 350.00 | 8400.00 | 240.00 | 5760.00 | 700.00 | 16800.00 | 2131.20 | Messers Rajesh Gawde
38.30 | 3.5 X 50 sq. mm (35mm) | 1.00 | Each |  | 450.00 | 450.00 | 728.05 | 728.05 | 111.00 | 111.00 | 750.00 | 750.00 | 200.00 | 200.00 | 500.00 | 500.00 | 200.00 | 200.00 | 260.00 | 260.00 | 350.00 | 350.00 | 320.00 | 320.00 | 900.00 | 900.00 | 111.00 | Messers Rajesh Gawde
38.40 | 3.5 X 70 sq. mm (38mm) | 2.00 | Each |  | 500.00 | 1000.00 | 885.75 | 1771.50 | 166.50 | 333.00 | 850.00 | 1700.00 | 250.00 | 500.00 | 650.00 | 1300.00 | 250.00 | 500.00 | 312.00 | 624.00 | 370.00 | 740.00 | 336.00 | 672.00 | 900.00 | 1800.00 | 333.00 | Messers Rajesh Gawde
38.50 | 3.5 X 95 sq. mm (45mm) | 3.00 | Each |  | 500.00 | 1500.00 | 1087.45 | 3262.35 | 199.80 | 599.40 | 1000.00 | 3000.00 | 280.00 | 840.00 | 1000.00 | 3000.00 | 300.00 | 900.00 | 364.00 | 1092.00 | 500.00 | 1500.00 | 440.00 | 1320.00 | 900.00 | 2700.00 | 599.40 | Messers Rajesh Gawde
38.60 | 3.5 X 120 sq. mm (45mm) | 8.00 | Each |  | 750.00 | 6000.00 | 1176.30 | 9410.40 | 222.00 | 1776.00 | 1250.00 | 10000.00 | 320.00 | 2560.00 | 1500.00 | 12000.00 | 300.00 | 2400.00 | 396.00 | 3168.00 | 550.00 | 4400.00 | 480.00 | 3840.00 | 1200.00 | 9600.00 | 1776.00 | Messers Rajesh Gawde
38.70 | 3.5 X 240 sq. mm (62mm) | 1.00 | Each |  | 1000.00 | 1000.00 | 1810.55 | 1810.55 | 277.50 | 277.50 | 1650.00 | 1650.00 | 350.00 | 350.00 | 2500.00 | 2500.00 | 300.00 | 300.00 | 520.00 | 520.00 | 800.00 | 800.00 | 800.00 | 800.00 | 1500.00 | 1500.00 | 277.50 | Messers Rajesh Gawde
39.10 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 1.1 KV grade as required 4 X 16 sq. mm | 6.00 | Each |  | 1500.00 | 9000.00 | 93.71 | 562.26 | 610.50 | 3663.00 | 500.00 | 3000.00 | 3850.00 | 23100.00 | 7500.00 | 45000.00 | 3000.00 | 18000.00 | 1560.00 | 9360.00 | 2000.00 | 12000.00 | 1680.00 | 10080.00 | 1200.00 | 7200.00 | 562.26 | Instapower Ltd
39.20 | 4 X 25 sq. mm | 8.00 | Each |  | 1500.00 | 12000.00 | 103.71 | 829.68 | 721.50 | 5772.00 | 500.00 | 4000.00 | 3850.00 | 30800.00 | 8500.00 | 68000.00 | 3000.00 | 24000.00 | 1798.00 | 14384.00 | 2000.00 | 16000.00 | 1920.00 | 15360.00 | 1400.00 | 11200.00 | 829.68 | Instapower Ltd
39.30 | 3.5 X 50 sq. mm | 2.00 | Each |  | 2000.00 | 4000.00 | 133.18 | 266.36 | 832.50 | 1665.00 | 500.00 | 1000.00 | 4200.00 | 8400.00 | 10000.00 | 20000.00 | 3000.00 | 6000.00 | 2288.00 | 4576.00 | 2200.00 | 4400.00 | 1920.00 | 3840.00 | 2000.00 | 4000.00 | 266.36 | Instapower Ltd
39.40 | 3.5 X 70 sq. mm | 2.00 | Each |  | 2000.00 | 4000.00 | 148.85 | 297.70 | 943.50 | 1887.00 | 1000.00 | 2000.00 | 4200.00 | 8400.00 | 12500.00 | 25000.00 | 3000.00 | 6000.00 | 2600.00 | 5200.00 | 2800.00 | 5600.00 | 2640.00 | 5280.00 | 2500.00 | 5000.00 | 297.70 | Instapower Ltd
39.50 | 3.5 X 95 sq. mm | 2.00 | Each |  | 2500.00 | 5000.00 | 165.33 | 330.66 | 1054.50 | 2109.00 | 1250.00 | 2500.00 | 4500.00 | 9000.00 | 15000.00 | 30000.00 | 3000.00 | 6000.00 | 2808.00 | 5616.00 | 2900.00 | 5800.00 | 2800.00 | 5600.00 | 3000.00 | 6000.00 | 330.66 | Instapower Ltd
39.60 | 3.5 X 120 sq. mm | 3.00 | Each |  | 2500.00 | 7500.00 | 175.33 | 525.99 | 1332.00 | 3996.00 | 1850.00 | 5550.00 | 5200.00 | 15600.00 | 18500.00 | 55500.00 | 4000.00 | 12000.00 | 3952.00 | 11856.00 | 2900.00 | 8700.00 | 3600.00 | 10800.00 | 3500.00 | 10500.00 | 525.99 | Instapower Ltd
39.70 | 3.5 X 240 sq. mm | 1.00 | Each |  | 3500.00 | 3500.00 | 237.17 | 237.17 | 1998.00 | 1998.00 | 2000.00 | 2000.00 | 5500.00 | 5500.00 | 25000.00 | 25000.00 | 4000.00 | 4000.00 | 5200.00 | 5200.00 | 5500.00 | 5500.00 | 3920.00 | 3920.00 | 4500.00 | 4500.00 | 237.17 | Instapower Ltd
40.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting/LED fitting of all types upto height of 10 meter, complete with all accessories and tube etc. directly on ceiling/ false ceiling/ wall/ Pole/Banner,including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. (supporting structure for fitting , rectification of reducer or adjustment of angle of light or minor cutting and welding etc as per site requirement and stairs/ scaffolding will be under scope of this item ) | 538.00 | Job |  | 650.00 | 349700.00 | 468.00 | 251784.00 | 777.00 | 418026.00 | 690.00 | 371220.00 | 750.00 | 403500.00 | 1000.00 | 538000.00 | 250.00 | 134500.00 | 208.00 | 111904.00 | 175.00 | 94150.00 | 80.00 | 43040.00 | 500.00 | 269000.00 | 43040.00 | Edge Telecom Pvt Ltd
41.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting/LED fitting of all types upto height of 20 meter, complete with all accessories and tube etc. directly on ceiling/ false ceiling/ wall/ Pole/Banner,including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. (supporting structure for fitting , rectification of reducer or adjustment of angle of light or minor cutting and welding etc as per site requirement and boom lift/ scaffolding will be under scope this item ) | 158.00 | Job |  | 900.00 | 142200.00 | 1625.00 | 256750.00 | 2500.00 | 395000.00 | 690.00 | 109020.00 | 1850.00 | 292300.00 | 1200.00 | 189600.00 | 1000.00 | 158000.00 | 364.00 | 57512.00 | 500.00 | 79000.00 | 144.00 | 22752.00 | 600.00 | 94800.00 | 22752.00 | Edge Telecom Pvt Ltd
42.00 | SITC of 1 phase module, 24 Hours Programmable Digital Automatic Time Switch , 240V,50Hz, etc in suitable Enclosure as per site requirement (Make- Legrand, Cat No.- 412631, Model- ALPHAREX D22 or equivalent AAI approved make ) | 23.00 | Job |  | 5000.00 | 115000.00 | 4655.00 | 107065.00 | 8880.00 | 204240.00 | 8338.00 | 191774.00 | 1750.00 | 40250.00 | 9000.00 | 207000.00 | 6000.00 | 138000.00 | 6448.00 | 148304.00 | 4800.00 | 110400.00 | 6000.00 | 138000.00 | 7000.00 | 161000.00 | 40250.00 | Variant Infratech Private Limited
43.00 | SITC of Computer for Fire control monitoring system having 13th Gen Intel® Core™ i7-13700 (13th Gen) Processor including Serial ports (RS232), media card reader, TCP/IP Giga Ethernet Network Adapter ,internal speaker and ports (USB 2.0- 02 Nos, USB 3.2 Gen 2- 1 No, USB 3.2 Gen 2x2 Type-C​- 1 No.) and following accessories etc. complete with software all as specified a) 16 GB, 2 x 8 GB, DDR5 RAM memory b) 500 Gigabytes of hard disk space c) 256 Gigabytes of M.2 SSD additional c) DVD ROM d) more than 22" Full HD, virtually borderless, IPS Panel colour monitor with suitable ports. e) Mouse with Mouse Pad f) English International keyboard (Plunger technology) g) Windows 11 Pro Operating System h) Graphics card- 6 GB i) Warranty, Accidental Damage Protection and ProSupport service on Next Business Day Onsite for 36 Month(s) from OEM | 1.00 | Set |  | 158538.00 | 158538.00 | 44200.00 | 44200.00 | 75000.00 | 75000.00 | 75000.00 | 75000.00 | 245000.00 | 245000.00 | 150000.00 | 150000.00 | 135000.00 | 135000.00 | 158080.00 | 158080.00 | 129725.00 | 129725.00 | 48000.00 | 48000.00 | 80000.00 | 80000.00 | 44200.00 | Instapower Ltd
44.00 | SITC of UL/FM Listed VESDA Panel on the place of existing vesda panel suitable for integration with existing vesda panel (Make- System Sensor, Model- 9400X) and monitor module/ Comupter system all acessoseries required as per site reqirement. (Make- Honeywell, Model- VEP-A10-P or equivalent as per AAI preferred make list) | 3.00 | Set |  | 415000.00 | 1245000.00 | 247060.00 | 741180.00 | 471750.00 | 1415250.00 | 435615.00 | 1306845.00 | 215000.00 | 645000.00 | 250000.00 | 750000.00 | 510000.00 | 1530000.00 | 52000.00 | 156000.00 | 450000.00 | 1350000.00 | 640000.00 | 1920000.00 | 550000.00 | 1650000.00 | 156000.00 | girnar electricals
45.00 | Supply of resin for softener water treatement plant which having minimum exchange capacity 2.0 meq/ml and other technical data as per details mentioned in specification. (Make: ION Exchange, Model: INDION 225 Na or Equivalent) | 5200.00 | Ltrs |  | 132.00 | 686400.00 | 181.50 | 943800.00 | 172.05 | 894660.00 | 131.00 | 681200.00 | 215.00 | 1118000.00 | 250.00 | 1300000.00 | 145.00 | 754000.00 | 177.00 | 920400.00 | 115.00 | 598000.00 | 170.00 | 884000.00 | 150.00 | 780000.00 | 598000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
46.00 | Removal,packing and placing of old resin (within airport premises) as directed by EIC, filling of new resin in the existing vessel, testing and comissiong of softener water plant, tools and other all minor accessories as per site requirement shall be arrange by agency. | 2.00 | Job |  | 34500.00 | 69000.00 | 16000.00 | 32000.00 | 33300.00 | 66600.00 | 10000.00 | 20000.00 | 176000.00 | 352000.00 | 25000.00 | 50000.00 | 15000.00 | 30000.00 | 4160.00 | 8320.00 | 1000.00 | 2000.00 | 40000.00 | 80000.00 | 120000.00 | 240000.00 | 2000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
47.00 | SITC of touch free Stainless steel-Brushed (304L) airblade (without heating element) having high efficiency particulate air (HEPA) filtered ( cable to captures more than 99.90% of particles as small as 0.1 microns) , throw air speed more than 600 km/h, minimum operating airflow 22 Litre / second, Motor speed more than 70000 RPM, capable to hand dry in 10 sec (max), noise less than 85 dB , IP24, Maximum upto 950W motor suitable for 160-253 V, 50-60 Hz single phase supply and warranty for all parts for 05 years from OEM (Make- Dyson, model-air blade 9kJ or Equivalent) | 8.00 | Job |  | 93168.00 | 745344.00 | 98750.00 | 790000.00 | 111000.00 | 888000.00 | 107350.00 | 858800.00 | 211000.00 | 1688000.00 | 20000.00 | 160000.00 | 121200.00 | 969600.00 | 110500.00 | 884000.00 | 75000.00 | 600000.00 | 100000.65 | 800005.20 | 110000.00 | 880000.00 | 160000.00 | MITESH R HAPANI
| Total in Figures |  |  |  |  | 8089828.00 |  | 7563394.97 |  | 9177346.70 |  | 8005998.00 |  | 9090467.00 |  | 8949175.00 |  | 8570955.00 |  | 7424931.00 |  | 7024940.00 |  | 8254189.20 |  | 8600600.00
Lowest Amount Quoted BY: Krishsons International Engineers And Consultants (I) Pvt. Ltd(7024940.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Lighting on walking track of park, replacement of LT Panel of old colony and other miscellaneous works at Vadodara Airport. Tender ID: 2023_AAI_175937_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Krishsons International Engineers And Consultants (I) Pvt. Ltd | 7024940.00 | L1
| 2 | girnar electricals | 7424931.00 | L2
| 3 | Instapower Ltd | 7563394.97 | L3
| 4 | Ascent Electrification Engineers | 8005998.00 | L4
| 5 | Techno Electricals | 8089828.00 | L5
| 6 | Edge Telecom Pvt Ltd | 8254189.20 | L6
| 7 | GAYATRI ELECTRICAL | 8570955.00 | L7
| 8 | Patel Electricals | 8600600.00 | L8
| 9 | MITESH R HAPANI | 8949175.00 | L9
| 10 | Variant Infratech Private Limited | 9090467.00 | L10
| 11 | Messers Rajesh Gawde | 9177346.70 | L11