## BoQ1
Government eProcurement System Created By: ANANTHASUBRAMANIAN P R Created Date/Time: 08-Jan-2024 05:32 PM Tender Title: Augmentation of Power supply to GLF by Provision of UPS Tender ID: 2023_AAI_176152_1
Tender Inviting Authority: Senior Manager(Engg-E), AAI, Kadapa Airport, Kadapa (A.P)-516003.
Name of Work: Augmentation of Power Supply to GLF by Provision of UPS and associated electrical works at Kadapa Airport.
Contract No: 2023_AAI_176152_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | surbhi association(GSTN-23AGKPD2522N1ZK) |  | SUN POWER CONVERSION PVT LTD(GSTN-09AAICS9074K1ZL) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Part - I (Capital Works) 2 X 80 KVA capacity, 3-phase input / 3 phase output online UPS Supply, Installation, Testing and Commissioning (SITC) of 2 X 80 KVA capacity, 3-phase input / 3 phase output online UPS with double conversion type advance IGBT technology with suitable rated (min. K-13) inbuilt isolation transformer to drive constant current regulators with 100% unbalanced load at various loads incl. full load condition. The UPS shall have built in 100% rated automatic static by pass, manual by pass facilities for maintenance, active input power factor correction, phase sequence corrector, pure sine wave output, input/output isolation, compatibility with generator supply, cold start capability, EMI/RFI noise filter, advanced communication- RS232/RS485 ports and user friendly LCD display and run in parallel redundant system configuration for equal sharing of load,battery management features integrated with main UPS controller, suitable to operate at 400V±15%, 50Hz, 3 phase AC supply, suitable IP rated enclosure and capable to take 2 phase & single phase loads on 3phase output of UPS with 100% unbalanced and necessary safety protections etc complete as required. The job also includes supply, Installation, Testing & Commissioning of battery bank sets of required/suitable size with required number of VRLA SMF batteries suitable to give a backup time of minimum 30 minutes per each UPS in all load conditions as stipulated for UPS, along with battery racks/enclosure, suitable rated battery circuit breaker, interconnections between batteries as well as battery bank to UPS with suitable insulated copper conductors, connectors, glanding & terminations etc., complete as required. | 1.00 | Job |  | 3600000.00 | 3600000.00 | 3300000.00 | 3300000.00 | 3395000.00 | 3395000.00 | 3300000.00 | SUN POWER CONVERSION PVT LTD
2.00 | UPS Input panel: Design, Fabrication, Assembling, Supply,Installation, Testing and Commissioning of self-standing, floor mounted indoor type LT cubicle panel made out of 14SWG CRCA sheet steel, totally enclosed, weather, dust, vermin proof ; having IP class of not less than IP-42, fully compartmentalized, Form 4 b separation, , with high conductivity aluminium bas bar having minimum current capacity of 400 A, suitable for operation at 415 V, 3 phase, 4 Wire, 50 Hz AC system complete with all accessories, making all necessary connections and interconnections, providing and fixing required set of metering and protection CTs of appropriate class and burden, cable alley for termination of cables with top/bottom entry as required as per site conditions, necessary locking arrangements, powder coated with approved shade etc. A bottom base channel of suitable size and thickness, shall be provided during installation. Two runs of GI earth bar shall run throughout the entire length and also pass through all compartments. The size of the GI earth bar shall be designed as per the SC fault current at the site. Overall, the LT panel shall comply with the relevant IS and the tender technical specifications in complete . If BIS specifications are not available, relevant IEC shall be applicable. INCOMERS: i) Thermal Magnetic MCCB , 250 A , 4 Pole, 415V , 36KA (ICu=ICs) with inbuilt adjustable overload & short circuit protection with Spreader link & Suitable Extended Rotary Handle - 02 Nos. ii) Digital Multi Function Meter , 3 Nos CTs of Suitable Amps ratio having Class 1 Accuracy - 02 Sets iii) R,Y ,B Phase Indication LED lamps for each phase with 3 Nos of 2A ,MCBS & Breaker Indication Lamps (ON/OFF/TRIP) with 2A control MCBs -02 Sets. iv) Two incomers shall be with suitable interlocking such that only one MCCB shall be operative at a time. OUTGOINGS : i) Thermal Magnetic MCCB , 250 A , 4 Pole, 415V , 36 KA (ICu=ICs) with inbuilt adjustable overload & Short Circuit protection with Spreader link & Suitable Extended Rotary Handle- 3 Nos ii) Thermal magnetic MCCB 63 A, 4 Pole, 415V, 36 KA (ICu=ICs) with input adjustable overload & Short Circuit protection with Spreader link & Suitable Extended Rotary Handle - 02 Nos. ii)Breaker Indication Lamps(ON/OFF/TRIP ) with 2A control MCBs - 5 Sets. | 1.00 | Job |  | 550000.00 | 550000.00 | 200000.00 | 200000.00 | 395000.00 | 395000.00 | 200000.00 | SUN POWER CONVERSION PVT LTD
3.00 | UPS Output panel: Design, Fabrication, Assembling, Supply,Installation, Testing and Commissioning of self-standing, floor mounted indoor type LT cubicle panel made out of 14SWG CRCA sheet steel, totally enclosed, weather, dust, vermin proof ; having IP class of not less than IP-42, fully compartmentalized, Form 4 b separation, , with high conductivity aluminium bas bar having minimum current capacity of 400 A, suitable for operation at 415 V, 3 phase, 4 Wire, 50 Hz AC system complete with all accessories, making all necessary connections and interconnections, providing and fixing required set of metering and protection CTs of appropriate class and burden, cable alley for termination of cables with top/bottom entry as required as per site conditions, necessary locking arrangements, powder coated with approved shade etc. A bottom base channel of suitable size and thickness, shall be provided during installation. Two runs of GI earth bar shall run throughout the entire length and also pass through all compartments. The size of the GI earth bar shall be designed as per the SC fault current at the site. Overall, the LT panel shall comply with the relevant IS and the tender technical specifications in complete . If BIS specifications are not available, relevant IEC shall be applicable. INCOMER: i) Thermal Magnetic MCCB , 250 A , 4 Pole, 415V , 36KA (ICu=ICs) with inbuilt adjustable overload & short circuit protection with Spreader link & Suitable Extended Rotary Handle -02 Nos. ii) Digital Multi Function Meter , 3 Nos CTs of Suitable Amps ratio having Class 1 Accuracy - 02 Sets iii) R,Y ,B Phase Indication LED lamps for each phase with 3 Nos of 2A ,MCBS & Breaker Indication Lamps (ON/OFF/TRIP) with 2A control MCBs -02 Sets. Outgoing : i) Thermal Magnetic MCCB , 250 A , 4 Pole, 415V , 36 KA (ICu=ICs) with inbuilt adjustable overload & Short Circuit protection with Spreader link & Suitable Extended Rotary Handle- 02 Nos ii) Thermal Magnetic MCCB , 32 A , 4 Pole, 415V , 36 KA (ICu=ICs) with inbuilt adjustable overload & Short Circuit protection with Spreader link & Suitable Extended Rotary Handle- 02 Nos iii)Breaker Indication Lamps(ON/OFF/TRIP ) with 2A control MCBs - 04 Sets. | 1.00 | Job |  | 500000.00 | 500000.00 | 200000.00 | 200000.00 | 355000.00 | 355000.00 | 200000.00 | SUN POWER CONVERSION PVT LTD
4.00 | Supplying and making Removal of end terminations along with brass gland and aluminium lugs for following size (3.5C X 240 sq.mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 2.00 | Set |  | 300.00 | 600.00 | 5000.00 | 10000.00 | 500.00 | 1000.00 | 600.00 | surbhi association
5.00 | Laying Rerouting (Retreiving and Re-laying) of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size (3.5C X 240 sq.mm) in the existing masonry open duct as required. (From Existing CCR Panels to UPS I/P panel) Above 185 sq. mm and upto 400sq. mm | 15.00 | Metre |  | 150.00 | 2250.00 | 500.00 | 7500.00 | 125.00 | 1875.00 | 1875.00 | Awasthi Electric Works
6.00 | Supplying and making end terminations with brass gland and aluminium lugs for following size (3.5C X 240 sq.mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 2.00 | Set |  | 1200.00 | 2400.00 | 2950.00 | 5900.00 | 1150.00 | 2300.00 | 2300.00 | Awasthi Electric Works
7.00 | Supply of XLPE/PVC insualated PVC sheathed, armoured alluminium conductor power cable of 1.1kV grade of 3.5C X 185 sq.mm cable size etc., as per IS 7098 Part - 1 1988 with uptodate ammendments etc complete as required. (i) 3.5C x 185 Sq. mm | 75.00 | Metre |  | 950.00 | 71250.00 | 750.00 | 56250.00 | 845.00 | 63375.00 | 56250.00 | SUN POWER CONVERSION PVT LTD
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size (3.5C X 185 sq.mm) on cable tray as required. Above 95 sq. mm and upto 185 sq.mm (clamped with 25/40 x 3mm MS flat clamp) | 45.00 | Metre |  | 120.00 | 5400.00 | 125.00 | 5625.00 | 195.00 | 8775.00 | 5400.00 | surbhi association
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 95 sq. mm and upto 185 sq. mm | 18.00 | Metre |  | 80.00 | 1440.00 | 300.00 | 5400.00 | 90.00 | 1620.00 | 1440.00 | surbhi association
10.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size (3.5C X 185 sq. mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 6.00 | Set |  | 1000.00 | 6000.00 | 3000.00 | 18000.00 | 975.00 | 5850.00 | 5850.00 | Awasthi Electric Works
11.00 | Supply of 1 Core, 95 Sq.mm ,1.1 KV grade, PVC insulated, unsheathed, Un-armoured, FRLS, Copper conductor power cable confirms to IS 694:1990 with up to date amendments etc. Complete as required. | 340.00 | Metre |  | 1300.00 | 442000.00 | 900.00 | 306000.00 | 955.00 | 324700.00 | 306000.00 | SUN POWER CONVERSION PVT LTD
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (b) Above 35 sq. mm and upto 95 sq.mm (clamped with 25 x 3mm MS flat clamp) | 276.00 | Metre |  | 50.00 | 13800.00 | 125.00 | 34500.00 | 130.00 | 35880.00 | 13800.00 | surbhi association
13.00 | Supplying and making end termination with PVC gland and Copper lugs for following size (1 C X 95 sq.mm) of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 kV grade as required. | 16.00 | Set |  | 250.00 | 4000.00 | 375.00 | 6000.00 | 650.00 | 10400.00 | 4000.00 | surbhi association
14.00 | Supply of following size XLPE insulated and PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to relevant IS 7098 (Part-1) with upto date amendments. (i) 3.5C x 25 Sq. mm | 30.00 | Metre |  | 200.00 | 6000.00 | 150.00 | 4500.00 | 185.00 | 5550.00 | 4500.00 | SUN POWER CONVERSION PVT LTD
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 16.00 | Metre |  | 25.00 | 400.00 | 250.00 | 4000.00 | 50.00 | 800.00 | 400.00 | surbhi association
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (i)Upto 35 sq.mm | 12.00 | Metre |  | 20.00 | 240.00 | 250.00 | 3000.00 | 30.00 | 360.00 | 240.00 | surbhi association
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium/copper conductor cable of 1.1 kV grade as required. 3.5C X 25 sq. mm | 2.00 | Set |  | 300.00 | 600.00 | 1000.00 | 2000.00 | 350.00 | 700.00 | 600.00 | surbhi association
18.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 16500.00 | 33000.00 | 17500.00 | 35000.00 | 16000.00 | 32000.00 | 32000.00 | Awasthi Electric Works
19.00 | Providing and fixing 25 mm X 5 mm Copper strip on surface / Cable tray or in recess for connections etc. as required. | 130.00 | Metre |  | 1200.00 | 156000.00 | 1400.00 | 182000.00 | 1175.00 | 152750.00 | 152750.00 | Awasthi Electric Works
20.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 12.00 | Metre |  | 1500.00 | 18000.00 | 1800.00 | 21600.00 | 1450.00 | 17400.00 | 17400.00 | Awasthi Electric Works
21.00 | Earthing with G.I earth pipe 4.5 metre long, 40mm dia, including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 7500.00 | 30000.00 | 10000.00 | 40000.00 | 9000.00 | 36000.00 | 30000.00 | surbhi association
22.00 | Providing and fixing 25 mm X 6 mm G.I strip on surface/ Cable tray or in recess for connections etc. as required. | 160.00 | Metre |  | 180.00 | 28800.00 | 300.00 | 48000.00 | 155.00 | 24800.00 | 24800.00 | Awasthi Electric Works
23.00 | Providing and fixing 25 mm X 6 mm G.I strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I nut, bolt, spring, washer excavation and re-filling etc. as required. | 24.00 | Metre |  | 650.00 | 15600.00 | 850.00 | 20400.00 | 650.00 | 15600.00 | 15600.00 | surbhi association, Awasthi Electric Works
24.00 | Demolishing cement concrete manually / by mechanical means including disposal of material within 50 meters lead as per direction of Engineer-in-charge. – Nominal concrete 1:1.5:3 or richer mix (i/c equivalent design mix) | 30.00 | Cum |  | 1500.00 | 45000.00 | 5000.00 | 150000.00 | 600.00 | 18000.00 | 18000.00 | Awasthi Electric Works
25.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket , bend , Couplers etc consfirming to IS 14930 , Part - II complete with fitting and cutting , jointing etc in existing trench, complete as required - 200 mm dia (OD- 200 mm & ID 175 mm nominal) | 350.00 | Metre |  | 300.00 | 105000.00 | 300.00 | 105000.00 | 425.00 | 148750.00 | 105000.00 | SUN POWER CONVERSION PVT LTD, surbhi association
26.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays bends with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 375 mm width X 50 mm depth X 2.0 mm thickness | 39.00 | Metre |  | 1800.00 | 70200.00 | 1500.00 | 58500.00 | 1050.00 | 40950.00 | 40950.00 | Awasthi Electric Works
27.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays bends with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 375 mm width X 50 mm depth X 2.0 mm thickness | 7.00 | Nos |  | 2000.00 | 14000.00 | 1250.00 | 8750.00 | 2200.00 | 15400.00 | 8750.00 | SUN POWER CONVERSION PVT LTD
28.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays TEE with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 375 mm width X 50 mm depth X 2.0 mm thickness | 6.00 | Nos |  | 2000.00 | 12000.00 | 1250.00 | 7500.00 | 2450.00 | 14700.00 | 7500.00 | SUN POWER CONVERSION PVT LTD
29.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays Reducer with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 375 mm width X 50 mm depth X 2.0 mm thickness | 1.00 | Nos |  | 2000.00 | 2000.00 | 1250.00 | 1250.00 | 1650.00 | 1650.00 | 1250.00 | SUN POWER CONVERSION PVT LTD
30.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 200 mm width X 50 mm depth X 1.6 mm thickness | 18.00 | Metre |  | 1000.00 | 18000.00 | 800.00 | 14400.00 | 550.00 | 9900.00 | 9900.00 | Awasthi Electric Works
31.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays bends with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 200 mm width X 50 mm depth X 1.6 mm thickness | 3.00 | Nos |  | 1500.00 | 4500.00 | 875.00 | 2625.00 | 1050.00 | 3150.00 | 2625.00 | SUN POWER CONVERSION PVT LTD
32.00 | Supplying and installing following size of perforated, painted with powder coating M.S. cable trays TEE with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders supported on wall with 50 X 50 X 5 mm L angle brackets, Including bolts & nuts, painting of L angle brackets, fasteners for anchoring support on wall etc., as required. 200 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Nos |  | 1500.00 | 3000.00 | 1000.00 | 2000.00 | 1190.00 | 2380.00 | 2000.00 | SUN POWER CONVERSION PVT LTD
33.00 | Supply of following size 5KV grade Airfield lighting cables with stranded annealed plain copper conductor un-armoured, un-screened PVC insulated and PVC sheathed cable etc. complete as required (a) 2 C X 6 sqmm | 360.00 | Metre |  | 220.00 | 79200.00 | 450.00 | 162000.00 | 285.00 | 102600.00 | 79200.00 | surbhi association
34.00 | Supply of following size 5KV grade Airfield lighting cables with stranded annealed plain copper conductor un-armoured, un-screened PVC insulated and PVC sheathed cable etc. complete as required (a) 1 C X 16 sqmm | 700.00 | Metre |  | 120.00 | 84000.00 | 825.00 | 577500.00 | 245.00 | 171500.00 | 84000.00 | surbhi association
35.00 | Supply of following size 5KV grade dry type plug and receptacle of Type - I class B Primary connector kit suitable for the following Size of Field attchments with 5 KV Grade PVC insulated PVC sheathed copper conductor cable confirming to relevant IS specification etc., complete as required. (a) 6 sqmm | 10.00 | Kits |  | 650.00 | 6500.00 | 3500.00 | 35000.00 | 1590.00 | 15900.00 | 6500.00 | surbhi association
36.00 | Supply of following size 5KV grade dry type plug and receptacle of Type - I class B Primary connector kit suitable for the following Size of Field attchments with 5 KV Grade PVC insulated PVC sheathed copper conductor cable confirming to relevant IS specification etc., complete as required. (b) 16 sqmm | 10.00 | Kits |  | 650.00 | 6500.00 | 4500.00 | 45000.00 | 1690.00 | 16900.00 | 6500.00 | surbhi association
37.00 | Making field connections by crimping of following sizes Plug & Receptable connectors with suitable existing size single core PVC / XLPE copper condutor cable of 5kv grade airfield cables including filling the gap with water sealant material applying HT insulation tape over which PVC tape etc as required. (a) 6 sqmm | 10.00 | Job |  | 100.00 | 1000.00 | 1500.00 | 15000.00 | 2500.00 | 25000.00 | 1000.00 | surbhi association
38.00 | Making field connections by crimping of following sizes Plug & Receptable connectors with suitable existing size single core PVC / XLPE copper condutor cable of 5kv grade airfield cables including filling the gap with water sealant material applying HT insulation tape over which PVC tape etc as required. (a) 16 sqmm | 10.00 | Job |  | 100.00 | 1000.00 | 1500.00 | 15000.00 | 2500.00 | 25000.00 | 1000.00 | surbhi association
39.00 | Construction of Chambers of inside size 1.2 mtrs X 1.2 Mtrs X 1.5 mtrs in brick work in CM 1: 4 (1 cement: 4 Coarse sand) for Cables along with cover, I/c necessary excavation, foundation concrete 1:3:6 and inside plastering with cement mortar 1:3, 12mm thick, finished with floating coat of neat cement as per standard design & providing 8 thick Chequer plate with stiffeners, lifting arrangement, angle iron edge, angle frame work etc, complete with providing anticorrosive paint on both sides. Cover size 1.2 mtrs x 1.2 mtrs. in all types of soil. | 3.00 | JOB |  | 15000.00 | 45000.00 | 65000.00 | 195000.00 | 25000.00 | 75000.00 | 45000.00 | surbhi association
40.00 | Providing and laying Pavement Quality Concrete (PQC) using 350 Kg of ordinary Portland cement of required grade, fine aggregate, graded stone aggregates of 40 mm nominal size in appropriate proportion as per specification and job mix formula, laid in panels using Slip form paver/Fixed form paver/Manual method including making necessary provision for expansion joint, curing, etc. complete as per site requirement . The item for execution shall also include the following operations (a) Mechanically vibrated by using needle and surface vibrators, including steel form work with sturdy M.S channels / sections including curing. | 21.00 | Cum |  | 8000.00 | 168000.00 | 4000.00 | 84000.00 | 9500.00 | 199500.00 | 84000.00 | SUN POWER CONVERSION PVT LTD
| Total in Figures |  |  |  |  | 6152680.00 |  | 5994200.00 |  | 5773015.00
Lowest Amount Quoted BY: Awasthi Electric Works(5773015.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of Power supply to GLF by Provision of UPS Tender ID: 2023_AAI_176152_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 5773015.00 | L1
| 2 | SUN POWER CONVERSION PVT LTD | 5994200.00 | L2
| 3 | surbhi association | 6152680.00 | L3