## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 04-Jan-2024 12:21 PM Tender Title: Re Configuration of NITB Bhopal Airport. SH. Fire Alarm System and Fire Fighting System works. Tender ID: 2023_AAI_176200_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Re-Configuration of NITB Bhopal Airport. SH: Fire Alarm System & Fire Fighting works.
Contract No: AAI/BPL/ENGG(E)/NIT-10/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | FIRE PROTECTION SYSTEM(GSTN-23ADAPC9892R1ZY) |  | BA-PAN ENGINEERING co.(GSTN-07AYDPS2409Q1ZX) |  | M/S JAYSHWAL ENTERPRISES(GSTN-24AEFPC8401C1Z9) |  | PYROGUARD ENGINEERS PRIVATE LIMITED(GSTN-07AACCP9466E1Z7) |  | A K TECHNOCRATS(GSTN-NA) |  | J.K.DEFENCE FIRE ENGG. SERVICES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Networkable (upto 4kms) Microprocessor based intelligent analog Addressable Type Fire Alarm Control Panel of 4 loop, with minimum 320 character graphics / LCD / LED display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM) ,The panel should be equipped with loop capacity to take minimum 240 intelligent addressable detectors/ devices (In any combination ) in one loop. Four access levels, capable of taking Protocol Devices, Graphical Display, sufficient number of programmable relay controls for controlling pressurization fans, ventilation fans, fire pump room, monitoring of fire sprinkler and fire hydrant pump etc, suitable for operation at 230 volts, 50 Hz AC power supply including automatic battery charger, 24 volts sealed maintenance free /Li-ion lead acid batteries sufficient for 24 hours normal working and shall be capable of operating the system for 30 minutes during an emergency / fault conditions in addition as required. The panel shall be UL/EN listed (Latest Version) and shall be compatible to interface with PA system. (For Giving trigger Signal to Start pre-recorded Digital Voice Evacuation from PA system in case of fire). The panel shall have either ann in-built or external printer as per specifications. It shall have interfacing connectivity (BACNET/ MODBUS/ Open protocol gateway) for Building Management System complete as required. | 1.00 | Each |  | 290000.00 | 290000.00 | 284000.00 | 284000.00 | 248400.00 | 248400.00 | 65560.00 | 65560.00 | 47700.00 | 47700.00 | 500000.00 | 500000.00 | 47700.00 | A K TECHNOCRATS
2.00 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) Repeater Panel shall provide pin point location of the fault or fire event and should Provide complete control of system at remote location. The panel shall have a 320 character graphics / LCD display / HMI display with touch screen or other keypad. | 1.00 | Each |  | 74000.00 | 74000.00 | 103000.00 | 103000.00 | 108600.00 | 108600.00 | 40250.00 | 40250.00 | 20000.00 | 20000.00 | 175000.00 | 175000.00 | 20000.00 | A K TECHNOCRATS
3.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable smoke detector with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling, roof and concealed space and as per enclosed specifications complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) | 380.00 | Each |  | 2730.00 | 1037400.00 | 2740.00 | 1041200.00 | 2760.00 | 1048800.00 | 3795.00 | 1442100.00 | 3450.00 | 1311000.00 | 3000.00 | 1140000.00 | 1037400.00 | FIRE PROTECTION SYSTEM
4.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable multi criteria detector {Smoke + heat} with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling, roof and concealed space and as per enclosed specifications complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) | 380.00 | Each |  | 2840.00 | 1079200.00 | 2740.00 | 1041200.00 | 3000.00 | 1140000.00 | 4020.00 | 1527600.00 | 3650.00 | 1387000.00 | 3500.00 | 1330000.00 | 1041200.00 | BA-PAN ENGINEERING co.
5.00 | Supply, installation, testing and commissioning of UL/EN listed (latest version) Intelligent addressable Control Module/ Relay Module (output module) with inbuilt fault isolator or isolator module for tripping of AHU & Ventilation / pressurisation fans / hooter complete with termination etc. complete as required and as per enclosed specifications. | 8.00 | Each |  | 3215.00 | 25720.00 | 4000.00 | 32000.00 | 3840.00 | 30720.00 | 2860.00 | 22880.00 | 2000.00 | 16000.00 | 4000.00 | 32000.00 | 16000.00 | A K TECHNOCRATS
6.00 | Supply, installation, testing and commissioning of Response Indicator for getting fire indications of detectors i/c mounting boxes installed above/below false ceiling area interconnecting to loop cable complete as required. | 380.00 | Each |  | 100.00 | 38000.00 | 320.00 | 121600.00 | 1020.00 | 387600.00 | 100.00 | 38000.00 | 170.00 | 64600.00 | 450.00 | 171000.00 | 38000.00 | FIRE PROTECTION SYSTEM, PYROGUARD ENGINEERS PRIVATE LIMITED
7.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable Manual call station (Resettable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or polycarbonate equivalent) with clear operating instruction and the word "FIRE" appearing on the front complete with connections etc. as required and as per enclosed specifications. | 15.00 | Each |  | 3620.00 | 54300.00 | 4000.00 | 60000.00 | 4380.00 | 65700.00 | 7350.00 | 110250.00 | 2000.00 | 30000.00 | 5000.00 | 75000.00 | 30000.00 | A K TECHNOCRATS
8.00 | Supply, installation, testing and commissioning of UL / EN listed (latest version) loop powered addressable Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 8.00 | Each |  | 5065.00 | 40520.00 | 8000.00 | 64000.00 | 6300.00 | 50400.00 | 9100.00 | 72800.00 | 2500.00 | 20000.00 | 3500.00 | 28000.00 | 20000.00 | A K TECHNOCRATS
9.00 | Supplying, Installing, Testing and Commissioning of UL / EN listed (Latest Version) Addressable motorised auto align Beam detector with transmitter, receiver & control panel as per specification, complete as required. | 2.00 | Each |  | 70000.00 | 140000.00 | 71000.00 | 142000.00 | 90000.00 | 180000.00 | 65210.00 | 130420.00 | 15000.00 | 30000.00 | 150000.00 | 300000.00 | 30000.00 | A K TECHNOCRATS
10.00 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | 2000.00 | Meter |  | 190.00 | 380000.00 | 202.00 | 404000.00 | 90.00 | 180000.00 | 180.00 | 360000.00 | 130.00 | 260000.00 | 130.00 | 260000.00 | 180000.00 | M/S JAYSHWAL ENTERPRISES
11.00 | Supplying & fixing Internal and External SS single headed fire hydrant landing valve with instantaneous Gun metal coupling of 63mm dia with cast iron wheel ISI marked conforming to IS:5290 (Type-A) with blank Gunmetal/ Stainless steel cap and chain as required. | 5.00 | Each |  | 6840.00 | 34200.00 | 5900.00 | 29500.00 | 4800.00 | 24000.00 | 6090.00 | 30450.00 | 7000.00 | 35000.00 | 7500.00 | 37500.00 | 24000.00 | M/S JAYSHWAL ENTERPRISES
12.00 | Providing & fixing 63 mm dia SS short Branch pipe with 20mm (nominal internal diameter) in size stainless steel nozzle conforming to IS:903 suitable for instantaneous connection complete to inter-connect hose pipe, coupling etc. as required and as per tender specification. | 5.00 | Each |  | 2700.00 | 13500.00 | 2200.00 | 11000.00 | 2200.00 | 11000.00 | 2140.00 | 10700.00 | 3500.00 | 17500.00 | 2500.00 | 12500.00 | 10700.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
13.00 | Providing & fixing 63mm dia., 15mtr. long RRL hose pipe with 63mm dia. male and female gun metal couplings duly binded with GI wire, rivets etc. conforming to IS- 636 (Type-A) complete as required & as per tender specification. | 10.00 | Each |  | 6300.00 | 63000.00 | 4500.00 | 45000.00 | 4650.00 | 46500.00 | 4830.00 | 48300.00 | 6000.00 | 60000.00 | 4500.00 | 45000.00 | 45000.00 | J.K.DEFENCE FIRE ENGG. SERVICES, BA-PAN ENGINEERING co.
14.00 | Providing and fixing First - Aid Hose Reel 20mm dia. x 30m long (minimum length) (Thermo plastic Type as per I.S. 12585) complete with drum, bracket, 25mm dia. shut-off valve and 5mm Gun-Metal nozzle conforming to IS-:884, connection with riser with MS C- class pipe, painting the MS works complete as required & as per tender specification. | 5.00 | Each |  | 6840.00 | 34200.00 | 8000.00 | 40000.00 | 6200.00 | 31000.00 | 7630.00 | 38150.00 | 7500.00 | 37500.00 | 8500.00 | 42500.00 | 31000.00 | M/S JAYSHWAL ENTERPRISES
15.00 | Providing and fixing Fire hose cabinet made of angle iron (40mmx40mmx5mm) door frame and S.S. sheet (2mm thick) cum glass shutter of size 2.1mtrx0.9mtr with 25mmx25mmx3mm angle frame all around and stiffened in between i/c hinges, handle, locking arrangement, painting with approved synthetic enamel paint i/c sign writing on glass at internal hydrant including providing & fixing S.S. sheet 2mm thick on remaining portion above door to close opening i/c painting etc. as required. Glass shall be 6 mm thick. | 5.00 | Each |  | 7600.00 | 38000.00 | 22000.00 | 110000.00 | 2850.00 | 14250.00 | 25000.00 | 125000.00 | 9000.00 | 45000.00 | 6500.00 | 32500.00 | 14250.00 | M/S JAYSHWAL ENTERPRISES
16.00 | Supplying and fixing orifice plate made of 6 mm. thick stainless steel (Grade 304) with orifice of required size to be fitted between flange & landing valve of external and internal hydrant to reduce pressure to working pressure of 3.5 kg/cm2 complete as required & as per tender specification. | 5.00 | Each |  | 760.00 | 3800.00 | 1400.00 | 7000.00 | 1500.00 | 7500.00 | 2000.00 | 10000.00 | 3500.00 | 17500.00 | 1250.00 | 6250.00 | 3800.00 | FIRE PROTECTION SYSTEM
17.00 | Providing, fixing, jointing and commissioning of following sizes of C- class heavy duty Mild Steel pipes conforming to IS-1239/ IS-3589, including cutting, welding, nut-bolts, gasket, fitting viz. bends, tees, reducers, crosses, flanges etc. and fixing the pipes on wall / ceiling / beam / floor with suitable MS clamps / structural supports/PCC block and painting complete as required and as per tender specification.
17.01 | 150 mm dia. | 500.00 | Meter |  | 2340.00 | 1170000.00 | 2002.00 | 1001000.00 | 2200.00 | 1100000.00 | 2800.00 | 1400000.00 | 2400.00 | 1200000.00 | 2350.00 | 1175000.00 | 1001000.00 | BA-PAN ENGINEERING co.
17.02 | 100 mm dia | 100.00 | Meter |  | 1565.00 | 156500.00 | 1300.00 | 130000.00 | 1520.00 | 152000.00 | 1930.00 | 193000.00 | 1650.00 | 165000.00 | 1200.00 | 120000.00 | 120000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
17.03 | 80 mm dia. | 50.00 | Meter |  | 1110.00 | 55500.00 | 1102.00 | 55100.00 | 1100.00 | 55000.00 | 1410.00 | 70500.00 | 1300.00 | 65000.00 | 1100.00 | 55000.00 | 55000.00 | J.K.DEFENCE FIRE ENGG. SERVICES, M/S JAYSHWAL ENTERPRISES
17.04 | 65 mm dia. | 70.00 | Meter |  | 890.00 | 62300.00 | 1004.00 | 70280.00 | 895.00 | 62650.00 | 1175.00 | 82250.00 | 1050.00 | 73500.00 | 1000.00 | 70000.00 | 62300.00 | FIRE PROTECTION SYSTEM
17.05 | 50mm dia. | 50.00 | Meter |  | 670.00 | 33500.00 | 800.00 | 40000.00 | 710.00 | 35500.00 | 960.00 | 48000.00 | 811.00 | 40550.00 | 800.00 | 40000.00 | 33500.00 | FIRE PROTECTION SYSTEM
17.06 | 40 mm dia. | 200.00 | Meter |  | 460.00 | 92000.00 | 540.00 | 108000.00 | 540.00 | 108000.00 | 740.00 | 148000.00 | 555.00 | 111000.00 | 650.00 | 130000.00 | 92000.00 | FIRE PROTECTION SYSTEM
17.07 | 32 mm dia. | 50.00 | Meter |  | 410.00 | 20500.00 | 500.00 | 25000.00 | 480.00 | 24000.00 | 650.00 | 32500.00 | 505.00 | 25250.00 | 600.00 | 30000.00 | 20500.00 | FIRE PROTECTION SYSTEM
17.08 | 25 mm dia. | 500.00 | Meter |  | 340.00 | 170000.00 | 450.00 | 225000.00 | 395.00 | 197500.00 | 550.00 | 275000.00 | 375.00 | 187500.00 | 550.00 | 275000.00 | 170000.00 | FIRE PROTECTION SYSTEM
18.00 | Providing, fixing, testing and commissioning of following sizes of butterfly valve of rating PN 16, wafer type, in cast iron body with Ductile Iron disc, EPDM seal, SS single piece shaft, conforming to IS-13095 of the following sizes complete with cast iron hand lever companion flanges, bolts, nuts, washers & inserted rubber gaskets, as required and as per tender specification.
18.01 | 150mm dia. | 7.00 | Each |  | 31000.00 | 217000.00 | 8000.00 | 56000.00 | 5800.00 | 40600.00 | 6760.00 | 47320.00 | 4500.00 | 31500.00 | 5500.00 | 38500.00 | 31500.00 | A K TECHNOCRATS
18.02 | 100mm dia. | 2.00 | Each |  | 16000.00 | 32000.00 | 6454.00 | 12908.00 | 4800.00 | 9600.00 | 4340.00 | 8680.00 | 3500.00 | 7000.00 | 4000.00 | 8000.00 | 7000.00 | A K TECHNOCRATS
18.03 | 80mm dia. | 5.00 | Each |  | 5700.00 | 28500.00 | 4100.00 | 20500.00 | 3800.00 | 19000.00 | 3280.00 | 16400.00 | 2500.00 | 12500.00 | 3000.00 | 15000.00 | 12500.00 | A K TECHNOCRATS
19.00 | Providing & fixing gunmetal gate valve with PN 16 rating with nut, bolts & washers, painting etc complete as required as per tender specifications. a) 25 mm nominal bore | 5.00 | Each |  | 610.00 | 3050.00 | 2200.00 | 11000.00 | 2200.00 | 11000.00 | 1410.00 | 7050.00 | 3500.00 | 17500.00 | 2950.00 | 14750.00 | 3050.00 | FIRE PROTECTION SYSTEM
20.00 | Providing and fixing following size Pressure gauge (0-15 Kg/Cm2) complete with shut off valve duly calibrated before installation complete as required & as per tender specification. 150mm dia. | 5.00 | Each |  | 1440.00 | 7200.00 | 2200.00 | 11000.00 | 1500.00 | 7500.00 | 1500.00 | 7500.00 | 2000.00 | 10000.00 | 1950.00 | 9750.00 | 7200.00 | FIRE PROTECTION SYSTEM
21.00 | Providing & fixing of 15 mm dia. sprinkler head with standard response Quartzoid Bulb operate at 68 degree C complete with all accessories as required and as per tender specification (UL Listed) Pendent type in chrome finish (Standard Coverage) | 380.00 | Each |  | 245.00 | 93100.00 | 500.00 | 190000.00 | 300.00 | 114000.00 | 395.00 | 150100.00 | 215.00 | 81700.00 | 300.00 | 114000.00 | 81700.00 | A K TECHNOCRATS
22.00 | Providing & fixing of 15 mm dia. sprinkler head with standard response Quartzoid Bulb operate at 68 degree C complete with all accessories as required and as per tender specification (UL Listed) Upright type in chrome finish (Standard Coverage) | 380.00 | Each |  | 260.00 | 98800.00 | 500.00 | 190000.00 | 300.00 | 114000.00 | 395.00 | 150100.00 | 215.00 | 81700.00 | 350.00 | 133000.00 | 81700.00 | A K TECHNOCRATS
23.00 | Providing & fixing flexible tubes in corrugated SS, for connecting pendant sprinklers to branch lines complete with all necessary accessories, reducers, O-rings, nipples etc., supporting structural arrangements in the false ceiling/slab as per site requirement for the below lengths and tested for min 15 Kg/Sq.cm pressure with G.I. retainer rings & guide bolts complete as required and as per tender specification (UL Listed) For 1000 mm length | 380.00 | Each |  | 1200.00 | 456000.00 | 1300.00 | 494000.00 | 1050.00 | 399000.00 | 1450.00 | 551000.00 | 955.00 | 362900.00 | 1200.00 | 456000.00 | 362900.00 | A K TECHNOCRATS
24.00 | Providing and fixing 25mm dia inspecting & testing assembly with S.S. isolation valve, S.S. sight glass bypass valve & connected to line drain complete in all respect as per standard practice of code including pressure gauges of approved make. | 5.00 | Each |  | 1200.00 | 6000.00 | 2200.00 | 11000.00 | 1050.00 | 5250.00 | 4500.00 | 22500.00 | 3000.00 | 15000.00 | 5500.00 | 27500.00 | 5250.00 | M/S JAYSHWAL ENTERPRISES
25.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and wall suspension bracket as required as per tender specifications. | 8.00 | Each |  | 5600.00 | 44800.00 | 8000.00 | 64000.00 | 5100.00 | 40800.00 | 5875.00 | 47000.00 | 5500.00 | 44000.00 | 6500.00 | 52000.00 | 40800.00 | M/S JAYSHWAL ENTERPRISES
26.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) portable fire extinguisher, water (gas pressure) type capacity 9 kg with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets as required as per tender specifications. | 8.00 | Each |  | 2800.00 | 22400.00 | 2200.00 | 17600.00 | 4500.00 | 36000.00 | 2875.00 | 23000.00 | 4000.00 | 32000.00 | 2500.00 | 20000.00 | 17600.00 | BA-PAN ENGINEERING co.
27.00 | Supply, installation, testing and commissioning of 6kg ABC (Powder Type) Fire Extinguisher. Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and conforming to IS:15683 as required as per tender specifications. | 8.00 | Each |  | 2200.00 | 17600.00 | 2200.00 | 17600.00 | 1850.00 | 14800.00 | 2750.00 | 22000.00 | 4500.00 | 36000.00 | 2350.00 | 18800.00 | 14800.00 | M/S JAYSHWAL ENTERPRISES
28.00 | Providing detailed design as per site requirement including submission of GFC drawing including detailed layout of FHC, pendent & upright sprinkler and smoke / heat detector as per CPWD Specification for Wet riser & Sprinkler system 2006 with upto date ammendment, Fire alarm & detection system 2018 and NBC 2016 (Fire & Life safety) etc. complete in all respects for Lower Ground Floor. | 1.00 | Job |  | 13000.00 | 13000.00 | 4000.00 | 4000.00 | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 711.00 | 711.00 | 100000.00 | 100000.00 | 711.00 | A K TECHNOCRATS
| Total in Figures |  |  |  |  | 6145590.00 |  | 6289488.00 |  | 6170670.00 |  | 7424360.00 |  | 5999111.00 |  | 7089550.00
Lowest Amount Quoted BY: A K TECHNOCRATS(5999111.00)

## BOQ Summary
BOQ Summary Details Tender Title: Re Configuration of NITB Bhopal Airport. SH. Fire Alarm System and Fire Fighting System works. Tender ID: 2023_AAI_176200_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | A K TECHNOCRATS | 5999111.00 | L1
| 2 | FIRE PROTECTION SYSTEM | 6145590.00 | L2
| 3 | M/S JAYSHWAL ENTERPRISES | 6170670.00 | L3
| 4 | BA-PAN ENGINEERING co. | 6289488.00 | L4
| 5 | J.K.DEFENCE FIRE ENGG. SERVICES | 7089550.00 | L5
| 6 | PYROGUARD ENGINEERS PRIVATE LIMITED | 7424360.00 | L6