## BoQ1
Government eProcurement System Created By: Jose K Paul Created Date/Time: 05-Jan-2024 03:42 PM Tender Title: Replacement of filter press for existing 200KLD STP at Madurai Airport Tender ID: 2023_AAI_177006_2
Tender Inviting Authority: Airports Authority of India, Madurai Airport, Madurai -625 022.
Name of Work: Replacement of filter press for existing 200KLD STP at Madurai Airport
Contract No: 2023_AAI_177006_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Enviro Chem Engineers and Consultants India Pvt Ltd(GSTN-33AADCE8901A1Z8) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, fixing, testing & commissioning of centrifugal fully submersible, non clog sewage handling type pump with cutter fan arrangement at suction to agitate the liquid for raw sewage transfer from Sludge digester cum thickner tank to proposed over head tank or to sludge dry beds. The pump shall have bronze impeller, high grade stainless steel shaft, cast iron seal cover, pump casing cast iron/NICI, TEFC induction motor suitable for 400/440 volts, 3 phase, 50HZ AC supply, suction & delivery pipes, lifting arrangment, power cables from starter panel to pump, reducer, tee, pipe nipple, couplings,gasket, DOL starter and other associted accessories etc. complete as required as per technical specifications and site requirements. The pump shall be compatable with the exisitng 200KLD STP installed at Madurai Airport. Solid handling shall be 20-50mm. Capacity 12 m³ / hr @ 14 m head. | 1.00 | Job |  | 54900.00 | 54900.00 | 89999.00 | 89999.00 | 54900.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
2.00 | Servicing & overhauling of PP plate CI base frame filter press including replacement of filter cloth, effluent water tray, sludge disposal tray and other associated accessories to make the filter press completely functional as per TNPCB requirements. Cloth Size:500 x 500 Tray size: 1400 x 600 | 1.00 | Job |  | 42700.00 | 42700.00 | 55999.00 | 55999.00 | 42700.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
3.00 | Servicing and overhauling of Twin lobe positive displacement type, rotary air blowers with V-belt drive, belt guard, base plate, inlet filter-silencer, flexible connectors, control valves, pressure gauge and piping etc. including supply of necessary spares as per site requirement to make the blower function ascending to manufacture reccommendation. | 2.00 | Job |  | 21960.00 | 43920.00 | 25999.00 | 51998.00 | 43920.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
4.00 | Supply of 5 inch MS pipe (Class C) for interconnecting the pipe lines at existing 200KLD STP etc. as required. | 18.00 | Mtr |  | 1944.00 | 34992.00 | 1199.00 | 21582.00 | 21582.00 | CHENNAI ENGINEERING SERVICES
5.00 | Excavation up to 50 cm and laying of 5 inch MS pipe (Class C) along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specifications and site requirement. | 10.00 | Mtr |  | 854.00 | 8540.00 | 699.00 | 6990.00 | 6990.00 | CHENNAI ENGINEERING SERVICES
6.00 | Laying of 5 inch MS pipe (Class C) on wall surface/above ground with MS supports/clamps along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specifications and site requirement. | 6.00 | Mtr |  | 732.00 | 4392.00 | 599.00 | 3594.00 | 3594.00 | CHENNAI ENGINEERING SERVICES
7.00 | Supply of 3 inch MS pipe (Class C) for interconnecting the pipe lines at existing 200KLD STP etc. as required. | 13.00 | Mtr |  | 1037.00 | 13481.00 | 659.00 | 8567.00 | 8567.00 | CHENNAI ENGINEERING SERVICES
8.00 | Excavation up to 50 cm and laying of 3 inch MS pipe (Class C) along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specifications and site requirement. | 7.00 | Mtr |  | 671.00 | 4697.00 | 399.00 | 2793.00 | 2793.00 | CHENNAI ENGINEERING SERVICES
9.00 | Laying of 3 inch MS pipe (Class C) on wall surface/above ground with MS supports/clamps along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per site requirement. | 4.00 | Mtr |  | 610.00 | 2440.00 | 399.00 | 1596.00 | 1596.00 | CHENNAI ENGINEERING SERVICES
10.00 | Supply of 2.5 inch MS pipe (Class C) for interconnecting the pipe lines at existing 200KLD STP etc. as required. | 14.00 | Mtr |  | 976.00 | 13664.00 | 599.00 | 8386.00 | 8386.00 | CHENNAI ENGINEERING SERVICES
11.00 | Excavation up to 50 cm and laying of 2.5 inch MS pipe (Class C) along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specifications and site requirement. | 9.00 | Mtr |  | 671.00 | 6039.00 | 399.00 | 3591.00 | 3591.00 | CHENNAI ENGINEERING SERVICES
12.00 | Laying of 2.5 inch MS pipe (Class C) on wall surface/above ground with MS supports/clamps along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specifications and site requirement. | 3.00 | Mtr |  | 586.00 | 1758.00 | 399.00 | 1197.00 | 1197.00 | CHENNAI ENGINEERING SERVICES
13.00 | SITC of 1000 ltr capacity water tank (chemical grade) made of PP/HDPE material along with suitable accessories like tank nipple, elbow, tee, H nipple, pipe nipple, brass ball valve, coupling, reducer, bend etc. as per site requirement. | 1.00 | Job |  | 14640.00 | 14640.00 | 15999.00 | 15999.00 | 14640.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
14.00 | Providing MS Stand for the 1000 ltr capacity water tank of MS angle minimum size 25mm X 5mm upto a height not less than 1.5m as per technical specifications and site requirement. | 1.00 | Job |  | 18300.00 | 18300.00 | 10999.00 | 10999.00 | 10999.00 | CHENNAI ENGINEERING SERVICES
15.00 | Repairing, overhauling, shifting & reinstallation of horizontal, helical progressive cavity pump for the disposal of sludge from over head tank to feed the filter press with positive suction. The pump is with Cl casing, SS shaft & sleeve with shaft seal connected by a V-belt drive to TEFC induction motor suitable for 400/440 volts, 3 phase, 50 Hz AC supply. The job includes shifting & reinstallation of structural base plate, providing suitable foundation and suitable vibration pads, repairing shaft, replacing bearing, seals, coupling and other associted accessories etc. complete as required as per technical specifications and site requirement. Solid handling shall be 20-50mm. Capacity 1 m³/hr | 1.00 | Job |  | 48800.00 | 48800.00 | 5099.00 | 5099.00 | 5099.00 | CHENNAI ENGINEERING SERVICES
16.00 | Supply, installing, testing & commissioning of hypochlorite solution dozer comprising of 100 Ltrs. Cap, working pressure 4bar, HDPE (chemical grade) tank with inlet/outlet connection and along with 01 no. metering pump of adjustable capacity for dosing of chlorine solution (each 0-5 LPH) etc. as per technical specifications and site requirement. | 1.00 | Job |  | 12200.00 | 12200.00 | 20999.00 | 20999.00 | 12200.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
17.00 | Repairing & overhauling of vertical self supporting multigrade sand filter fabricated from MS sheet as per IS: 2825 Pressure gauges at inlet and outlet, sample cock, MS class 'C' face piping, Cl butterfly valves and all accessories, including supply & charging of filter media for multigrade sand filter painting outside with two coats of epoxy primer and two or more coats of synthetic enamel paint etc. complete as required as per technical specifications and site requirement. Capacity - 12 m³/hr Filtration rate - 18 m³/m²/hr Maximum operating pressure - 3.5 Kg/sq.cm Test pressure - 7.0 Kg/sq.cm Diameter - 1000 mm | 1.00 | Job |  | 36600.00 | 36600.00 | 65999.00 | 65999.00 | 36600.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
18.00 | Repairing & overhauling of vertical self supporting activated carbon filter (ACF) FRP Pressure gauges at inlet and outlet sample cock, MS class 'C' face piping. Cl butterfly valves and all accessories etc. as required including supply & charging of filter media for activated carbon filter, painting outside with two coats of epoxy primer and outside with two coats of synthetic enamel paint, etc. complete as required as per technical specifications and site requirement. Capacity - 12 m³/hr Filtration rate - 15 m³/m²/hr Maximum operating pressure - 3.5 Kg/sq.cm Test pressure - 7.0 Kg/sq.cm Diameter - 1200 mm | 1.00 | Job |  | 39040.00 | 39040.00 | 70999.00 | 70999.00 | 39040.00 | Enviro Chem Engineers and Consultants India Pvt Ltd
19.00 | Providing and fixing of parallel plate separator of 864 mm(L) X 58 mm (W) X 1mm (thickness) size to match with the exisitng parallel plate separator plates in the existing parallel plate separator tank to increase the effective setting area of sedimentation basis etc. complete as required as per technical specifications and site requirement. | 2.25 | Cum |  | 21960.00 | 49410.00 | 12999.00 | 29247.75 | 29247.75 | CHENNAI ENGINEERING SERVICES
20.00 | Repairing & overhauling of horizontal self priming centrifugal pump to transfer the treated water from tank to gardening areas. The pump is made of heavy duty graded cast iron casing, cast iron impeller, carbon steel shaft, gland packed seal etc and is connected to TEFC induction motor, 400/440 volts, 3 phase, 50HZ AC supply, the job includes replacing of existing cast iron impeller, shaft, bearing, coupling, mounting base frame and other associted accessories etc. complete as required as per technical specifications and site requirements. Capacity 18 m³ / hr @ 35 m head | 1.00 | Job |  | 42700.00 | 42700.00 | 20809.00 | 20809.00 | 20809.00 | CHENNAI ENGINEERING SERVICES
21.00 | Supply, fixing, testing & commissioning of horizontal self priming centrifugal pump, for transfer the treated water from filter feed tank to Multi Sand Filter and Active Carbon Filter. The pump shall made of heavy duty graded cast iron casing, bronze impeller, SS shaft & sleeve, mechanical seal are connected to a TEFC induction motor suitable for 400/440 volts, 3 phase, 50HZ AC supply, suction & delivery pipes, ball valve, reducer, tee, pipe nipple, couplings,gasket, DOL starter, pressure gauge, necessary modifiction of existing foundation and other associted accessories etc. complete as required as per technical specifications and site requirements. Capacity 12 m³ / hr @ 30 m head | 1.00 | Job |  | 36600.00 | 36600.00 | 31499.00 | 31499.00 | 31499.00 | CHENNAI ENGINEERING SERVICES
22.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 Class-125 rating, Cast Iron, duly ISI marked complete with flanges, nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. a) 100mm dia | 5.00 | Job |  | 7076.00 | 35380.00 | 4279.00 | 21395.00 | 21395.00 | CHENNAI ENGINEERING SERVICES
23.00 | Supply of 2 inch MS pipe (Class C) for interconnecting the pipe lines at existing 200KLD STP etc. as required. | 14.00 | Mtr |  | 708.00 | 9912.00 | 399.00 | 5586.00 | 5586.00 | CHENNAI ENGINEERING SERVICES
24.00 | Excavation up to 50 cm and laying of 2 inch MS pipe (Class C) along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specification and site requirement. | 8.00 | Mtr |  | 586.00 | 4688.00 | 239.00 | 1912.00 | 1912.00 | CHENNAI ENGINEERING SERVICES
25.00 | Laying of 2 inch MS pipe (Class C) on wall surface/above ground with MS supports/clamps along with supply of suitable accessories like bend, elbow, reducer, coupler etc. to interconnect the pipe lines at existing 200KLD STP etc. as per technical specification and site requirement. | 4.00 | Mtr |  | 513.00 | 2052.00 | 209.00 | 836.00 | 836.00 | CHENNAI ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 581845.00 |  | 557670.75
Lowest Amount Quoted BY: CHENNAI ENGINEERING SERVICES(557670.75)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of filter press for existing 200KLD STP at Madurai Airport Tender ID: 2023_AAI_177006_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CHENNAI ENGINEERING SERVICES | 557670.75 | L1
| 2 | Enviro Chem Engineers and Consultants India Pvt Ltd | 581845.00 | L2