## BoQ1
Government eProcurement System Created By: Mukesh Meena Created Date/Time: 17-Jan-2024 05:05 PM Tender Title: Replacement of Old AHUs and allied works at ATS Complex, C.S.M.I.Airport, Mumbai - Phase - III Tender ID: 2023_AAI_178078_1
Tender Inviting Authority: Senior Manager (Engg.-Elect.),ATS Complex, Mumbai.
Name of Work: "Replacement of Old AHUs and allied works at ATS Complex, C.S.M.I.Airport, Mumbai - Phase - III"
Contract No: MUMBAI/ATS/ENGG-E/eNIT-03/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Air-O-Mec Engineers(GSTN-27AABPC1357K1ZX) |  | Ingenious Industries(GSTN-27AADFI4734Q1ZV)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal air handling units made of 25 mm. thick panels consisting of pre plasticized G.I. casing of thickness 0.8 mm. outside layer and 0.8 mm. inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure of 50 mm.W.G., minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5 mm.) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50 Hz, 3 Phase AC supply, drain connections, stainless steel (18 G) drain pan with PUF insulation, 150 mm. dia. dial type pressure guages (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement, etc. complete as per specification and of following capacities:-
2.00 | a) 10000 CFM | 2.00 | Set |  | 367400.00 | 734800.00 | 300000.00 | 600000.00 | 600000.00 | Ingenious Industries
3.00 | b) 18000 CFM | 2.00 | Set |  | 625200.00 | 1250400.00 | 510000.00 | 1020000.00 | 1020000.00 | Ingenious Industries
4.00 | Supply, Installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular / round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. a) Thickness 1.00 mm. sheet | 77.00 | Sq.Mtr. |  | 950.00 | 73150.00 | 1400.00 | 107800.00 | 73150.00 | Air-O-Mec Engineers
5.00 | Supply, Installation, Testing and commissioning of Starter panel for up to 15 HP VFD Drive wall/floor standing,compartmentlized double door totally enclosed dust and vermin proof fabricated with 14 G CRCA sheet,Powder coated of suitable size Panel should have detachable gland plates for incomer switch and cable chamber and having locking arrangement,6 inch cooling fan with grill and filter including supplying and fixing following switchgear,making connections,earthing, etc. as per IE Rules complete as required 1.Incomer: 63 A,3 Phase,25 KA MCCB with Rotatory Handle,ELCB and Multifunction meter - 1 No. 2.Main / Delta power contector 32 A, - 5 Nos. 3.R,Y,B Indication LED Lamp - 3 Nos. 4.MVK 32 , 240V AC over load Relay with base, 9 - 15 A - 1 No. 5.Digital Ammeter and Voltmeter - 1 Set. 6. ON,OFF, TRIP, RUN Indication Lamp - 4 Nos. 7.Star Delta Timer A 1DS,240 V A.C or equipment - 1 No. 8.Changover relay with base - 1 No. 9.Indication lamp - LED Type one no. each,for ON/OFF & TRIP, STOP / START - PUSH BUTTON - 2 Nos. | 4.00 | Set |  | 68000.00 | 272000.00 | 45000.00 | 180000.00 | 180000.00 | Ingenious Industries
6.00 | Supply, Installation, Testing and commissioning of Motor control centre - wall/floor standing, 15 HP VFD Panel suitable to operate on 415 ± 10% volts, 50 Hz., 3 Phase AC including earthing, etc. as per IE Rules complete as required | 4.00 | No. |  | 95000.00 | 380000.00 | 75000.00 | 300000.00 | 300000.00 | Ingenious Industries
7.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of MS 'C' class chilled water piping inside the building as per IS : 1239 (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastomeric nitril rubber of class 'O' insulation applied by adhesive confirming to standard specifications and finally applying 0.63 mm aluminum sheet cladding complete with type 3, grade 1 roofing felt strip (as per IS: 1322 as amended upto date) at joints and repairing of damage to building etc. as per specifications and as required.
8.00 | a) 50 mm. dia. (25 mm. insulation) | 20.00 | Meter |  | 2200.00 | 44000.00 | 2800.00 | 56000.00 | 44000.00 | Air-O-Mec Engineers
9.00 | b) 65 mm. dia. (25 mm. insulation) | 19.00 | Meter |  | 2500.00 | 47500.00 | 3200.00 | 60800.00 | 47500.00 | Air-O-Mec Engineers
10.00 | Supply, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water duly insulated to same specifications as the connected piping and adequately supported as per specifications.
11.00 | a) Up to 65 mm. dia. Butterfly valve (manual) with CI body SS disc, nitrile Rubber Seal & O-Ring PN 16 pressure rating for chilled water circulation complete with flanges, bolts, nuts, gaskets, etc. confirming to specifications as required. | 16.00 | No. |  | 5500.00 | 88000.00 | 7000.00 | 112000.00 | 88000.00 | Air-O-Mec Engineers
12.00 | b) Up to 65 mm. dia. Y-Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled circulation including insulation as specified. | 4.00 | No. |  | 6500.00 | 26000.00 | 7000.00 | 28000.00 | 26000.00 | Air-O-Mec Engineers
13.00 | S.I.T.C. of 40 mm. ball valve for supply and return chilled water pipes i/c tightening, etc. complete as required. | 4.00 | Job |  | 2000.00 | 8000.00 | 5500.00 | 22000.00 | 8000.00 | Air-O-Mec Engineers
14.00 | Supply, Installation, Testing & Commissioning of Three way mixing valve Proportionate type with modulating Actuator suitable for Temp. of -25LC to 130LC. This assembly shall have 2 nos. Universal controller operating on 24 Volts AC Supply having analogue output 0 to 10 Volts DC & activated by duct temperature sensor and differential pressure sensor installed in return air duct of measuring range -15°C to 65°C including complete wiring etc as required. a) 50 mm. | 4.00 | Set |  | 35000.00 | 140000.00 | 65000.00 | 260000.00 | 140000.00 | Air-O-Mec Engineers
15.00 | Supplying, fixing, testing and commissioning of fire dampers in supply air duct/ main branch and return air path as and where required of required sizes i/c control wiring. The damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
16.00 | a) Fire damper | 18.00 | Sq.Mtr. |  | 15000.00 | 270000.00 | 8000.00 | 144000.00 | 144000.00 | Ingenious Industries
17.00 | b) Actuator | 4.00 | No. |  | 12500.00 | 50000.00 | 7500.00 | 30000.00 | 30000.00 | Ingenious Industries
18.00 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges, etc. as per specifications. | 4.00 | Sq.Mtr. |  | 8000.00 | 32000.00 | 6500.00 | 26000.00 | 26000.00 | Ingenious Industries
19.00 | Supply and laying of following sizes of XLPE insulated (heavy duty), aluminum conductor cables, aromoured power cable of 1.1 KV grade conforming of IS 7098 part-I, amended upto date and laying on walls/ceiling / cable tray from main panel boards to AHUs and fixing arrangements, etc. as per specifications. a) 4C X 10 Sq.mm. | 75.00 | Meter |  | 225.00 | 16875.00 | 750.00 | 56250.00 | 16875.00 | Air-O-Mec Engineers
20.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. a) 4C X 10 Sq.mm. | 8.00 | Set |  | 450.00 | 3600.00 | 1500.00 | 12000.00 | 3600.00 | Air-O-Mec Engineers
21.00 | Supplying and fixing of 50 mm. dia. Medium duty class 'B' GI pipe duly insulated with following closed cell elastomeric nitril rubber of class 'O' insulation applied by adhesive confirming to standard specifications and finally applying 0.63 mm. aluminum sheet cladding complete with type 3, grade 1 roofing felt strip (as per IS: 1322 as amended upto date) at joints and repairing of damage to building, etc. as per specifications and as required. | 21.00 | Meter |  | 1250.00 | 26250.00 | 2200.00 | 46200.00 | 26250.00 | Air-O-Mec Engineers
22.00 | Supply and fixing of 100 m dia flexible duct with insulation complete as required. | 5.00 | Meter |  | 200.00 | 1000.00 | 450.00 | 2250.00 | 1000.00 | Air-O-Mec Engineers
23.00 | Dismantling of existing old AHUs from the AHU rooms. The job include dismantling of pipe lines and AHUs enclosure and shifting of AHUs at the ground floor in the desired location as required. | 4.00 | Job |  | 9000.00 | 36000.00 | 10000.00 | 40000.00 | 36000.00 | Air-O-Mec Engineers
24.00 | Providing of 22 TR portable temporary air - conditioning units of (multi TR capacity) as required at the specified locations of ATS complex during the removal of old AHU and installation of new 04 nos. AHU in AHU rooms at different floors of ATS Complex. The job includes supply and fixing of AC units at desired locations,gas charging and removal of ACs after completion of shut down. | 1.00 | Job |  | 174000.00 | 174000.00 | 347811.00 | 347811.00 | 174000.00 | Air-O-Mec Engineers
25.00 | Dismantling of existing UVGI (Ultra violet germicidal irradiation ) system i/c all accessories , power and control cables / wiring from existing AHUs and ITC of the dismantled UVGI system in newly installed AHUs, etc. as required. | 4.00 | Job |  | 5000.00 | 20000.00 | 10000.00 | 40000.00 | 20000.00 | Air-O-Mec Engineers
| Total in Figures |  |  |  |  | 3693575.00 |  | 3491111.00
Lowest Amount Quoted BY: Ingenious Industries(3491111.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Old AHUs and allied works at ATS Complex, C.S.M.I.Airport, Mumbai - Phase - III Tender ID: 2023_AAI_178078_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ingenious Industries | 3491111.00 | L1
| 2 | Air-O-Mec Engineers | 3693575.00 | L2