## BoQ1
Government eProcurement System Created By: Jagannath singh Deshmukh Created Date/Time: 09-Feb-2024 05:14 PM Tender Title: Supply, Installation, Testing, Commissioning and of 30 KLD Sewage Treatment Plant of SBR Technology including 5 years OandM at Jamnagar Airport Tender ID: 2023_AAI_178319_1
Tender Inviting Authority: Sr.Manager (E-E)
Name of Work:“Supply, Installation, Testing, Commissioning and of 30 KLD Sewage Treatment Plant of SBR Technology including 5 years O&M at Jamnagar Airport"
Tender ID: 2023_AAI_178319_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CLEAR ION EXPERTS PVT LTD(GSTN-06AAACC5410H1Z6) |  | RAVEENA WATERTECH(GSTN-27AKBPP2096A1ZE)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Engineering, Supply, Installation, Testing, Commissioning and Operationalization of 30KLD Sewage Treatment Plant of Sequential Batch Reactor (SBR) Technology at Jamnagar airport including Site inspection, Process design, preparation and submission of complete Layout Drawings, Hydraulic Drawings and Construction Drawings considering the following SOQ, Scope of work and as per Technical specification of the contract, obtaining initial and final NOC from State Pollution Control Board (if required) etc complete as required with a DLP of 1 Years
2.00 | Design, Drawing, Construction of Container Plant Room (Operator Cabin) having size of minimum 3000 mm X 4000 mm x 3000mm (H) including 1 no. Door and door panel having size of 1000mm (width)x 2000mm(height), 2 nos Windows each having size of 1000mm x1000mm with window panel, fabrication with minimum 3 mm corrugated MS Sheet and minimum 5 mm thick Angles/Channels, Rain proof, all finishing works such as Painting inside and outside walls, Roof with plastic emulsion paint, CC flooring etc including provision for fixing required electric wiring, LED fittigs, fan, sockets, complete as directed by the Engineer-in-charge. The necessary provision for cable entry for incoming and outgoing power cables, control cables, data cables, earthing, fixing arrangement of wall mounting / self standing control panel to be incorporated. The installation shall complete with proper locking arrangement & handles etc. on door and windows, finishing, cleaning etc complete as required. The appropriate foundation shall be provided based on the structure design. The design of Foundation and Structure shall be vetted from any Govt. Engineering Colleges/NIT/IIT etc. The cost is inclusive of all the above and nothing extra shall be paid. | 1.00 | Job |  | 500000.00 | 500000.00 | 278500.00 | 278500.00 | 278500.00 | RAVEENA WATERTECH
3.00 | Design,Supply/Construct & Installation of Bar screen chamber,pre-collection tank, oil & Grease chamber,Equalisation tank, SBR tank,treated water tank,Clean Water Tank,sludge holding tank and platform for equipment's & providing required inlet connection for Tanks outlet connection, inter connection with valve and all accessories complete etc as required. and as per specifications for 30 KLD STP plant.(Bidder shall use an existing newly constructed RCC tank ( 15.5 x 5.5 x 3.5 m) with modifications as required). The minimum Size and specifications of tanks( shall be as below:- 1.Seperate Bar Screen Chambers-2nos (one for Fine Bar Screen and the other for Coarse Bar Screen)- 0.75m3 minimum holding capacity 2.Pre Collection Tank(Material of construction RCC) of 16 m3 minimum holding capacity with depth of 2 m (1.5 m liquid depth + 0.5 m free board) below invert level,covered from the top with RCC with manhole having MS cover of approx. 500mm x 500 mm for maintenance purpose and provisions for fixing of Level Switchs, provisons for keeping 02 Nos. submersible pumps, Providing proper lifting arrangment to lift the the submiersible pumps fabricated from GI angle/GI pipe, Guide pipe and Chain made from SS 304 and providing suitable foundation of the tank. 3.Oil and Grease Tank(Material of construction RCC) of 03 m3 minimum holding capacity. 4.Equalisation Tank (Material of construction RCC) of 35 m3 holding capacity. 5.SBR tank (Material of construction RCC) of 35 m3 holding capacity. 6.Sludge Holding Tank:(Material of construction RCC) of 7 m3 holding capacity. 7.Treated Water tank:(Material of construction RCC) of 15 m3 holding capacity. 8.Clean water tank:(Material of construction RCC) of 15 m3 holding capacity. The tanks should have provisions for fixing of Level Switches with necessary Puddle Flanges.The foundation design shall be vetted through any Govt. Engineering Colleges/NIT/IIT. Note: Oil & Grease chamber,Equalisation tank, SBR tank,treated water tank,Clean Water Tank,sludge holding tank can be accomodated in existing tank of mentioned capacity but bidder has to quote as per the modification required in the existing tank. | 1.00 | Job |  | 2200000.00 | 2200000.00 | 1275200.00 | 1275200.00 | 1275200.00 | RAVEENA WATERTECH
4.00 | Supply and fixing of 2 Nos of Bar Screens of SS-304 of spacing of 10 mm & 6mm respectively for Coarse and fine Bar Screen. The Bar Screens shall be provided with Hand Rake suitable for lifting purpose. Bar Screens to be fitted at the Bar Screen chambers of pre collection tank | 1.00 | Job |  | 30000.00 | 30000.00 | 50780.00 | 50780.00 | 30000.00 | CLEAR ION EXPERTS PVT LTD
5.00 | Supply & Installation of Non Clog Type Submersible Pump (cutter type)- 02 Nos, Solid Passage of 35 mm max, Discharge of minimum 2 m3/hr, Head of 10 mtrs, minimum HP-1, RPM-2900, Motor body and shaft-SS, working voltage 3 phase, 415 +/-10% volts, 50Hz, Continuous Duty, Class 'F' insulation placed at inlet of pre collection tank to lift raw sewage from Pre-Collection Tank to Oil & grease chamberr, providing suitable length of 40mm UPVC pipe on delivery connection with flange, SS bolts and nuts, gasket, Water tight power supply connection, earthing connection, interlinking and common delivery lines with 40 mm UPVC pipe, UPVC valves, Non Return Valves, Pressure Gauges with Isolation Valve including all necessary accessories etc. and as per Technical specification of the Tender Document complete as required. (For Raw sewage transfer from Pre-Collection Tank to Oil & grease Chamber) | 1.00 | Job |  | 78000.00 | 78000.00 | 100700.00 | 100700.00 | 78000.00 | CLEAR ION EXPERTS PVT LTD
6.00 | Supply & Installation of Non Clog Type Submersible sewage transfer Pump (cutter type)- 02 Nos, Solid Passage of 35 mm max, Discharge of minimum 2 m3/hr, Head of 10 mtrs, minimum HP-1, RPM-2900, Motor body and shaft-SS, working voltage 3 phase, 415 +/-10% volts, 50Hz, Continuous Duty, Class 'F' insulation placed at inlet of Equalisation tank to lift sewage from Equalisation tank to SBR tank, providing suitable length of 40mm UPVC pipe on delivery connection with flange, SS bolts and nuts, gasket, Water tight power supply connection, earthing connection, interlinking and common delivery lines with 40 mm UPVC pipe, UPVC valves, Non Return Valves, Pressure Gauges with Isolation Valve including all necessary accessories etc. and as per Technical specification of the Tender Document complete as required. (For sewage transfer from Equalisation Tank to SBR tank) | 1.00 | Job |  | 78000.00 | 78000.00 | 100700.00 | 100700.00 | 78000.00 | CLEAR ION EXPERTS PVT LTD
7.00 | Supply & Installation of 63m3/Hr capacity (minimum) of Twin Lobe Rotary Air Blower -02 Nos (1 W + 1S), discharge pressure 5000 mmwc, 'V' belt or flexible couple drive, suitable capacity motor working on 415 +/- 10% volts, 3 phase, 50Hz with necessary enclosure for protecting the unit from rain water for fresh air supply to SBR Tank and Eqalization Tank. Supplying and providing air grid distribution system with non clog type fine bubble diffusers for SBR tanks and seperate Air Grid Distribution for Equalization Tank. Air distribution shall be comprise of isolation valves, pipe droppers, laterals, interlinking etc. including Mild Steel Epoxy Painted (MSEP) pipeline with all fittings, supports, clamps, flanges, non clog, modular type air dispersion system capable of handling 3-5 cfm of air to the required depth with necessary supports, valves, with all necessary accessories, operation of aeration system with PLC based control etc. complete as required. | 1.00 | Job |  | 240000.00 | 240000.00 | 175700.00 | 175700.00 | 175700.00 | RAVEENA WATERTECH
8.00 | Supply & Installation of complete Floating type Decanter Mechanism of suitable capacity suitable for SBR Tank including moving weir arm fabricated from SS 304 with suitable drive, Scum Guard, Down comer & supports with PLC controlled Auto Operation, motorized valves with by-pass arrangement, local control box with manual operation selection, push buttons, electrical and communication cables, wiring, communication to main PLC by RS 485/Ethernet etc. as required. | 1.00 | Job |  | 125000.00 | 125000.00 | 175700.00 | 175700.00 | 125000.00 | CLEAR ION EXPERTS PVT LTD
9.00 | Supply & Installation of Centrifugal Monoblock Filter Feed Pump - 02 Nos (1W+1S) to transfer water from Treated Water Tanks to filters with following specifications a) Discharge of 1.5 m3/hr at 35 meter head (Minimum), b) Minimum 1.5HP motor capacity, c) Impeller-Cast iorn, d) Motor body-Cast iron, e) Power supply-415v+/-10%, 3-phase, concrete foundation, necessary enclosure for rain protection, providing individual 25 mm UPVC suction lines, interlinking and common delivery line upto Multi Grade Filter with UPVC piping, UPVC butterfly valves (for both suction & discharge), UPVC Non Return Valves, Pressure Gauges with isolation including all necessary accessories etc complete as required. | 1.00 | Job |  | 34000.00 | 34000.00 | 57800.00 | 57800.00 | 34000.00 | CLEAR ION EXPERTS PVT LTD
10.00 | Supply & Installation of Pressure Sand Filter made of Mild Steel Epoxy Painted (MSEP) of minimum dia 0.60m and 1.875m height of capacity not less than 1.5 m3/hr at 3 kg/cm2 pressure with max pressure rating of 3.5 kg/cm2 pressure vessel, necessary foundation, along with 50 mm UPVC frontal pipeline, necessary valves, interlinking pipes, delivery line upto Activated Carbon Filter, drain line upto collection tank, Pressure Gauge with isolation, Air Release, provision of back wash arrangement, valves and all necessary accessories complete with filtering media , support media etc as required. | 1.00 | Job |  | 57000.00 | 57000.00 | 110000.00 | 110000.00 | 57000.00 | CLEAR ION EXPERTS PVT LTD
11.00 | Supply & Installation of Activated Carbon Filter made of Mild Steel Epoxy Painted (MSEP) of minimum dia 0.60m and 1.875m height of capacity not less than 1.5 m3/hr at 3.0 kg/cm2 pressure with max pressure rating of 3.5 kg/cm2 pressure vessel, necessary foundation, 50mm UPVC frontal pipeline, necessary valves, interlinking pipes for delivery line upto Treated water tank, drain line upto collection tank, Pressure Gauge with isolation valve, Air Release, provision of back wash arrangement, valves, all necessary accessories complete with filtering media, support media etc as required. | 1.00 | Job |  | 61000.00 | 61000.00 | 115700.00 | 115700.00 | 61000.00 | CLEAR ION EXPERTS PVT LTD
12.00 | Supply, Installation of UV System of capacity 1.5 cum/hr, fabricated from SS for 30KLD Packaged type SBR technology Sewage Treatment Plant including wiring, all accessories complete etc as required. | 1.00 | Job |  | 32000.00 | 32000.00 | 67800.00 | 67800.00 | 32000.00 | CLEAR ION EXPERTS PVT LTD
13.00 | Supply, Installation of Centrifugal Monoblock Clean Water Pump - 02 Nos (1 W + 1 S) to transfer water from clean water tank with following specifications a) Discharge of 2 m3/hr at 25 meter head (Minimum), b) minimum 1HP motor capacity, c) Impeller-Cast iron, d) Motor body-Cast iron, e) Power supply-415v+/- 10%, 3-Phase, concrete foundation, necessary out door enclosure for rain protection, providing individual UPVC suction lines, interlinking and common delivery line upto 1mtr with UPVC piping, UPVC Butterfly Valves (for both suction & discharge), UPVC Non Return Calves, Pressure Gauges with isolation including all necessary accessories etc as required. | 1.00 | Job |  | 22000.00 | 22000.00 | 55700.00 | 55700.00 | 22000.00 | CLEAR ION EXPERTS PVT LTD
14.00 | Supply, Installation of Sludge Feed Pump Screw type -02 Nos. (1W+1S) of capacity of 1m3/hr & 50 mwc for 30KLD Packaged type Sewage Treatment Plant SBR technology with following specifications a) Minimum motor capacity- 0.5HP, b) Impeller-Cast iron, c) Motor body-Cast iron, d) Power supply-415v+/- 10%, 3-Phase, concrete foundation, necessary out door enclosure for rain protection, providing individual UPVC suction lines from Sludge holding Tank, interlinking and common delivery line to Filter Press, valves, Pressure Gauges with isolation, including all necessary accessories etc as required. | 1.00 | Job |  | 22000.00 | 22000.00 | 57500.00 | 57500.00 | 22000.00 | CLEAR ION EXPERTS PVT LTD
15.00 | Supply, Installation of Hydraulic/Automatic Filter Press for 30 KLD Packaged type SBR technology Sewage Treatment Plant, concrete foundation, enclosure, drain pipe to collection tank etc complete as required. | 1.00 | Job |  | 190000.00 | 190000.00 | 145700.00 | 145700.00 | 145700.00 | RAVEENA WATERTECH
16.00 | Supply & Installation of Level Switches in Pre-Collection Tank, Equalisation Tank, Collection tank and Treated Water Tank for Low & High Level alongwith suitable Wiring, Connection & Interconnection as required | 1.00 | Job |  | 20000.00 | 20000.00 | 25700.00 | 25700.00 | 20000.00 | CLEAR ION EXPERTS PVT LTD
17.00 | Supply & Installation of 1-1/2 inch Magnetic Flow Water Meter for Treated Water Delivery Line including isolation valves, sampling point and all accessories etc as required. | 1.00 | Job |  | 24000.00 | 24000.00 | 97500.00 | 97500.00 | 24000.00 | CLEAR ION EXPERTS PVT LTD
18.00 | Supply & Installation of Flow Water Meter suitable for Raw Sewage Inlet Line of collection tank including isolation valves, sampling point and all accessories etc. complete as required. | 1.00 | Job |  | 12000.00 | 12000.00 | 15700.00 | 15700.00 | 12000.00 | CLEAR ION EXPERTS PVT LTD
19.00 | A) Fabrication, Supply, Installation, testing & Commissioning of Compartmentalised type PLC based Motor Control Center (MCC) Panel with all accessaries for Auto/Manual On/Off control of entire 30 KLD Packaged type Seawage Treatment Plant of SBR technology, fabricated from 1.6mm CRCA sheet, totally enclosed, IP 54, floor mounted/wall mounted, powder coated, fabricated with following accessories:- 1) Incomer - 4pole MCCB 100Amp, 25KA - 2 nos. with electrical and mechanical interlocking. 2) 4-Pole Al Bus Bar 150 amps -1 set. 3) Outgoings: (a) 32 Amps 3pole MCB, Contactors, ON/OFF Push Button, OLR, SPP for SBR Blowers -2nos, (b)25 Amps 3pole MCB, Contactors, ON/OFF Push Button, OLR, SPP for Submerisible Sewage Pumps- 2nos, (c)25 Amps 3pole MCB, Contactors, ON/OFF Push Button, OLR, SPP for Sewage Feed Pumps- 2nos, (d)25Amps,3 pole MCB, Contactors, ON/OFF Push Button, OLR,SPP for Filter Feed Pumps -2nos, (e)25 Amps 3pole MCB, Contactors, ON/OFF Push Button, OLR,SPP, for Clean Water Pumps -2nos. (f) 25 Amps 3pole MCB, Contactors, ON/OFF Push Button , OLR,SPP for Sludge Feed Pumps -2nos. (g) 25 Amps 2pole MCB for internal/external lighting- 3nos. (h) 25 Amps 3 Pole MCB (Spare) - 3 nos. (B) Supply and laying of required numbers and length of XLPE insulated, PVC sheathed Copper conductor cable including cable glanding, GI Cable tray, fixing of cables on Tray/Wall/Surface etc. as required for following Pumps / equipments: a) 3C X 6sqmm cable for blower motor-2 Nos. b) 3C X 6sqmm submersible cable for submersible pumps-2 Nos. c) 3C X 6sqmm cable for Sewage Feed Pumps -2 Nos. c) 3C X 6sqmm for Filter Feed Pumps-2 Nos. d) 3C X 6sqmm cable for Clean Water Pumps -2 Nos. f) 3C X 6sqmm cable for Sludge Feed Pump -2 No. (C) 8 SWG GI Wire to all individual motors from main panel for earth connections - 2 runs each. (D) 'ON' Red coloured LED Indicator for each outgoing with protection MCBs . (E) R,Y,B LED indication (incomer side) with protection MCBs - 2 sets. (F) 96mmx96mm Digital Voltmeter with Selector Switch including interconnections -2 nos. (G) 96mmx96mm Digital Ammeter with Selector Switch including interconnections and 3 nos. CT's of suitable rating - 1set (H) Power supply and control wiring to Motorized Valves, All Pumps, Blowers, UV System etc. complete as required. (Note: Quoted rate shall include SITC of MCC panel, Supply and Laying of armoured XLPE copper cables on GI trays of suitable size, Supports, Cable Glands, Providing and Laying of 2 nos 8 SWG GI Wire for earthings to all equipment, Providing and laying of all Communication and Control cables, PLC etc. complete as required.) | 1.00 | Job |  | 375000.00 | 375000.00 | 125700.00 | 125700.00 | 125700.00 | RAVEENA WATERTECH
20.00 | Supply & Installation of PLC Software System including all Hardwares and Softwares to Control the entire 30KLD SBR STP including all the pumps and blowers etc. in Auto/Manual mode. The automation system includes automatic valves with 4.3" HMI dispay, process and operator software with dynamic flow chart displayed on monitor, Furniture, UPS, Computer etc complete as required. | 1.00 | Job |  | 150000.00 | 150000.00 | 128700.00 | 128700.00 | 128700.00 | RAVEENA WATERTECH
21.00 | Earthing with G.I. earth plate 600 mm x 600 mm x 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 10000.00 | 20000.00 | 27800.00 | 55600.00 | 20000.00 | CLEAR ION EXPERTS PVT LTD
22.00 | Providing and fixing 25 mm x 5 mm G.I. Strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and refilling etc. as required. | 30.00 | Meter |  | 300.00 | 9000.00 | 1250.00 | 37500.00 | 9000.00 | CLEAR ION EXPERTS PVT LTD
23.00 | Providing and fixing 25 mm x 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Meter |  | 300.00 | 6000.00 | 1250.00 | 25000.00 | 6000.00 | CLEAR ION EXPERTS PVT LTD
24.00 | Providing Internal & External Electrical Installations inside the Operator Cabin, Inside Covered Shed of STP and outside of STP with suitable size Copper conductor, PVC insulated, FRLS wires/cables as per CPWD specifications, ISI marked MS conduiting on surface i/c painting & providing Modular type switch board, Modular type Switches/Sockets along with supply and installation of following fittings including all accessories etc. complete as required. (a) LED Tube light Fittings (2000lm, Efficacy ≥110 lm/W): 6 nos. (b) 400 mm sweep Wall mounted fan: 1no, (c) 6/16A Sockets: 4nos, (d) IP 65 Outdoor LED Light Fitting (4500lm, Efficacy ≥100 lm/W) - 4 nos. (e) Double Door SPN DB with required numbers of MCBs- 1 set | 1.00 | Job |  | 42000.00 | 42000.00 | 57500.00 | 57500.00 | 42000.00 | CLEAR ION EXPERTS PVT LTD
25.00 | Supply of 3.5C X 50 sq.mm. Al conductor, XLPE insulated, PVC sheathed, armoured power cable of 1.1 kV Grade conforming to IS:7098 Part-I amended upto date etc. complete all as required and as specified in Technical Specifications. | 200.00 | Meter |  | 500.00 | 100000.00 | 850.00 | 170000.00 | 100000.00 | CLEAR ION EXPERTS PVT LTD
26.00 | Supply of 63 mm dia (OD- 63 mm and ID- 51mm nominal) ISI marked DWC HDPE pipe along with all accessories like socket, bend, couplers and plug etc. conforming to IS:16205 Part-24 or amended complete as required and as specified in Technical Specifications. | 100.00 | Meter |  | 300.00 | 30000.00 | 340.00 | 34000.00 | 30000.00 | CLEAR ION EXPERTS PVT LTD
27.00 | Laying of one number 63 mm dia DWC HDPE pipe complete with fittings, cutting, jointing etc. direct in ground at a depth of 75 cm including excavation and refilling the trench etc. complete as required. | 100.00 | Meter |  | 100.00 | 10000.00 | 75.00 | 7500.00 | 7500.00 | RAVEENA WATERTECH
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size 3.5C x 50 sq mm. in the existing RCC/ HUME/ METAL/ HDPE/DWC HDPE Pipe /Open Trench etc as required. | 200.00 | Meter |  | 100.00 | 20000.00 | 75.00 | 15000.00 | 15000.00 | RAVEENA WATERTECH
29.00 | Supplying & making End termination with Brass compression gland and Aluminium Lugs for 3-1/2 x 50 sq mm PVC insulated PVC sheathed /XLPE Aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Set |  | 500.00 | 2000.00 | 300.00 | 1200.00 | 1200.00 | RAVEENA WATERTECH
30.00 | Testing, Commissioning and Operationalization of complete Sewage Treatment Plant including all the accessories/equipments in Manual/Auto mode after providing sewage by AAI and conducting trial run for a period of minimum One month. During this period contractor shall arrange all required manpower and materials for the trial run. The date of completion of SH-I will be recorded after completion of trial run and submission of treated water test certificate fully meeting the tender criteria and pollution norms along with all documents as per scope of work. | 1.00 | Job |  | 100000.00 | 100000.00 | 15700.00 | 15700.00 | 15700.00 | RAVEENA WATERTECH
32.00 | FOR FIRST YEAR DURING DLP
33.00 | Operation of complete Sewage Treatment Plant 30 KLD based on SBR Technology for all days i/c Sundays and holidays (One trained Technician cum Operator(Highly Skilled Manpower) in 1 shift per day, 6 days in a week and one trained Technician cum operator as reliever) with uniform, necessary tools as per specification. (Minimum Wage as labour laws shall be followed)-FOR FIRST YEAR DURING DLP Providing of consumable items such as cotton waste, grease, UV lamp, Chemicals, safety materials such as shoes, gloves, mask etc. monitoring and maintaining the required registers, monthly testing of treated water from the State govt. approved Lab/ NABL accredited Lab, monitoring the reading of water meter etc. as required for operation of Sewage Treatment Plant 30 KLD as per specification. -FOR FIRST YEAR DURING DLP | 1.00 | Year |  | 647508.00 | 647508.00 | 505107.00 | 505107.00 | 505107.00 | RAVEENA WATERTECH
34.00 | Operation and comprehensive maintenance of complete Sewage Treatment Plant 30 KLD based on SBR Technology for all days i/c Sundays and holidays (One trained Technician cum Operator(Highly Skilled Manpower) in 1 shift per day, 6 days in a week and one trained Technician cum operator as reliever, for Sundays and Holidays) with uniform, necessary tools, consumable items such as cotton waste, grease, UV lamp, Chemicals, safety materials such as shoes, gloves, mask etc. monitoring and maintaining the required registers, monthly testing of treated water from the State govt. approved Lab/ NABL accredited Lab, monitoring the reading of water meter etc. as required and as per specification. (Minimum Wage as labour laws shall be followed)-After DLP period
35.00 | 2nd Year Operation and AICMC | 1.00 | Year |  | 686358.00 | 686358.00 | 535413.00 | 535413.00 | 535413.00 | RAVEENA WATERTECH
36.00 | 3rd Year Operation and AICMC | 1.00 | Year |  | 728912.00 | 728912.00 | 568609.00 | 568609.00 | 568609.00 | RAVEENA WATERTECH
37.00 | 4th Year Operation and AICMC | 1.00 | Year |  | 774833.00 | 774833.00 | 604431.00 | 604431.00 | 604431.00 | RAVEENA WATERTECH
38.00 | 5th Year Operation and AICMC | 1.00 | Year |  | 825197.00 | 825197.00 | 643719.00 | 643719.00 | 643719.00 | RAVEENA WATERTECH
| Total in Figures |  |  |  |  | 8251808.00 |  | 6437059.00
Lowest Amount Quoted BY: RAVEENA WATERTECH(6437059.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply, Installation, Testing, Commissioning and of 30 KLD Sewage Treatment Plant of SBR Technology including 5 years OandM at Jamnagar Airport Tender ID: 2023_AAI_178319_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RAVEENA WATERTECH | 6437059.00 | L1
| 2 | CLEAR ION EXPERTS PVT LTD | 8251808.00 | L2