## BoQ1
Government eProcurement System Created By: SUJATHA R Created Date/Time: 12-Jan-2024 04:09 PM Tender Title: Provision of UPS at Salem Airport Tender ID: 2023_AAI_178619_1
Tender Inviting Authority: Asst. General Manager (Engg-Electrical), AAI, RHQ SR, Chennai Airport, Chennai - 600027
Name of Work: Provision of UPS for GLF at Salem Airport.
Contract No: 2023_AAI_ 178619_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | POWER ONE MICRO SYSTEMS PVT LTD(GSTN-29AABCP6384L1ZS) |  | Numax Energy Solutions(GSTN-36AAIFN0814D1ZO) |  | DEEPAKELECTRICALS(GSTN-33ALUPD3531C1ZI) |  | SUN POWER CONVERSION PVT LTD(GSTN-09AAICS9074K1ZL) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | SH-I: SITC of UPS and allied works
1.01 | 2 X 80 KVA capacity, 3-phase input / 3 phase output online UPS with Isolation Transformer and Battery Bank: Supply, Installation, Testing and Commissioning (SITC) of 2 X 80 KVA capacity, 3-phase input / 3 phase output online UPS with double conversion type advance IGBT technology with suitable rated (min. K-1 rated) aluminum wound 100 kVA capacity isolation transformer at input of the each UPS with MCCB and soft starter for parallel redundancy also to drive constant current regulators with 100% unbalanced load at full load condition. The UPS shall have built in 100% rated automatic static by pass, manual by pass facilities for maintenance, active input power factor correction, phase sequence corrector, pure sine wave output, input/output isolation, compatibility with generator supply, cold start capability, EMI/RFI noise filter, advanced communication- RS232 / RS 485 ports and user friendly LCD display and run in parallel redundant system configuration for equal sharing of load,battery management features integrated with main UPS controller, suitable to operate at 400V±15%, 50Hz, 3 phase AC supply, suitable IP rated enclosure and capable to take 2 phase & single phase loads on 3phase output of UPS with 100% unbalanced and necessary safety protections along with suitable size MCCB inside etc complete as required. The job also includes supply, installation, testing & commissioning of two battery bank sets of required/suitable size with required number of 12V VRLA SMF batteries suitable to give a backup time of minimum 30 minutes per each UPS ,along with battery racks/enclosure, suitable rated battery circuit breaker, interconnections between batteries as well as battery bank to UPS and interconnections between isolation transformer to UPS with suitable insulated copper conductors, connectors,glanding & terminations etc., complete as required. (Entire system shall be provided with 2 years warranty). Note: Bidders shall quote for SITC portion only. | 1.00 | Job | Item no.1 | 2085322.00 | 2460679.96 | 3283169.00 | 3874139.42 | 3333333.00 | 3933332.94 | 2850000.00 | 3363000.00 | 2775000.00 | 3274500.00 | 2897000.00 | 3418460.00 | 2085322.00 | POWER ONE MICRO SYSTEMS PVT LTD | 2460679.96 | POWER ONE MICRO SYSTEMS PVT LTD
2.00 | SH:II All Inclusive Comprehensive Maintenance Contract (AICMC) except replacement of batteries after DLP.
2.01 | 1st Year AICMC cost after 2 years of DLP @ 4.68% on item no 1.01
2.02 | 2nd Year of AICMC cost after 2 years of DLP @ 4.96% on item no 1.01
2.03 | 3rd Year of AICMC cost after 2 years of DLP @ 5.45% on item no 1.01
2.04 | 4th Year of AICMC cost after 2 years of DLP @ 5.81% on item no 1.01
2.05 | 5th Year of AICMC cost after 2 years of DLP @ 6.59% on item no 1.01
2.06 | 6th Year of AICMC cost after 2 years of DLP @ 7.16% on item no 1.01
2.07 | 7th Year of AICMC cost after 2 years of DLP @ 7.76% on item no 1.01
2.08 | 8th Year of AICMC cost after 2 years of DLP @ 8.45% on item no 1.01
| Total in Figures |  |  |  | 2085322.00 | 2460679.96 | 3283169.00 | 3874139.42 | 3333333.00 | 3933332.94 | 2850000.00 | 3363000.00 | 2775000.00 | 3274500.00 | 2897000.00 | 3418460.00

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS at Salem Airport Tender ID: 2023_AAI_178619_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | POWER ONE MICRO SYSTEMS PVT LTD | 2460679.96 | L1
| 2 | vk sam engineering | 3274500.00 | L2
| 3 | SUN POWER CONVERSION PVT LTD | 3363000.00 | L3
| 4 | Awasthi Electric Works | 3418460.00 | L4
| 5 | Numax Energy Solutions | 3874139.42 | L5
| 6 | DEEPAKELECTRICALS | 3933332.94 | L6