## BoQ1
Government eProcurement System Created By: Rudra Prasad Acharya Created Date/Time: 07-May-2024 06:59 PM Tender Title: Provision of Frangible mast with FFM antenna for ILS at B.P.I Airport, Bhubaneswar. SH-Electrical works. Tender ID: 2023_AAI_179278_1
Tender Inviting Authority: Asst. General Manager (Engg.-Elect.)-II, Airports Authority of India, B.P.I.Airport, Bhubaneswar.
Name of Work: Provision of Frangible mast with FFM antenna for ILS at B.P.I Airport, Bhubaneswar. SH-Electrical works.
Contract No: 2023_AAI_179278_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -659325
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of 1 x 20 WATT Batten type LED tube light fittings with LED tube having minimum 2200 lumen output & minimum CCT from 5700K to 6500K i/c necessary electronic driver, LED lamp suitable to operate with 230V AC power supply as per tender specifications complete as required. | 4.00 | Each |  | 350.00 | 1400.00 | 1400.00 | Manish Electricals
2.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 4.00 | Point |  | 1200.00 | 4800.00 | 4800.00 | Manish Electricals
3.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 4.00 | Point |  | 950.00 | 3800.00 | 3800.00 | Manish Electricals
4.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
4.01 | 2 X 2.5 sq. mm +1 X 2.5 sq. mm earth wire | 20.00 | Meter |  | 180.00 | 3600.00 | 3600.00 | Manish Electricals
4.02 | 2 X 4 sq. mm +1 X 4 sq. mm earth wire | 20.00 | Meter |  | 240.00 | 4800.00 | 4800.00 | Manish Electricals
4.03 | 2 X 6 sq. mm +1 X 6 sq. mm earth wire | 20.00 | Meter |  | 280.00 | 5600.00 | 5600.00 | Manish Electricals
5.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 5 pin 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 8.00 | each |  | 450.00 | 3600.00 | 3600.00 | Manish Electricals
6.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/ Isolator)
6.01 | 6 way (4 + 18), Double door | 1.00 | Each |  | 4500.00 | 4500.00 | 4500.00 | Manish Electricals
7.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required
7.01 | Single pole | 12.00 | Each |  | 170.00 | 2040.00 | 2040.00 | Manish Electricals
7.02 | Triple pole and Neutral | 2.00 | Each |  | 1050.00 | 2100.00 | 2100.00 | Manish Electricals
8.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
8.01 | 63 amps | 1.00 | Each |  | 800.00 | 800.00 | 800.00 | Manish Electricals
9.00 | Supply, Installation, Testing and Commissioning of 1.5 Ton(4500kCal/Hr capacity), 5 star rating Inverter split Air conditioner with all the internal component of indoor unit shall be fire retardant, cordless remote & fitted with rotary /scroll /semi-hermetic compressor, copper condenser coil, operating on refrigerant R-22 /Non CFC suitable for high wall mounting & suitable for operation on 230V, 50Hz, single phase AC supply capable of performing following functions; (i) Cooling (ii) Dehumidifying, (iii) Air Circulating, & (iv) Filtering.. (Minimum five or more star rating) including 3 mtrs refrigerant piping and 3 mtrs hard drain pipe.(As per AAI Preferred Make List) | 2.00 | Each |  | 45000.00 | 90000.00 | 90000.00 | Manish Electricals
10.00 | Supply & fixing of Iron Angle stand suitable for installation of outdoor unit of above mentioned 1.5 TR split air-conditioners including paining etc. complete as required. | 2.00 | Job |  | 1200.00 | 2400.00 | 2400.00 | Manish Electricals
11.00 | Supply, Installation, Testing and Commissioning of auto change over switch for two numbers of split air conditioners on a pre-set time interval including termination etc complete as required. | 4.00 | Each |  | 2000.00 | 8000.00 | 8000.00 | Manish Electricals
12.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 40 mm dia and 3.0 meter long etc. with charcoal/ coke and salt as required. | 8.00 | Set |  | 16000.00 | 128000.00 | 128000.00 | Manish Electricals
13.00 | Supplying and laying 25 mm X 3 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm including brazing of all joints) | 200.00 | Meter |  | 950.00 | 190000.00 | 190000.00 | Manish Electricals
14.00 | Providing and fixing 4.00 mm dia copper wire in existing pipe/ surface for loop earthing etc complete as required. | 200.00 | Meter |  | 150.00 | 30000.00 | 30000.00 | Manish Electricals
15.00 | Supply and Fixing of surge protection device type 2 or class B, I max 40kA protection against direct and indirect lighting surges in the existing MCB DB including making connection etc as required. | 3.00 | Each |  | 22000.00 | 66000.00 | 66000.00 | Manish Electricals
16.00 | Supply of following size 1.1 kv grade, XLPE insulated and PVC inner sheathed Aluminum conductor armored power cable conforming to IS: 7098(Part 1)1988/ IS: 7098 (Part 1) with up to date amendments etc. complete as required.
16.01 | 4 core x 25 sq mm | 1000.00 | Meter |  | 180.00 | 180000.00 | 180000.00 | Manish Electricals
17.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
17.01 | upto 35 sq. mm | 150.00 | Meter |  | 30.00 | 4500.00 | 4500.00 | Manish Electricals
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
18.01 | 4 core x 25 sq mm(28mm) | 4.00 | Each |  | 800.00 | 3200.00 | 3200.00 | Manish Electricals
19.00 | Supply and laying of 12 core Armored Single-Mode Optic Fiber Cable in existing pipe/ surface complete as required | 2000.00 | Meter |  | 70.00 | 140000.00 | 140000.00 | Manish Electricals
20.00 | Supply, Installation, Testing & Commissioning of 24 port Light guide Interconnect Unit (LIU) fully populated with modules/adapters complete as required. | 2.00 | Each |  | 3000.00 | 6000.00 | 6000.00 | Manish Electricals
21.00 | Supply, Installation, Testing and commissioning of 3 KVA UPS with 30 minutes battery back up including provision of necessary battery rack, battery to UPS cabling, termination etc complete as required. | 2.00 | Set |  | 40000.00 | 80000.00 | 80000.00 | Manish Electricals
22.00 | Supply, Installation, Testing, and Commissioing of five spike air terminals of 16 mm dia.of 1000 mm length as required and as per site conditions. the air terminal shall be manufactured with copper. The terminal shall be provided with the integrated / attached threaded base support suitable for mounting the terminals as per site condition. The base support shall be minimum 3 mm thick and shall have inbuilt connector fitting for connection of lightning conductor in such away that conductor contact area shall not be less than 40mm on all side of the conductor. The air terminal shall be supplied with necessary fixing arrangement for fixing on surface complete as required. | 4.00 | Each |  | 8000.00 | 32000.00 | 32000.00 | Manish Electricals
23.00 | Supply of 63 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 80, PN 10 complete as required. | 2000.00 | Meter |  | 225.00 | 450000.00 | 450000.00 | Manish Electricals
24.00 | Laying of 63 mm dia HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 2000.00 | Meter |  | 140.00 | 280000.00 | 280000.00 | Manish Electricals
| Total in Figures |  |  |  |  | 1727140.00
Lowest Amount Quoted BY: Manish Electricals(1727140.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Frangible mast with FFM antenna for ILS at B.P.I Airport, Bhubaneswar. SH-Electrical works. Tender ID: 2023_AAI_179278_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 1727140.00 | L1