## BoQ1
Government eProcurement System Created By: SRIKANTH GADE Created Date/Time: 21-Dec-2023 03:40 PM Tender Title: Repair/Overhauling of high mast poles of height 25/30 meters -Quantity-07 Nos and High mast poles of height 12.5 meters Quantity-12 Nos and replacement of conventional flood lights with LED flood lights in OFMK estate. Tender ID: 2023_AVNL_166537_1
Tender Inviting Authority: CHIEF GENERAL MANAGER ORDNANCE FACTORY MEDAK (A UNIT OF AVNL)
Name of Work: Repair/Overhauling of High mast poles of height 25/30 meters (Quantity- 07 No’s) & High mast poles of height 12.5 meters (Quantity- 12 No’s) and Replacement of Conventional flood lights with LED Flood lights in Ordnance Factory Medak Estate area.
Contract No: 76025/ TE-39/ OFMK/EOC/HIGH MAST POLES/ 2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ANU ELECTRICALS(GSTN-29AKWPM5631P1Z2) |  | elektron(GSTN-09AAFFE6230P1Z2) |  | INDUSTRIAL INSTRUMENTS(GSTN-NA) |  | RAM ELECTRICALS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Dismantling of the lantern carriage system from the high mast pole safely along with the luminaries. | 19.00 | No | 100.00 | 10000.00 | 190000.00 | 3927.00 | 74613.00 | 15000.00 | 285000.00 | 7500.00 | 142500.00 | 74613.00 | elektron
2.00 | Removing of the high mast pole from the plinth and re-installation after completion of repair/overhauling work safely by the suitable means of equipment. | 19.00 | No | 100.00 | 19000.00 | 361000.00 | 28050.00 | 532950.00 | 59000.00 | 1121000.00 | 57000.00 | 1083000.00 | 361000.00 | ANU ELECTRICALS
3.00 | Double drum winch : Supply and Fixing of double drum winch along with suitable bracket, Motorized and manual method of operation, With separate handle for manual operation, Each driving spindle of the winch shall be positively locked when not in use, gravity activated pawls. The capacity, operating speed, safe working load of minimum 750 KG, recommended lubrication and serial number of the winch shall be clearly marked on each winch. The winch shall be of self lubricating type by means of an oil bath and oil shall be readily available grades of reputed producers. The winch drums shall be grooved to ensure perfect seat for stable and tidy rope lay, with no chances of rope slippage. Bobbin and flanges should have enough physical dimensions so that rope shall not come out during up and down mechanism. The rope termination in the winch shall be such that distortion or twisting is eliminated and at least 5 to 6 turns of rope remains on the drum even when the lantern carriage is fully lowered and rested on the rest pads. S&F of chain, chain pulley, necessary SS D-clamps, Re-rings etc. A test certificate shall be furnished by the contractor from the original equipment manufacturer for each winch in support of the maximum load operated by the winch. The winch shall be type tested in presence of the reputed laboratories/ Institutions. Type test report shall be submitted along with the offer. Suitable gear box system with necessary hardware accessories for fixing. Make: Bajaj/Crompton/Wipro. | 7.00 | No | 10.00 | 46000.00 | 322000.00 | 48526.00 | 339682.00 | 45000.00 | 315000.00 | 94000.00 | 658000.00 | 315000.00 | INDUSTRIAL INSTRUMENTS
4.00 | Double drum winch :Supply and Fixing of double drum winch along with suitable bracket, motorized and manual method of operation, with separate handle for manual operation, Each driving spindle of the winch shall be positively locked when not in use, gravity activated pawls. The capacity, operating speed, safe working load of minimum 350 KG, recommended lubrication and serial number of the winch shall be clearly marked on each winch. The winch shall be of self lubricating type by means of an oil bath and oil shall be readily available grades of reputed producers. The winch drums shall be grooved to ensure perfect seat for stable and tidy rope lay, with no chances of rope slippage. Bobbin and flanges should have enough physical dimensions so that rope shall not come out during up and down mechanism. The rope termination in the winch shall be such that distortion or twisting is eliminated and at least 5 to 6 turns of rope remains on the drum even when the lantern carriage is fully lowered and rested on the rest pads. S&F of chain, chain pulley, necessary SS D-clamps, Re-rings etc . A test certificate shall be furnished by the contractor from the original equipment manufacturer for each winch in support of the maximum load operated by the winch. The winch shall be type tested in presence of the reputed laboratories/ Institutions. Type test report shall be submitted along with the offer. Suitable gear box system with necessary hardware accessories for fixing. Make: Bajaj/Crompton/Wipro. | 12.00 | No | 10.00 | 41500.00 | 498000.00 | 18419.00 | 221028.00 | 39000.00 | 468000.00 | 86500.00 | 1038000.00 | 221028.00 | elektron
5.00 | Power tool for Winch: A suitable, electrically driven, internally mounted power tool, with mounting plate, with manual over ride shall be supplied for the raising and lowering of the lantern carriage for maintenance purposes. The speed of the power tool shall be to suit the system. The power tool shall be single speed, provided with a motor of the required rating 1.5 H.P (minimum). The power tool shall be supplied complete with suitable control. The capacity and speed of the electric motor used in the power tool shall be suitable for the lifting of the design load installed on the lantern carriage. The power tool mounting shall be so designed that it will be not only self-supporting but also aligns the power tool perfectly with respect to the winch spindle during the operations. Also, a handle for the manual operation of the winches in case of problems with the electrically operated tool shall be provided and shall incorporate a torque limiting device. The power tool operation shall always be through a separate torque limiting device to protect the wire ropes from over stretching. It shall be mechanical with suitable load adjusting device. The torque limiter shall trip the load when it exceeds the adjusted limits. There shall be suitable provision for warning the operator once the load is tripped off. The torque limiter is a requirement as per the relevant standards in view of the over all safety of the system. Make: Kirloskar/crompton/Hindustan Electric/Universal company. | 7.00 | No | 10.00 | 28000.00 | 196000.00 | 14960.00 | 104720.00 | 28700.00 | 200900.00 | 23000.00 | 161000.00 | 104720.00 | elektron
6.00 | Power tool for Winch: A suitable, electrically driven, internally mounted power tool, with mounting plate, with manual over ride shall be supplied for the raising and lowering of the lantern carriage for maintenance purposes. The speed of the power tool shall be to suit the system. The power tool shall be single speed, provided with a motor of the required rating 0.75 H.P (minimum). The power tool shall be supplied complete with suitable control. The capacity and speed of the electric motor used in the power tool shall be suitable for the lifting of the design load installed on the lantern carriage. The power tool mounting shall be so designed that it will be not only self-supporting but also aligns the power tool perfectly with respect to the winch spindle during the operations. Also, a handle for the manual operation of the winches in case of problems with the electrically operated tool shall be provided and shall incorporate a torque limiting device. The power tool operation shall always be through a separate torque limiting device to protect the wire ropes from over stretching. It shall be mechanical with suitable load adjusting device. The torque limiter shall trip the load when it exceeds the adjusted limits. There shall be suitable provision for warning the operator once the load is tripped off. The torque limiter is a requirement as per the relevant standards in view of the over all safety of the system. Make: Kirloskar/Crompton/Hindustan Electric/Universal company. | 12.00 | No | 10.00 | 28000.00 | 336000.00 | 12716.00 | 152592.00 | 23500.00 | 282000.00 | 20000.00 | 240000.00 | 152592.00 | elektron
7.00 | Stainless steel wire ropes: Supply and Fixing of SS rope of size not less than 8 mm without intermediate joints between winch and lantern carriage, suitable to withstand the load of existing high mast lights of length 25/30 meters height, shall consist of only non-corrodible stainless steel of AISI 316 grade. 7/19 construction, The breaking load of each rope shall not be less than 2350 kg. The end constructions of ropes to the winch drum shall be fitted with talurit. The thimbles shall be secured on ropes by compression splices. The 3 point suspension system shall essentially be without any intermediate joint. Make: Bajaj/Crompton/Wipro. | 910.00 | Mtr | 10.00 | 220.00 | 200200.00 | 223.00 | 202930.00 | 450.00 | 409500.00 | 190.00 | 172900.00 | 172900.00 | RAM ELECTRICALS
8.00 | Stainless steel wire ropes: Supply and Fixing of SS rope of size not less than 6 mm without intermediate joints between winch and lantern carriage, suitable to withstand the load of existing high mast lights of length 12.5 meters height, shall consist of only non-corrodible stainless steel of AISI 316 grade. 7/19 construction, The breaking load of each rope shall not be less than 1400 kg. The end constructions of ropes to the winch drum shall be fitted with talurit. The thimbles shall be secured on ropes by compression splices. The 3 point suspension system shall essentially be without any intermediate joint. Make: Bajaj/Crompton/Wipro. | 780.00 | Mtr | 10.00 | 180.00 | 140400.00 | 159.00 | 124020.00 | 375.00 | 292500.00 | 180.00 | 140400.00 | 124020.00 | elektron
9.00 | Supply and Fixing of high power LED flood lights 500 Watt suitable for stadium lighting purpose. (i). CCT 5000-5500 K (ii). Beam angle 60-90 degrees (iii). Overvoltage and short circuit protection (iv). Optical lens: Polycarbonate high performance type (iv). Warranty – Minimum 5 years (v). Non-corrosive Die cast Al body with angle adjustment clamps with suitable holes to fix at the site (vi). Suitable number of SS nut bolts for fixing purpose. (vii).IP66 protection (viii) Make: Philips/Crompton/Wipro. | 112.00 | No | 10.00 | 32400.00 | 3628800.00 | 28480.00 | 3189760.00 | 19000.00 | 2128000.00 | 27500.00 | 3080000.00 | 2128000.00 | INDUSTRIAL INSTRUMENTS
10.00 | Supply and Fixing of high power LED flood lights 200 Watt (i). CCT 5000-5500 K (ii). IP 66 Protection (iii). Overvoltage and short circuit protection (iv). Optical lens: Polycarbonate high performance type (iv). Warranty – Minimum 5 years (v).Non-corrosive Die cast Al body with angle adjustment clamps with suitable holes to fix at the site (vi). Suitable number of SS nut bolts for fixing purpose. (vii).Make: Philips/Crompton/Wipro. | 40.00 | No | 10.00 | 28000.00 | 1120000.00 | 10995.00 | 439800.00 | 12000.00 | 480000.00 | 13500.00 | 540000.00 | 439800.00 | elektron
11.00 | Supply and Fixing of weather proof outdoor control panel, compartmentalized of suitable size, housing fabricated out of 14 SWG CRCA sheet and finished with two coats of red oxide primer and gray enamel paint at the appropriate location near the high mast pole, canopy at top, hinged door with locking system, suitable holes for cable entry/exit, Legs of suitable length and size grouted in concrete foundation, with suitable number of SP,DP,TPN MCB's at incoming and outgoing along with suitable rating, suitable number of Contactors for control of motor and control of LED Luminaries along with suitable rating, Digital astronomical programmable timer, with circuit for automatic control of luminaries, with voltmeter & ammeter. All necessary equipment and copper wiring for controlling of Electrical motor for raising/lowering mechanism of lantern carriage, with necessary input & output terminals. Including erection on suitable foundation with all necessary civil works. Make of MCB's, Contactor, Timer : Siemens/L&T/Schneider/Havells/Legrand. | 19.00 | No | 10.00 | 28000.00 | 532000.00 | 41140.00 | 781660.00 | 28000.00 | 532000.00 | 42000.00 | 798000.00 | 532000.00 | ANU ELECTRICALS, INDUSTRIAL INSTRUMENTS
12.00 | Suply and fixing of suitable weather proof junction box, confirming to IP 66 protection class or higher, made of cast aluminium, shall be mounted on the lantern carriage as required to facilitate interconnection of designed LED flood light luminaries. | 19.00 | No | 10.00 | 28000.00 | 532000.00 | 5984.00 | 113696.00 | 4500.00 | 85500.00 | 4500.00 | 85500.00 | 85500.00 | INDUSTRIAL INSTRUMENTS, RAM ELECTRICALS
13.00 | Construction of Earth pit station as per IS 3043 standard, with galvanized steel earth plate electrode 60×60cm× 6mm thick, buried directly in ground (earth pit not less than 2.25 meters deep below ground level) with top edge of the plate not less than 1.5 meters below normal ground level, connected to galvanized earth lead wire 4.0 mm dia by means of bolts, nuts, check nuts and washers of galvanized iron or steel connected to earthing test point, with adequate quantity of charcoal and salt, with necessary length of earth continuity conductor GI strip 25X4 mm along with necessary length of GI 40 mm pipe for protecting earth continuity conductor, the earth continuity strip shall be terminated to the earth stud at mast & control panel from earth pit electrode. All metal works shall be bonded to earth studs. a watering pipe of medium class G.I pipe 20 mm shall be provided. The top of the pipe shall be provided with a funnel and a G.I. mesh screen for watering the earth all as specified or indicated including testing on completion. Including civil and masonry works like soil digging, refilling, cement concrete work. | 38.00 | No | 10.00 | 5000.00 | 190000.00 | 16830.00 | 639540.00 | 13000.00 | 494000.00 | 8000.00 | 304000.00 | 190000.00 | ANU ELECTRICALS
14.00 | Aircraft warning lights of reputed make shall be supplied and installed on top of each high mast pole | 19.00 | No | 10.00 | 5000.00 | 95000.00 | 2805.00 | 53295.00 | 7000.00 | 133000.00 | 2500.00 | 47500.00 | 47500.00 | RAM ELECTRICALS
15.00 | Supply and Fixing of lantern carriage, for fixing of LED floodlights(16 No's of 500 Watt)) symmetrically and also have self-balance, It shall be of special design of steel tube construction, joined by bolted flanges with stainless steel bolts &nuts, shall be able to carry out the operation of raising/lowering. shall be hot dip galvanized after fabrication. | 2.00 | No | 10.00 | 50000.00 | 100000.00 | 41140.00 | 82280.00 | 26000.00 | 52000.00 | 38000.00 | 76000.00 | 52000.00 | INDUSTRIAL INSTRUMENTS
16.00 | Supply and Fixing Trailing cable of 5 coreX 4 sq.mm EPR insulated, PCP sheathed, flexible multistrand copper conductor cable Make: Finolex/Havells/Polycab. | 280.00 | Mtr | 10.00 | 150.00 | 42000.00 | 487.00 | 136360.00 | 700.00 | 196000.00 | 280.00 | 78400.00 | 42000.00 | ANU ELECTRICALS
17.00 | Supply and Fixing Trailing cable of 5 coreX 2.5 sq.mm EPR insulated, PCP sheathed, flexible multistrand copper conductor cable Make: Finolex/Havells/Polycab. | 240.00 | Mtr | 10.00 | 100.00 | 24000.00 | 465.00 | 111600.00 | 500.00 | 120000.00 | 225.00 | 54000.00 | 24000.00 | ANU ELECTRICALS
18.00 | Supply and Fixing cable of 3 coreX 1.5 sq.mm PVC, FRLS, flexible multistrand copper conductor cable for interconnection of LED flood lights. Make: Finolex/Havells/Polycab. | 900.00 | Mtr | 10.00 | 19.00 | 17100.00 | 84.00 | 75600.00 | 112.00 | 100800.00 | 140.00 | 126000.00 | 17100.00 | ANU ELECTRICALS
19.00 | Supply and Fixing armoured copper cable of size 4X1.5 sq.mm for motor supply from control panel to the motor shall be supplied by the contractor. It shall be laid under the ground as per the standards. Including excavation and civil works. Make: Finolex/Havells/Polycab. | 100.00 | Mtr | 10.00 | 120.00 | 12000.00 | 188.00 | 18800.00 | 120.00 | 12000.00 | 745.00 | 74500.00 | 12000.00 | ANU ELECTRICALS, INDUSTRIAL INSTRUMENTS
| Total in Figures |  |  |  |  | 8536500.00 |  | 7394926.00 |  | 7707200.00 |  | 8899700.00
Lowest Amount Quoted BY: elektron(7394926.00)

## BOQ Summary
BOQ Summary Details Tender Title: Repair/Overhauling of high mast poles of height 25/30 meters -Quantity-07 Nos and High mast poles of height 12.5 meters Quantity-12 Nos and replacement of conventional flood lights with LED flood lights in OFMK estate. Tender ID: 2023_AVNL_166537_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | elektron | 7394926.00 | L1
| 2 | INDUSTRIAL INSTRUMENTS | 7707200.00 | L2
| 3 | ANU ELECTRICALS | 8536500.00 | L3
| 4 | RAM ELECTRICALS | 8899700.00 | L4