## BoQ1
Government eProcurement System Created By: SRIKANTH GADE Created Date/Time: 31-Jul-2024 09:40 AM Tender Title: Replacement of outlived LT 400 V over head line distribution system with underground cabling system at Ordnance Factory Medak estate area as per the scope of work enclosed at Annexure-A Tender ID: 2023_AVNL_175323_1
Tender Inviting Authority: CHIEF GENERAL MANAGER ORDNANCE FACTORY MEDAK (A UNIT OF AVNL)
Name of Work: Replacement of outlived LT(400V) over head line distribution system with underground cabling system at Ordnance Factory Medak estate area as per the scope of work enclosed at Annexure-A
Contract No: 76025/OFMK/EOC/TE-40/LT 400 V/ 2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | JITENDRA ELECTRICALS (GSTN-24AACFJ9752E1ZE) BID ID -642313 |  | Anil Electrical and Sanitary Goods Stores(GSTN-NA)--644051
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and laying PVC insulated and PVC Sheathed, armoured, heavy duty electric underground cable with aluminium conductor, 1100 volts grade, cross-sectional area 3 1/2 X 120 sq. mm. Type AYFY,Complete all as specified and directed. Make: Finolex/Havells/Polycab/Gloster | 17000.00 | R.M |  | 640.00 | 10880000.00 | 720.00 | 12240000.00 | 10880000.00 | JITENDRA ELECTRICALS
2.00 | Supply and laying PVC insulated and PVC Sheathed, armoured, heavy duty electric underground cable with aluminium conductor, 1100 volts grade, cross-sectional area 3 1/2 X 240 sq. mm.Type AYFY,Complete all as specified and directed. Make: Finolex/Havells/Polycab/Gloster | 12050.00 | R.M |  | 1145.00 | 13797250.00 | 1293.96 | 15592218.00 | 13797250.00 | JITENDRA ELECTRICALS
3.00 | Supply and laying PVC insulated and PVC Sheathed, armoured, heavy duty electric underground cable with aluminium conductor, 1100 volts grade, cross-sectional area 4 X 25 sq. mm.Type AYFY, Complete all as specified and directed. Make: Finolex/Havells/Polycab/Gloster | 60000.00 | R.M |  | 220.00 | 13200000.00 | 269.00 | 16140000.00 | 13200000.00 | JITENDRA ELECTRICALS
4.00 | Supply and laying PVC insulated and PVC Sheathed, armoured, heavy duty electric underground cable with aluminium conductor, 1100 volts grade, cross-sectional area 4 X 35 sq. mm.Type AYFY, Complete all as specified and directed. Make: Finolex/Havells/Polycab/Gloster | 21800.00 | R.M |  | 270.00 | 5886000.00 | 335.00 | 7303000.00 | 5886000.00 | JITENDRA ELECTRICALS
5.00 | Supply and laying PVC insulated and PVC Sheathed, armoured, heavy duty electric underground cable with aluminium conductor, 1100 volts grade, cross-sectional area 2 X 25 sq. mm. Type AYFY, Complete all as specified and directed. Make: Finolex/Havells/Polycab/Gloster | 36300.00 | R.M |  | 145.00 | 5263500.00 | 157.00 | 5699100.00 | 5263500.00 | JITENDRA ELECTRICALS
6.00 | Excavation: Excavating in trenches in hard/dense soil not exceeding 1.5 metre wide and not exceeding 1.5 metre depth and getting out. Complete all as specified and directed. | 28000.00 | CU.M |  | 354.00 | 9912000.00 | 470.00 | 13160000.00 | 9912000.00 | JITENDRA ELECTRICALS
7.00 | Excavation: Excavating in trenches in hard/dense soil exceeding 1.5 metre depth and getting out. Complete all as specified and directed. | 420.00 | CU.M |  | 390.00 | 163800.00 | 500.00 | 210000.00 | 163800.00 | JITENDRA ELECTRICALS
8.00 | Returning, Filling: Returning, filling in, hard/dense soil including spreading, levelling, watering and well ramming in layers not exc 25 cm. Complete all as specified and directed. | 27500.00 | CU.M |  | 45.00 | 1237500.00 | 100.00 | 2750000.00 | 1237500.00 | JITENDRA ELECTRICALS
9.00 | Supply of river sand low grade aggregate. Complete all as specified and directed. | 5200.00 | CU.M |  | 2910.00 | 15132000.00 | 2478.00 | 12885600.00 | 12885600.00 | Anil Electrical and Sanitary Goods Stores
10.00 | Spreading and levelling of sand in layers not exc. 25 cm thick. Complete all as specified and directed. | 5200.00 | CU.M |  | 210.00 | 1092000.00 | 100.00 | 520000.00 | 520000.00 | Anil Electrical and Sanitary Goods Stores
11.00 | Modular Bricks: Supply and Fixing Brick tiles only with subclass ‘B’ bricks, straight or curved on plan to any radius in half brick thick walls. Complete all as specified and directed. | 21000.00 | Sq.M |  | 675.00 | 14175000.00 | 260.00 | 5460000.00 | 5460000.00 | Anil Electrical and Sanitary Goods Stores
12.00 | Modular Brick work with subclass ‘B’ bricks, straight or curved on plan to any radius in half brick thick walls, built in Cement mortar 1:6. Complete all as specified and directed. | 260.00 | Sq.M |  | 2080.00 | 540800.00 | 900.00 | 234000.00 | 234000.00 | Anil Electrical and Sanitary Goods Stores
13.00 | Earthing: Material and Labour for Earthing complete with galvanised steel earth plate electrode 60cmx60cmx6.3mm thick burried directly in ground (earth pit not less than 2.25 M deep below ground level) with top edges of plate not less than 1.5 M below normal ground level, connected to 25mmx4 mm GI strip as earthing lead by means of bolts, nuts, check nuts and washers of GI or steel connected to earthing test point all as specified including testing on completion. Complete all as specified and directed. | 200.00 | Each |  | 8380.00 | 1676000.00 | 5782.00 | 1156400.00 | 1156400.00 | Anil Electrical and Sanitary Goods Stores
14.00 | Earth continuity conductor: Material and Labour for Main earthing lead fixing to wall on batten or recess or chases or buried in around or drawn in conduit pipe or fixing to poles or any other indicating situation for loop earthing etc as required 25mmx4mm GI strip. Complete all as specified and directed. | 800.00 | R.M |  | 240.00 | 192000.00 | 150.78 | 120624.00 | 120624.00 | Anil Electrical and Sanitary Goods Stores
15.00 | Galvanised Steel Tube: Material and labour for galvanised steel tube medium grade 40 mm bore. with screwed socket joints, together with all tube fillings (such as bends, elbows, tees, short pieces, connectors, backnuts, diminishing pieces, caps, plugs and unions, etc.) and fixing complete with clips, wall hooks, wooden plugs, or laying in trenches, etc., also for cutting, screwing and waste and for making forged bends on piping as required. Connectors shall be inserted, where required or directed. The rates also include cutting through walls, floors, etc. and their making good. complete all as specified and directed. | 300.00 | R.M |  | 445.00 | 133500.00 | 481.18 | 144354.00 | 133500.00 | JITENDRA ELECTRICALS
16.00 | Galvanised Steel Tube: Material and labour for galvanised steel tube medium grade 20 mm bore. with screwed socket joints, together with all tube fillings (such as bends, elbows, tees, short pieces, connectors, backnuts, diminishing pieces, caps, plugs and unions, etc.) and fixing complete with clips, wall hooks, wooden plugs, or laying in trenches, etc., also for cutting, screwing and waste and for making forged bends on piping as required. Connectors shall be inserted, where required or directed. The rates also include cutting through walls, floors, etc. and their making good. complete all as specified and directed. | 200.00 | R.M |  | 235.00 | 47000.00 | 180.00 | 36000.00 | 36000.00 | Anil Electrical and Sanitary Goods Stores
17.00 | Galvanised Steel Tube: Material and labour for galvanised steel tube medium grade 50 mm bore. with screwed socket joints, together with all tube fillings (such as bends, elbows, tees, short pieces, connectors, backnuts, diminishing pieces, caps, plugs and unions, etc.) and fixing complete with clips, wall hooks, wooden plugs, or laying in trenches, etc., also for cutting, screwing and waste and for making forged bends on piping as required. Connectors shall be inserted, where required or directed. The rates also include cutting through walls, floors, etc. and their making good. complete all as specified and directed. | 5310.00 | R.M |  | 560.00 | 2973600.00 | 450.00 | 2389500.00 | 2389500.00 | Anil Electrical and Sanitary Goods Stores
18.00 | Supply and Fixing TMT bars, 10mm dia and over, cut to desired length, bent to shape required, including cranking, bending spirally for hooping for columns, hooking ends and binding with and including mild steel wire (annealed) not less than 0.9mm dia or securing with clips. Complete all as specified and directed. | 40.00 | KG |  | 180.00 | 7200.00 | 110.00 | 4400.00 | 4400.00 | Anil Electrical and Sanitary Goods Stores
19.00 | Precast cement concrete: B1 1:2:4 (20mm graded aggregate ) in covers slabs set in cement mortar 1:4 for earth pits with plain faces size (50x50x5cm). Complete all as specified and directed. | 3.00 | CU.M |  | 17700.00 | 53100.00 | 6608.00 | 19824.00 | 19824.00 | Anil Electrical and Sanitary Goods Stores
20.00 | Supply and Fixing Cement concrete type B-1, 1:2:4 (20mm graded aggregate), 100 mm Thickness. Complete all as specified and directed. | 500.00 | Sq.M |  | 975.00 | 487500.00 | 650.00 | 325000.00 | 325000.00 | Anil Electrical and Sanitary Goods Stores
21.00 | Supply and Fixing Stone Walling of squared rubble, regular coursed, well bonded, bedded and solidly hearted, built in cement mortor 1:6. Complete all as specified and directed. | 275.00 | CU.M |  | 8175.00 | 2248125.00 | 6000.00 | 1650000.00 | 1650000.00 | Anil Electrical and Sanitary Goods Stores
22.00 | Walling of squared rubble, regular coursed, well bonded, bedded and solidly hearted, built in cement mortor 1:6 except stone. Complete all as specified and directed. | 200.00 | CU.M |  | 8175.00 | 1635000.00 | 3300.00 | 660000.00 | 660000.00 | Anil Electrical and Sanitary Goods Stores
23.00 | Demolition of Brickwork or stone/boulder masonry, built in cement mortar or cement lime mortar including all quoins, arches, pillars, etc, but excluding ashlar facings, dressed stonework and precast concrete articles.Complete all as specified and directed. | 200.00 | CU.M |  | 4485.00 | 897000.00 | 400.00 | 80000.00 | 80000.00 | Anil Electrical and Sanitary Goods Stores
24.00 | Supply and Fixing flush pointing to squared rubble masonry, coursed or uncoursed in cement mortor 1:4. Complete all as specified and directed. | 150.00 | per 10 Sq.M |  | 3540.00 | 531000.00 | 100.00 | 15000.00 | 15000.00 | Anil Electrical and Sanitary Goods Stores
25.00 | Supply and Fixing Cement concrete in foundations, filling and mass concrete Type D2 1:4:8 (40 mm graded aggregate). Complete all as specified and directed. | 52.00 | CU.M |  | 6490.00 | 337480.00 | 4956.00 | 257712.00 | 257712.00 | Anil Electrical and Sanitary Goods Stores
26.00 | Supply and Fixing Structural steel Fe 410-W(Gde-E- 250) quality-A . Joist, channel, angle, or tee sections,fixed independently, without connecting plates, etc. (cut to ordinary lengths i.e. within 20mm of the length indicated). Complete all as specified and directed. | 9000.00 | KG |  | 160.00 | 1440000.00 | 98.00 | 882000.00 | 882000.00 | Anil Electrical and Sanitary Goods Stores
27.00 | Supply only Chain link MS galvanisd fencing, any size or type. Complete all as specified and directed. | 3000.00 | KG |  | 175.00 | 525000.00 | 140.00 | 420000.00 | 420000.00 | Anil Electrical and Sanitary Goods Stores
28.00 | Fixing only chain link fencing including line wires, any mesh, size and type to any type of standards, rails, straining bolts, etc.including provission of binding wire. Complete all as specified and directed. | 1000.00 | Sq.M |  | 485.00 | 485000.00 | 6.00 | 6000.00 | 6000.00 | Anil Electrical and Sanitary Goods Stores
29.00 | Clamps fabricated from structural steel sections including nuts, bolts, washers, welding, bending cold or hot, drilling holes for bolts, in any shape or size as indicated or directed and inclusive of one primer coat, one under coat and one finishing coat of paint. Complete all as specified and directed. | 30.00 | Per Quintal |  | 17700.00 | 531000.00 | 11571.00 | 347130.00 | 347130.00 | Anil Electrical and Sanitary Goods Stores
30.00 | Demolition of cement concrete(unreinforced) of any description and in any position not otherwise specifically provided for. Complete all as specified and directed. | 150.00 | CU.M |  | 4485.00 | 672750.00 | 1500.00 | 225000.00 | 225000.00 | Anil Electrical and Sanitary Goods Stores
31.00 | Material & Labor for Cement concrete Type B2, 1:2:4, (40 mm graded aggregate) in walls or retaining walls, any thickness, size or shape including pilasters, buttresses columns, pillars, boundary pillars and posts (including caps and bases). Complete all as specified and directed. | 150.00 | CU.M |  | 8615.00 | 1292250.00 | 6000.00 | 900000.00 | 900000.00 | Anil Electrical and Sanitary Goods Stores
32.00 | Supply and Fixing cable route indicators material:Cast Iron, Shape: Round, Size:100 mm dia, angle size, 300mm(L)X25mm(W)X 5mm(Thick), length, Marked as "LT Cable". Complete all as specified and directed. | 5000.00 | Each |  | 470.00 | 2350000.00 | 300.00 | 1500000.00 | 1500000.00 | Anil Electrical and Sanitary Goods Stores
33.00 | Supply and Fixing FRP boxes for fixing to street light poles with Dimensions Minimum of 40 cm(H) X23 cm(W) X 15 cm (D), (1).IP 65 Enclosure: Hot moulded fibre glass reinforced polyster material with non deteriorating Neoprene sponge rubber gasket for dust,water and verminproof ,IP 65 protection, Cover opening shall be on the side with fixed bolt type. (2).Clamping(Brackets 3 mm thickness)- 02 No's, SS brackets suitable for pole dia 190 mm, suitable clamps to be provided at the back side of FRP box also (3).Cable connection bus bar: 25 mm copper bus bar of length 120 mm- 04 No's with 4 no's of M6 tapped hole with 6mm Hexa bolts with screw driver slot , bus bar shall be on porcelain insulators. (4).MCB SP, 2 Amps- 01 No (5). Cable entry at the bottom suitable for 3 1/2x35 Sqmm cable with 3 No's of cable entries with dummies. Complete all as specified and directed. Make: C&C/SINTEX/POWERTECH | 2000.00 | Set |  | 5165.00 | 10330000.00 | 2810.50 | 5621000.00 | 5621000.00 | Anil Electrical and Sanitary Goods Stores
34.00 | Supply and Fixing of 3CX0.75 Sq.MM flexible copper cable on street light pole. Cable to drawn inside the pole. Necessary holes to be made on poles. Complete all as specified and directed. Make: Finolex/Havells/Polycab | 12000.00 | R.M |  | 48.00 | 576000.00 | 60.00 | 720000.00 | 576000.00 | JITENDRA ELECTRICALS
35.00 | Supply and Making End terminations on one side for 4X25 Sq.MM size PVC insulated and sheathed armoured cable with brass compression gland and Aluminium lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 2400.00 | Set |  | 295.00 | 708000.00 | 247.80 | 594720.00 | 594720.00 | Anil Electrical and Sanitary Goods Stores
36.00 | Supply and Making End terminations on one side for 4X35 Sq.MM size PVC insulated and sheathed armoured cable with brass compression gland and Aluminium lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 544.00 | Set |  | 355.00 | 193120.00 | 250.00 | 136000.00 | 136000.00 | Anil Electrical and Sanitary Goods Stores
37.00 | Supply and Making End terminations on one side for 2X25 Sq.MM size PVC insulated and sheathed armoured cable with brass compression gland and Aluminium lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 2400.00 | Set |  | 235.00 | 564000.00 | 200.00 | 480000.00 | 480000.00 | Anil Electrical and Sanitary Goods Stores
38.00 | Supply and Making End terminations on one side for 3 1/2X120 Sq.MM size PVC insulated and sheathed armoured cable with brass compression gland and Aluminium lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 220.00 | Set |  | 825.00 | 181500.00 | 800.00 | 176000.00 | 176000.00 | Anil Electrical and Sanitary Goods Stores
39.00 | Supply and Making End terminations on one side for 3 1/2X240 Sq.MM size PVC insulated and sheathed armoured cable with brass compression gland and Aluminium lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 80.00 | Set |  | 1180.00 | 94400.00 | 1500.00 | 120000.00 | 94400.00 | JITENDRA ELECTRICALS
40.00 | Supply and Making End terminations on one side for 3 X0.75 Sq.MM size copper flexible cable with copper lugs. Complete all as specified and directed. Make of Lugs: Dowells/Jainson/PPI | 1200.00 | Set |  | 30.00 | 36000.00 | 99.00 | 118800.00 | 36000.00 | JITENDRA ELECTRICALS
41.00 | Supply and laying of Under ground electric cables warning tape , 6 inch width, made of HDPE material, 35 micron, 0.5 mm thickmess, Yellow color, text to be printed as "CAUTION ELECTRIC CABLE BELOW". Complete all as specified and directed. Make: TOOLZONE/SINGHAL/ SVWCI/ WARNMAT | 42000.00 | R.M |  | 15.00 | 630000.00 | 18.52 | 777840.00 | 630000.00 | JITENDRA ELECTRICALS
42.00 | Horizontal directional drilling: Horizontal directional drilling of 150 mm dia bore size, at the road crossings of various lengths without disturbing the surface of the road, Necessary duct and cable to be pulled through bore. It also includes jointing work of pipes along with necessary accessories if required. at various locations as advised by EIC/SIC. Complete all as specified and directed. | 2200.00 | R.M |  | 885.00 | 1947000.00 | 2478.00 | 5451600.00 | 1947000.00 | JITENDRA ELECTRICALS
43.00 | Supply and Fixing of DWC electrical pipe, Outer dia 125mm, Inner dia 107mm, Material: HDPE,Orange color, shall have corrugation on outer wall but inner wall shall be plain confirming to IS:14930 part I & II(amended from time to time). used as burried underground conduit. ISI marked. Necessary jointing work along with accessories like HDPE snap fit coupler with neoprene 'O' ring to make joints shall be part of supply for water/damp proof.Complete all as specified and directed. Make: Crown/Duke/Texmo | 2200.00 | R.M |  | 170.00 | 374000.00 | 202.44 | 445368.00 | 374000.00 | JITENDRA ELECTRICALS
44.00 | Supply and Fixing of ICTPN (Iron clad 3 pole & neutral) switch, 400Amps, with HRC fuses of rating 250A. Make: HPL/SPUTNIK/BENLO | 20.00 | Each |  | 29115.00 | 582300.00 | 25650.00 | 513000.00 | 513000.00 | Anil Electrical and Sanitary Goods Stores
45.00 | Supply, Installation, Testing and commissioning of outdoor feeder pillar panel.I/C-1 & O/G-14 feeders as per the specification sheet enclosed at ANNEXURE 'B'. Complete all as specified and directed. | 25.00 | Set |  | 421000.00 | 10525000.00 | 610492.85 | 15262321.25 | 10525000.00 | JITENDRA ELECTRICALS
46.00 | Supply, Installation, Testing and commissioning of outdoor feeder pillar panel.I/C-1 & O/G-16 feeders as per the specification sheet enclosed at ANNEXURE 'C'. Complete all as specified and directed. | 41.00 | Set |  | 480500.00 | 19700500.00 | 647173.86 | 26534128.26 | 19700500.00 | JITENDRA ELECTRICALS
47.00 | Supply, Installation, Testing and commissioning of outdoor feeder pillar panel.I/C-1 & O/G-18 feeders as per the specification sheet enclosed at ANNEXURE 'D'. Complete all as specified and directed. | 7.00 | Set |  | 555000.00 | 3885000.00 | 720000.00 | 5040000.00 | 3885000.00 | JITENDRA ELECTRICALS
48.00 | Supply, Installation, Testing and commissioning of outdoor feeder pillar panel.I/C-1 & O/G-20 feeders as per the specification sheet enclosed at ANNEXURE 'E'. Complete all as specified and directed. | 3.00 | Set |  | 592000.00 | 1776000.00 | 730000.00 | 2190000.00 | 1776000.00 | JITENDRA ELECTRICALS
49.00 | Supply, Installation, Testing and commissioning of outdoor Street light feeder pillar panel as per the specification sheet enclosed at ANNEXURE 'F'. Complete all as specified and directed. | 10.00 | Set |  | 159000.00 | 1590000.00 | 265000.00 | 2650000.00 | 1590000.00 | JITENDRA ELECTRICALS
| Total in Figures |  |  |  |  | 163487175.00 |  | 170163639.51
Lowest Amount Quoted BY: JITENDRA ELECTRICALS(163487175.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of outlived LT 400 V over head line distribution system with underground cabling system at Ordnance Factory Medak estate area as per the scope of work enclosed at Annexure-A Tender ID: 2023_AVNL_175323_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | JITENDRA ELECTRICALS | 163487175.00 | L1
| 2 | Anil Electrical and Sanitary Goods Stores | 170163639.51 | L2