## BoQ1
Government eProcurement System Created By: BISHAR BIN ALI Created Date/Time: 23-Sep-2023 05:00 PM Tender Title: HIRING OF CONTRACT FOR MITIGATION WORKS FOR LIGHTNING PROTECTION SYSTEM OF DBPL PIPELINE INCLUDING SPUR LINE INSTALLATIONS Tender ID: 2023_GAIL_163218_1
Tender Inviting Authority: GAIL INDIA LIMITED
Name of Work: HIRING OF CONTRACT FOR MITIGATION WORKS FOR LIGHTNING PROTECTION SYSTEM OF DBPL PIPELINE INCLUDING SPUR LINE INSTALLATIONS
Tender No: 2023_GAIL_163218
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEHN INDIA PVT. LTD.(GSTN-06AADCD9928J1ZA) |  | JEF Techno Solutions Private Limited(GSTN-29AAACJ2639M1Z7)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Mitigation works for Lightning Protection System at GAIL, DBPL; BELGAUM O&M BASE: KARNATAKA
1.01 | Supply & Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 22.00 | Nos |  | 2000.00 | 44000.00 | 2090.00 | 45980.00 | 44000.00 | DEHN INDIA PVT. LTD.
1.02 | Supply & installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 20.00 | Nos |  | 3000.00 | 60000.00 | 3990.00 | 79800.00 | 60000.00 | DEHN INDIA PVT. LTD.
1.03 | Supply & installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 55.00 | Mtr |  | 145.00 | 7975.00 | 145.70 | 8013.50 | 7975.00 | DEHN INDIA PVT. LTD.
1.04 | Supply& installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 55.00 | Nos |  | 110.00 | 6050.00 | 77.00 | 4235.00 | 4235.00 | JEF Techno Solutions Private Limited
1.05 | Supply and installation of Expansion Piece without connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations to be provided on conductors length over 20 meters to connect Solid Round Al. Conductor at both ends to meet the requirements of IS/IEC 62305 | 4.00 | Nos |  | 440.00 | 1760.00 | 400.00 | 1600.00 | 1600.00 | JEF Techno Solutions Private Limited
1.06 | Supply and installation of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 8.00 | Nos |  | 205.00 | 1640.00 | 304.00 | 2432.00 | 1640.00 | DEHN INDIA PVT. LTD.
1.07 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 100.00 | Mtr |  | 145.00 | 14500.00 | 145.70 | 14570.00 | 14500.00 | DEHN INDIA PVT. LTD.
1.08 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 100.00 | Nos |  | 110.00 | 11000.00 | 77.00 | 7700.00 | 7700.00 | JEF Techno Solutions Private Limited
1.09 | Supply and installation of Cross splicer should be ttested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 8.00 | Nos |  | 205.00 | 1640.00 | 454.00 | 3632.00 | 1640.00 | DEHN INDIA PVT. LTD.
1.10 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 14.00 | Nos |  | 500.00 | 7000.00 | 1625.00 | 22750.00 | 7000.00 | DEHN INDIA PVT. LTD.
1.11 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 140.00 | Mtr |  | 225.00 | 31500.00 | 418.00 | 58520.00 | 31500.00 | DEHN INDIA PVT. LTD.
1.12 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 28.00 | Nos |  | 210.00 | 5880.00 | 62.50 | 1750.00 | 1750.00 | JEF Techno Solutions Private Limited
1.13 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 18.00 | Nos |  | 500.00 | 9000.00 | 902.50 | 16245.00 | 9000.00 | DEHN INDIA PVT. LTD.
1.14 | Supply and installation of Earth Electrode Cu Bonded Steel Rod 14.2mm dia x 3000mm-(250Microns);Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height).;14.2 / OD SS Clamp Both Side; Eco Safe carbon based backfill compound - 50 Pounds. | 3.00 | Set |  | 10600.00 | 31800.00 | 17060.00 | 51180.00 | 31800.00 | DEHN INDIA PVT. LTD.
1.15 | Supply and installation of SPD 415VAC | 5.00 | EA |  | 10100.00 | 50500.00 | 33250.00 | 166250.00 | 50500.00 | DEHN INDIA PVT. LTD.
1.16 | Supply and installation of SPD 230VAC | 1.00 | EA |  | 5850.00 | 5850.00 | 25750.00 | 25750.00 | 5850.00 | DEHN INDIA PVT. LTD.
2.00 | CHITRADURGA BASE: KARNATAKA
2.01 | Supply and Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 28.00 | Nos. |  | 2000.00 | 56000.00 | 2090.00 | 58520.00 | 56000.00 | DEHN INDIA PVT. LTD.
2.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 28.00 | Nos |  | 3000.00 | 84000.00 | 3990.00 | 111720.00 | 84000.00 | DEHN INDIA PVT. LTD.
2.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 105.00 | Mtr |  | 145.00 | 15225.00 | 145.70 | 15298.50 | 15225.00 | DEHN INDIA PVT. LTD.
2.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 105.00 | Nos |  | 110.00 | 11550.00 | 77.00 | 8085.00 | 8085.00 | JEF Techno Solutions Private Limited
2.05 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 14.00 | Nos |  | 500.00 | 7000.00 | 1625.00 | 22750.00 | 7000.00 | DEHN INDIA PVT. LTD.
2.06 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground level Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 140.00 | Mtr |  | 225.00 | 31500.00 | 1625.00 | 227500.00 | 31500.00 | DEHN INDIA PVT. LTD.
2.07 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 28.00 | Nos |  | 210.00 | 5880.00 | 62.50 | 1750.00 | 1750.00 | JEF Techno Solutions Private Limited
2.08 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 16.00 | Nos |  | 500.00 | 8000.00 | 902.50 | 14440.00 | 8000.00 | DEHN INDIA PVT. LTD.
2.09 | Supply and installation of SPD 415VAC | 7.00 | EA |  | 10100.00 | 70700.00 | 33250.00 | 232750.00 | 70700.00 | DEHN INDIA PVT. LTD.
2.10 | Supply and installation of SPD 230VAC | 3.00 | EA |  | 5850.00 | 17550.00 | 25750.00 | 77250.00 | 17550.00 | DEHN INDIA PVT. LTD.
3.00 | HUBLI BASE: KARNATAKA
3.01 | Supply and Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 22.00 | Nos. |  | 2000.00 | 44000.00 | 2090.00 | 45980.00 | 44000.00 | DEHN INDIA PVT. LTD.
3.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 20.00 | Nos |  | 3000.00 | 60000.00 | 3990.00 | 79800.00 | 60000.00 | DEHN INDIA PVT. LTD.
3.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 90.00 | Mtr |  | 145.00 | 13050.00 | 145.70 | 13113.00 | 13050.00 | DEHN INDIA PVT. LTD.
3.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 90.00 | Nos |  | 110.00 | 9900.00 | 77.00 | 6930.00 | 6930.00 | JEF Techno Solutions Private Limited
3.05 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 12.00 | Nos |  | 500.00 | 6000.00 | 1625.00 | 19500.00 | 6000.00 | DEHN INDIA PVT. LTD.
3.06 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 120.00 | Mtr |  | 225.00 | 27000.00 | 418.00 | 50160.00 | 27000.00 | DEHN INDIA PVT. LTD.
3.07 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 24.00 | Nos |  | 210.00 | 5040.00 | 62.50 | 1500.00 | 1500.00 | JEF Techno Solutions Private Limited
3.08 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 14.00 | Nos |  | 500.00 | 7000.00 | 902.50 | 12635.00 | 7000.00 | DEHN INDIA PVT. LTD.
3.09 | Supply and installation of SPD 415VAC | 7.00 | EA |  | 10100.00 | 70700.00 | 33250.00 | 232750.00 | 70700.00 | DEHN INDIA PVT. LTD.
4.00 | BIDADI BASE - KARNATAKA
4.01 | Supply and Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 20.00 | Nos. |  | 2000.00 | 40000.00 | 2090.00 | 41800.00 | 40000.00 | DEHN INDIA PVT. LTD.
4.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 13.00 | Nos |  | 3000.00 | 39000.00 | 3990.00 | 51870.00 | 39000.00 | DEHN INDIA PVT. LTD.
4.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 90.00 | Mtr |  | 145.00 | 13050.00 | 145.70 | 13113.00 | 13050.00 | DEHN INDIA PVT. LTD.
4.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 90.00 | Nos |  | 110.00 | 9900.00 | 77.00 | 6930.00 | 6930.00 | JEF Techno Solutions Private Limited
4.05 | Supply and installation of Expansion Piece without connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations to be provided on conductors length over 20 meters to connect Solid Round Al. Conductor at both ends to meet the requirements of IS/IEC 62305 | 5.00 | Nos |  | 440.00 | 2200.00 | 400.00 | 2000.00 | 2000.00 | JEF Techno Solutions Private Limited
4.06 | Supply and installation of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 10.00 | Nos |  | 205.00 | 2050.00 | 304.00 | 3040.00 | 2050.00 | DEHN INDIA PVT. LTD.
4.07 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305;Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 112.00 | Mtr |  | 145.00 | 16240.00 | 145.70 | 16318.40 | 16240.00 | DEHN INDIA PVT. LTD.
4.08 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited third party laboratory to meet the requirement of IS/ IEC 62305 | 112.00 | Nos |  | 110.00 | 12320.00 | 77.00 | 8624.00 | 8624.00 | JEF Techno Solutions Private Limited
4.09 | Supply & Installation of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 2.00 | Nos |  | 205.00 | 410.00 | 304.00 | 608.00 | 410.00 | DEHN INDIA PVT. LTD.
4.10 | Supply and installation of Cross splicer should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 6.00 | Nos |  | 205.00 | 1230.00 | 454.00 | 2724.00 | 1230.00 | DEHN INDIA PVT. LTD.
4.11 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 16.00 | Nos |  | 500.00 | 8000.00 | 1625.00 | 26000.00 | 8000.00 | DEHN INDIA PVT. LTD.
4.12 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground level Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 155.00 | Mtr |  | 225.00 | 34875.00 | 418.00 | 64790.00 | 34875.00 | DEHN INDIA PVT. LTD.
4.13 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 32.00 | Nos |  | 210.00 | 6720.00 | 62.50 | 2000.00 | 2000.00 | JEF Techno Solutions Private Limited
4.14 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 21.00 | Nos |  | 500.00 | 10500.00 | 902.50 | 18952.50 | 10500.00 | DEHN INDIA PVT. LTD.
4.15 | Supply and installation of Earth Electrode Cu Bonded Steel Rod 14.2mm dia x 3000mm-(250Microns);Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height).;14.2 / OD SS Clamp Both Side; Eco Safe carbon based backfill compound - 50 Pounds. | 2.00 | Set |  | 10600.00 | 21200.00 | 17060.00 | 34120.00 | 21200.00 | DEHN INDIA PVT. LTD.
4.16 | Supply and installation of SPD 415VAC | 5.00 | EA |  | 10100.00 | 50500.00 | 33250.00 | 166250.00 | 50500.00 | DEHN INDIA PVT. LTD.
4.17 | Supply and installation of SPD 230VAC | 2.00 | EA |  | 5850.00 | 11700.00 | 25750.00 | 51500.00 | 11700.00 | DEHN INDIA PVT. LTD.
5.00 | BANGALORE BASE- KARNATAKA
5.01 | Supply and installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 15.00 | Nos. |  | 2000.00 | 30000.00 | 2090.00 | 31350.00 | 30000.00 | DEHN INDIA PVT. LTD.
5.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement; | 15.00 | Nos |  | 3000.00 | 45000.00 | 3990.00 | 59850.00 | 45000.00 | DEHN INDIA PVT. LTD.
5.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305; | 459.00 | Mtr |  | 145.00 | 66555.00 | 145.70 | 66876.30 | 66555.00 | DEHN INDIA PVT. LTD.
5.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 459.00 | Nos |  | 110.00 | 50490.00 | 77.00 | 35343.00 | 35343.00 | JEF Techno Solutions Private Limited
5.05 | Supply and installation of Expansion Piece without connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations to be provided on conductors length over 20 meters to connect Solid Round Al. Conductor at both ends to meet the requirements of IS/IEC 62305 | 25.00 | Nos |  | 440.00 | 11000.00 | 380.00 | 9500.00 | 9500.00 | JEF Techno Solutions Private Limited
5.06 | Supply and installation of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 50.00 | Nos |  | 205.00 | 10250.00 | 304.00 | 15200.00 | 10250.00 | DEHN INDIA PVT. LTD.
5.07 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated third party laboratory to meet the requirement of IS/ IEC 62305 | 249.00 | Mtr |  | 145.00 | 36105.00 | 145.70 | 36279.30 | 36105.00 | DEHN INDIA PVT. LTD.
5.08 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 249.00 | Nos |  | 110.00 | 27390.00 | 67.00 | 16683.00 | 16683.00 | JEF Techno Solutions Private Limited
5.09 | Supply and installation of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 9.00 | Nos |  | 205.00 | 1845.00 | 304.00 | 2736.00 | 1845.00 | DEHN INDIA PVT. LTD.
5.10 | Supply and installation of Cross splicer should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 20.00 | Nos |  | 205.00 | 4100.00 | 454.00 | 9080.00 | 4100.00 | DEHN INDIA PVT. LTD.
5.11 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 27.00 | Nos |  | 500.00 | 13500.00 | 1625.00 | 43875.00 | 13500.00 | DEHN INDIA PVT. LTD.
5.12 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding | 482.00 | Mtr |  | 225.00 | 108450.00 | 418.00 | 201476.00 | 108450.00 | DEHN INDIA PVT. LTD.
5.13 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip | 54.00 | Nos |  | 210.00 | 11340.00 | 62.50 | 3375.00 | 3375.00 | JEF Techno Solutions Private Limited
5.14 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305 | 24.00 | Nos |  | 500.00 | 12000.00 | 902.50 | 21660.00 | 12000.00 | DEHN INDIA PVT. LTD.
5.15 | Supply and installation of Earth Electrode Cu Bonded Steel Rod 14.2mm dia x 3000mm-(250Microns);Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height).;14.2 / OD SS Clamp Both Side;Jef Eco Safe carbon based backfill compound - 50 Pounds | 10.00 | Set |  | 10600.00 | 106000.00 | 17060.00 | 170600.00 | 106000.00 | DEHN INDIA PVT. LTD.
5.16 | Supply and installation of Pipe type Clamp Holder -SS-Round for fixing conductor on pipe to meet the requirements of IS /IEC 62305 -3 | 90.00 | Nos |  | 750.00 | 67500.00 | 955.00 | 85950.00 | 67500.00 | DEHN INDIA PVT. LTD.
5.17 | Supply and installation of Standing Seam clamp :To hold 8 mm Al conductor at every 1m dist on the top roof without any drilling on roof , Installation can be made through simple fastening system ,mainly used for seaming sheet roof application tested as per IEC-62561-2 for conditioning & Ageing test & conducted in the Govt. accredited Third party laboratory to meet the requirements of IS/IEC 62305 | 324.00 | Mtr |  | 150.00 | 48600.00 | 292.00 | 94608.00 | 48600.00 | DEHN INDIA PVT. LTD.
5.18 | Supply and installation of Special standing seam fixureClamp for Air terminal on Metal Structure -Site specific | 2.00 | Nos |  | 750.00 | 1500.00 | 4750.00 | 9500.00 | 1500.00 | DEHN INDIA PVT. LTD.
5.19 | Supply and installation of SPD 415VAC | 9.00 | EA |  | 10100.00 | 90900.00 | 33250.00 | 299250.00 | 90900.00 | DEHN INDIA PVT. LTD.
5.20 | Supply and installation of SPD 230VAC | 1.00 | EA |  | 5850.00 | 5850.00 | 25750.00 | 25750.00 | 5850.00 | DEHN INDIA PVT. LTD.
6.00 | Mitigation works for Lightning Protection System at GAIL, DBPL. GOA BASE
6.01 | Supply and Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 22.00 | Nos. |  | 2000.00 | 44000.00 | 2090.00 | 45980.00 | 44000.00 | DEHN INDIA PVT. LTD.
6.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 22.00 | Nos |  | 3000.00 | 66000.00 | 3990.00 | 87780.00 | 66000.00 | DEHN INDIA PVT. LTD.
6.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 110.00 | Mtr |  | 145.00 | 15950.00 | 145.70 | 16027.00 | 15950.00 | DEHN INDIA PVT. LTD.
6.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 110.00 | Nos |  | 110.00 | 12100.00 | 77.00 | 8470.00 | 8470.00 | JEF Techno Solutions Private Limited
6.05 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 15.00 | Nos |  | 500.00 | 7500.00 | 1625.00 | 24375.00 | 7500.00 | DEHN INDIA PVT. LTD.
6.06 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 150.00 | Mtr |  | 225.00 | 33750.00 | 418.00 | 62700.00 | 33750.00 | DEHN INDIA PVT. LTD.
6.07 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 30.00 | Nos |  | 210.00 | 6300.00 | 62.50 | 1875.00 | 1875.00 | JEF Techno Solutions Private Limited
6.08 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 15.00 | Nos |  | 500.00 | 7500.00 | 902.50 | 13537.50 | 7500.00 | DEHN INDIA PVT. LTD.
6.09 | Supply and installation of Earth Electrode Cu Bonded Steel Rod 14.2mm dia x 3000mm-(250Microns);Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height).;14.2 / OD SS Clamp Both Side; Eco Safe carbon based backfill compound - 50 Pounds. | 1.00 | Set |  | 10600.00 | 10600.00 | 17060.00 | 17060.00 | 10600.00 | DEHN INDIA PVT. LTD.
6.10 | Supply and installation of SPD 415VAC | 5.00 | EA |  | 10100.00 | 50500.00 | 33250.00 | 166250.00 | 50500.00 | DEHN INDIA PVT. LTD.
6.11 | Supply and installation of SPD 230VAC | 2.00 | EA |  | 5850.00 | 11700.00 | 25750.00 | 51500.00 | 11700.00 | DEHN INDIA PVT. LTD.
7.00 | Mitigation works for Lightning Protection System at GAIL, DBPL; DABHOL & KOLHAPUR BASE: MAHARASHTRA
7.01 | Supply and Installation of Vertical Air Termination Solid Aluminium with base- 16 mm dia and 1000 mm long. Air Terminal Base should be tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | 33.00 | Nos. |  | 2000.00 | 66000.00 | 2090.00 | 68970.00 | 66000.00 | DEHN INDIA PVT. LTD.
7.02 | Supply and installation of Vertical Air Terminal of 1 Mtr Mast consisting of Air Terminal with base 34 mm dia and 1000 mm length GI Mast with base plate suitable for mounting on concrete / RCC roof Suitable for high wind load .Mounting arrangement may vary based on site requirement. | 33.00 | Nos |  | 3000.00 | 99000.00 | 3990.00 | 131670.00 | 99000.00 | DEHN INDIA PVT. LTD.
7.03 | Supply and installation of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | 150.00 | Mtr |  | 145.00 | 21750.00 | 145.70 | 21855.00 | 21750.00 | DEHN INDIA PVT. LTD.
7.04 | Supply and installation of Al conductor holding clamp suitable for fixing 8 mm ,.Conductor holder @ 1 meter distance should be tested as per IEC-62561-2 conditioning & Ageing test, conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/ IEC 62305 | 150.00 | Nos |  | 110.00 | 16500.00 | 77.00 | 11550.00 | 11550.00 | JEF Techno Solutions Private Limited
7.05 | Supply and installation of Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | 20.00 | Nos |  | 500.00 | 10000.00 | 1625.00 | 32500.00 | 10000.00 | DEHN INDIA PVT. LTD.
7.06 | Supply and installation of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground level Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding. | 335.00 | Mtr |  | 225.00 | 75375.00 | 418.00 | 140030.00 | 75375.00 | DEHN INDIA PVT. LTD.
7.07 | Supply and installation Holder -GI for fixing 25 x 6 mm GI Strip; | 38.00 | Nos |  | 210.00 | 7980.00 | 62.50 | 2375.00 | 2375.00 | JEF Techno Solutions Private Limited
7.08 | Supply and installation of connector -To connect air terminal 8-10 mm with earth fixing point to meet the requirements of IS/IEC 62305; | 20.00 | Nos |  | 500.00 | 10000.00 | 902.00 | 18040.00 | 10000.00 | DEHN INDIA PVT. LTD.
7.09 | Supply and installation of Earth Electrode Cu Bonded Steel Rod 14.2mm dia x 3000mm-(250Microns);Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height).;14.2 / OD SS Clamp Both Side; Eco Safe carbon based backfill compound - 50 Pounds. | 2.00 | Set |  | 10600.00 | 21200.00 | 17060.00 | 34120.00 | 21200.00 | DEHN INDIA PVT. LTD.
7.10 | Supply and installation of SPD 415VAC | 11.00 | EA |  | 10100.00 | 111100.00 | 33250.00 | 365750.00 | 111100.00 | DEHN INDIA PVT. LTD.
7.11 | Supply and installation of SPD 230VAC | 2.00 | EA |  | 5850.00 | 11700.00 | 25750.00 | 51500.00 | 11700.00 | DEHN INDIA PVT. LTD.
| Total in Figures |  |  |  |  | 2584965.00 |  | 4866335.00
Lowest Amount Quoted BY: DEHN INDIA PVT. LTD.(2584965.00)

## BOQ Summary
BOQ Summary Details Tender Title: HIRING OF CONTRACT FOR MITIGATION WORKS FOR LIGHTNING PROTECTION SYSTEM OF DBPL PIPELINE INCLUDING SPUR LINE INSTALLATIONS Tender ID: 2023_GAIL_163218_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DEHN INDIA PVT. LTD. | 2584965.00 | L1
| 2 | JEF Techno Solutions Private Limited | 4866335.00 | L2