## BoQ1
Government eProcurement System Created By: RAKESH SHARMA Created Date/Time: 30-Nov-2023 12:06 PM Tender Title: MECHANICAL AND ELECTRICAL WORKS FOR CONSTRUCTION OF CNG STATIONS AT BHUBANESHWAR AND CUTTACK GEOGRAPHICAL AREAS 2 YEARS ARC Tender ID: 2023_GAIL_166479_1
Tender Inviting Authority: Owner -GAIL (India) Ltd.; EPMC- MECON Ltd.
Name of Work: TENDER DOCUMENT FOR MECHANICAL AND ELECTRICAL WORKS FOR CONSTRUCTION OF CNG STATIONS AT BHUBANESHWAR AND CUTTACK GEOGRAPHICAL AREAS (2 YEARS ARC)
Tender No: 05/51/Q7NT/GAIL/001-iv-09
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RAJ CONSTRUCTION(GSTN-09AAIFR3131M1ZY) |  | NOPS INFRASTRUCTURE PVT. LTD.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Mechanical & Piping Works
2.00 | SECTION-A : SS TUBE & FITTING - SUPPLY, LAYING & TESTING
3.00 | Laying, testing and commissioning of SS tubes along with fittings as per Technical Specification, Typical P & ID for type of CNG station and scope of work including handling, lifting, transportation from stores to CNG stations.
4.00 | ¾”OD X 0.095” min Wall thk. SS Tube (Refer TS Section III - A) | 2890.00 | RM |  | 500.00 | 1445000.00 | 600.00 | 1734000.00 | 1445000.00 | RAJ CONSTRUCTION
5.00 | ½”OD X 0.083” min Wall thk. SS Tube (Refer TS Section III - A) | 297.00 | RM |  | 450.00 | 133650.00 | 600.00 | 178200.00 | 133650.00 | RAJ CONSTRUCTION
6.00 | SUPPLY OF SS TUBES as per Technical Specification
7.00 | ¾”OD X 0.095” min Wall thk.,Material SS316SS Tube (Refer TS Section III - A) | 288.00 | RM |  | 1750.00 | 504000.00 | 2200.00 | 633600.00 | 504000.00 | RAJ CONSTRUCTION
8.00 | ½”OD X 0.083” min Wall thk.,Material SS316 SS Tube (Refer TS Section III - A) | 36.00 | RM |  | 1700.00 | 61200.00 | 1900.00 | 68400.00 | 61200.00 | RAJ CONSTRUCTION
9.00 | Note: Quantities beyond mentioned quantities may be provided as free issue.
10.00 | Supply of SS Fittings,Valves
11.00 | Quick Connect Body & Stem
12.00 | End connection:½" Tube OD, for stem & ½”NPT (F) for body Material : SS316; Rated pressure : 5000 PSI @ 70°F Temperature: 0°F to 400°F | 25.00 | Nos. |  | 8500.00 | 212500.00 | 7000.00 | 175000.00 | 175000.00 | NOPS INFRASTRUCTURE PVT. LTD.
13.00 | Plug
14.00 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 1500.00 | 37500.00 | 475.00 | 11875.00 | 11875.00 | NOPS INFRASTRUCTURE PVT. LTD.
15.00 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 51.00 | Nos. |  | 1800.00 | 91800.00 | 885.00 | 45135.00 | 45135.00 | NOPS INFRASTRUCTURE PVT. LTD.
16.00 | Caps
17.00 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 1200.00 | 30000.00 | 548.00 | 13700.00 | 13700.00 | NOPS INFRASTRUCTURE PVT. LTD.
18.00 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 127.00 | Nos. |  | 1800.00 | 228600.00 | 881.00 | 111887.00 | 111887.00 | NOPS INFRASTRUCTURE PVT. LTD.
19.00 | Union
20.00 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 595.00 | Nos. |  | 2850.00 | 1695750.00 | 1782.00 | 1060290.00 | 1060290.00 | NOPS INFRASTRUCTURE PVT. LTD.
21.00 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 51.00 | Nos. |  | 1450.00 | 73950.00 | 1135.00 | 57885.00 | 57885.00 | NOPS INFRASTRUCTURE PVT. LTD.
22.00 | Reducing Union
23.00 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 119.00 | Nos. |  | 2750.00 | 327250.00 | 1833.00 | 218127.00 | 218127.00 | NOPS INFRASTRUCTURE PVT. LTD.
24.00 | Equal Tee
25.00 | Size:½” OD x ½” OD x ½” OD, Material:SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 8.00 | Nos. |  | 3000.00 | 24000.00 | 7000.00 | 56000.00 | 24000.00 | RAJ CONSTRUCTION
26.00 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 ( Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 76.00 | Nos. |  | 4500.00 | 342000.00 | 4026.00 | 305976.00 | 305976.00 | NOPS INFRASTRUCTURE PVT. LTD.
27.00 | Reducing Union Tee
28.00 | ¾" OD x ½" OD x ¾" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 8.00 | Nos. |  | 5050.00 | 40400.00 | 6500.00 | 52000.00 | 40400.00 | RAJ CONSTRUCTION
29.00 | Tube End Connection
30.00 | ½” Tube End & ¾” OD with Ferrule Fitting, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 102.00 | Nos. |  | 2450.00 | 249900.00 | 4000.00 | 408000.00 | 249900.00 | RAJ CONSTRUCTION
31.00 | Nut
32.00 | ¾ " OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 51.00 | Nos. |  | 700.00 | 35700.00 | 430.00 | 21930.00 | 21930.00 | NOPS INFRASTRUCTURE PVT. LTD.
33.00 | ½" OD, Material : SS316(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 600.00 | 15000.00 | 240.00 | 6000.00 | 6000.00 | NOPS INFRASTRUCTURE PVT. LTD.
34.00 | Front Ferrule
35.00 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 51.00 | Nos. |  | 305.00 | 15555.00 | 190.00 | 9690.00 | 9690.00 | NOPS INFRASTRUCTURE PVT. LTD.
36.00 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 250.00 | 6250.00 | 130.00 | 3250.00 | 3250.00 | NOPS INFRASTRUCTURE PVT. LTD.
37.00 | Back Ferrule
38.00 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 51.00 | Nos. |  | 285.00 | 14535.00 | 275.00 | 14025.00 | 14025.00 | NOPS INFRASTRUCTURE PVT. LTD.
39.00 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 220.00 | 5500.00 | 110.00 | 2750.00 | 2750.00 | NOPS INFRASTRUCTURE PVT. LTD.
40.00 | Male Connector
41.00 | Size ¼” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 8.00 | Nos. |  | 1500.00 | 12000.00 | 589.00 | 4712.00 | 4712.00 | NOPS INFRASTRUCTURE PVT. LTD.
42.00 | Size 1/2” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 25.00 | Nos. |  | 1500.00 | 37500.00 | 790.00 | 19750.00 | 19750.00 | NOPS INFRASTRUCTURE PVT. LTD.
43.00 | Cross
44.00 | 3/4" OD X 3/4” X 3/4" OD X3/4" OD Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | 8.00 | Nos. |  | 7000.00 | 56000.00 | 12087.00 | 96696.00 | 56000.00 | RAJ CONSTRUCTION
45.00 | SS Ball Valves, conforming to MECON’s Technical Specification No. MEC/TS/05/62/048 for SS Ball Valves of following sizes, specifications as indicated below :
46.00 | 2-Way Trunnion Full Bore Ball Valve ¾" | 8.00 | Nos. |  | 15000.00 | 120000.00 | 22000.00 | 176000.00 | 120000.00 | RAJ CONSTRUCTION
47.00 | 2-Way Floating Full Bore Ball Valve ¾" | 382.00 | Nos. |  | 15500.00 | 5921000.00 | 20000.00 | 7640000.00 | 5921000.00 | RAJ CONSTRUCTION
48.00 | 2-Way Trunnion Full Bore Ball Valve ½" | 8.00 | Nos. |  | 15000.00 | 120000.00 | 20000.00 | 160000.00 | 120000.00 | RAJ CONSTRUCTION
49.00 | 2-Way Floating Full Bore Ball Valve ½" | 119.00 | Nos. |  | 15000.00 | 1785000.00 | 18000.00 | 2142000.00 | 1785000.00 | RAJ CONSTRUCTION
50.00 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection | 8.00 | Nos. |  | 17500.00 | 140000.00 | 30000.00 | 240000.00 | 140000.00 | RAJ CONSTRUCTION
51.00 | Conductive Core Thermoplastic Hose
52.00 | 3/8” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling | 8.00 | Nos. |  | 55000.00 | 440000.00 | 85000.00 | 680000.00 | 440000.00 | RAJ CONSTRUCTION
53.00 | Supply of SS 304 Tubes along with isolation valves, reducers & fittings etc.as per Technical Specification, Typical schematic drg. for Ins. air line of CNG station and scope of work including handling, storage,lifting, transportation upto CNG stations. (Note:Total no.of ferrule fittings may be considered as one jointing ferrule at every 5.0 m)
54.00 | ½”OD X 0.083” min Wall thk. SS Tube (Refer TS Section III - A) | 42.00 | RM |  | 850.00 | 35700.00 | 1200.00 | 50400.00 | 35700.00 | RAJ CONSTRUCTION
55.00 | Laying, testing and commissioning of SS 304 Tubes along with isolation valves, reducers & fittings etc.as per Technical Specification, Typical schematic drg. for Ins. air line of CNG station and scope of work including handling, storage,lifting, transportation upto CNG stations. (Note:Total no.of ferrule fittings may be considered as one jointing ferrule at every 5.0 m)
56.00 | ½”OD X 0.083” min Wall thk. SS Tube (Refer TS Section III - A) | 42.00 | RM |  | 300.00 | 12600.00 | 500.00 | 21000.00 | 12600.00 | RAJ CONSTRUCTION
57.00 | SECTION-B : ERECTION OF MECH. EQUIPMENT
58.00 | Handling (including lifting and transportation from Client's store within city to CNG stations) and erecting in position, the following equipment either on the foundation at Ground level or on roof at 3.5 m above ground level. Contractor's scope shall include supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, etc. :
59.00 | Cascade 4500/3000/2200 L water capacity. Erection at + 4.0 M level (Refer TS Section III - B) | 25.00 | Nos. |  | 30000.00 | 750000.00 | 40000.00 | 1000000.00 | 750000.00 | RAJ CONSTRUCTION
60.00 | Cascade 4500/3000/2200 L water capacity, Erection at + Ground level (Refer TS Section III - B) | 8.00 | Nos. |  | 25000.00 | 200000.00 | 35000.00 | 280000.00 | 200000.00 | RAJ CONSTRUCTION
61.00 | Dispenser Erection at + Ground Level | 38.00 | Nos. |  | 10000.00 | 380000.00 | 12000.00 | 456000.00 | 380000.00 | RAJ CONSTRUCTION
62.00 | Note: The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may increase or decrease at site at the time of actual execution and as per the discretion of Owner/ Engineer-in-charge. The unit rate shall be operated to work out the final payment due to Contractor.
63.00 | SECTION-C : SUPPLY, ERECTION & COMMISSIONING OF MISCELLANEOUS ITEM
64.00 | Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC
65.00 | Air compressor pump (Refer TS Section III - C) (Tyre Inflator) | 1.00 | No. |  | 115000.00 | 115000.00 | 280000.00 | 280000.00 | 115000.00 | RAJ CONSTRUCTION
66.00 | Water cooler (Refer TS Section III - C) | 1.00 | No. |  | 45000.00 | 45000.00 | 85000.00 | 85000.00 | 45000.00 | RAJ CONSTRUCTION
67.00 | Fire fighting Equipments (Refer TS Section III - C)
68.00 | DCP -9 Kg | 89.00 | Nos. |  | 3550.00 | 315950.00 | 11000.00 | 979000.00 | 315950.00 | RAJ CONSTRUCTION
69.00 | DCP -75 Kg | 25.00 | Nos. |  | 32500.00 | 812500.00 | 52000.00 | 1300000.00 | 812500.00 | RAJ CONSTRUCTION
70.00 | CO2 – 4.5 Kg | 25.00 | Nos. |  | 8200.00 | 205000.00 | 8500.00 | 212500.00 | 205000.00 | RAJ CONSTRUCTION
71.00 | Sand Bucket (4 Nos. on each strand) | 25.00 | Nos. |  | 4500.00 | 112500.00 | 2384.00 | 59600.00 | 59600.00 | NOPS INFRASTRUCTURE PVT. LTD.
73.00 | STRUCTURAL WORKS
74.00 | Pipe Supports & Other Structures
75.00 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-in-charge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | 6.00 | MTon. |  | 125000.00 | 750000.00 | 140000.00 | 840000.00 | 750000.00 | RAJ CONSTRUCTION
76.00 | Notes: 1)The quantities indicated above are tentative and may vary as per the site requirements. Final payment will be made based on executed quantities certified by the Owner/Owner's representative. 2)The quoted rates shall be inclusive of the cost of MS bolts (permanent and service), washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required to complete the work. 3)All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates.
77.00 | PRESSURE GAUGES
78.00 | Supply, installation and calibration of pressure Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG. | 25.00 | Nos. |  | 3500.00 | 87500.00 | 32500.00 | 812500.00 | 87500.00 | RAJ CONSTRUCTION
79.00 | TEMPERATURE GAUGES
80.00 | Supply, installation and calibration of Temperature Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG. | 25.00 | Nos. |  | 3500.00 | 87500.00 | 38500.00 | 962500.00 | 87500.00 | RAJ CONSTRUCTION
81.00 | ELECTRICAL WORKS (SUPPLY)
82.00 | SUPPLY
83.00 | Design, engineering, manufacture, shop testing, supply including packing and forwarding, transportation, delivery at storage and from storage to site of power distribution board (PDB) :
84.00 | 415 V, 36 KA single front type indoor PDB to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no. MEC/Q7NT/05/E9/E/1081A & as per standard Specification. Single incomer of 125 Amp (with Single phase preventer & VMR) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) . Outgoing with 01 no. 80 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Booster Compressor. Outgoing with 01 no. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for APFC panel. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C & S/C RELASE) for UPS and Static Bypass. Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB without Timer | 15.00 | Nos. |  | 250000.00 | 3750000.00 | 500000.00 | 7500000.00 | 3750000.00 | RAJ CONSTRUCTION
85.00 | 415 V, 36 KA single front type indoor PDB to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no. MEC/Q7NT/05/E9/E/1081B & as per standard Specification. Single incomer of 100 Amp (with Single phase preventer & VMR) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) . Outgoing with 01 no. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Gas Driven Compressor. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C & S/C RELASE) for UPS and Static Bypass. Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB without Timer | 10.00 | Nos. |  | 230000.00 | 2300000.00 | 495000.00 | 4950000.00 | 2300000.00 | RAJ CONSTRUCTION
86.00 | Floor mounted APFC Panel of 10KVAR capacitor bank in steps of 4x2.5 KVAR capacitors consisting of bus bar chamber, cable alley incoming (MCCB), outgoing feeder (MCBs) as specified in tender specification | 15.00 | Nos. |  | 60000.00 | 900000.00 | 50000.00 | 750000.00 | 750000.00 | NOPS INFRASTRUCTURE PVT. LTD.
87.00 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 150A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5 x 120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with RYB Indication, Voltmeter & Ammeter etc. | 15.00 | Nos. |  | 35000.00 | 525000.00 | 60000.00 | 900000.00 | 525000.00 | RAJ CONSTRUCTION
88.00 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 125A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5 x 120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with RYB Indication, Voltmeter & Ammeter etc. | 10.00 | Nos. |  | 30000.00 | 300000.00 | 55000.00 | 550000.00 | 300000.00 | RAJ CONSTRUCTION
89.00 | Design, engineering,supply including packing and forwarding, transportation, delivery at storage, of the complete earthing and lightning protection system, earth electrodes/ pit, earth main ring, earthing of electrical equipments, instrument panels, field instruments, process equipments and pipes/ flanges including all associated civil work with all material (Like Bitumen coating) and labour as per specification and drawings approved by the company in with IS 3043.
90.00 | Earth Pits- GI PIPE Electrode with 6 mm thick chequered plate cover | 125.00 | Nos. |  | 14500.00 | 1812500.00 | 20000.00 | 2500000.00 | 1812500.00 | RAJ CONSTRUCTION
91.00 | Earth Pits- Copper plate Electrode with 6 mm thick chequered plate cover | 25.00 | Nos. |  | 19500.00 | 487500.00 | 26000.00 | 650000.00 | 487500.00 | RAJ CONSTRUCTION
92.00 | GI Strip (50X6) mm | 2500.00 | Mtrs |  | 340.00 | 850000.00 | 425.00 | 1062500.00 | 850000.00 | RAJ CONSTRUCTION
93.00 | GI Strip (25X3) mm | 5000.00 | Mtrs |  | 200.00 | 1000000.00 | 250.00 | 1250000.00 | 1000000.00 | RAJ CONSTRUCTION
94.00 | Advance maintenance free earthing system with 3mtr earth electrode of low carbon steel with 250 micron copper coating with carbon based backfill compound as per IS 3043/IEEE-80. | 1.00 | Nos. |  | 5500.00 | 5500.00 | 18000.00 | 18000.00 | 5500.00 | RAJ CONSTRUCTION
95.00 | Arrangement for Earthing of LCV with Flexible green Cu wire (25 sqmm of approx 30 Meter length) ,Clamp (including bolting arrangement) ,Flexible PVC, crcodile clamps(2 nos.each) and other item etc. including MS enclosure box with door of sheet thk (2.00mm) color etc. | 25.00 | Sets |  | 12000.00 | 300000.00 | 18000.00 | 450000.00 | 300000.00 | RAJ CONSTRUCTION
96.00 | Design, engineering,supply including packing and forwarding, transportation, delivery at storage, of the 1.1kV grade XLPE insulated, PVC sheathed, FRLS power and control cables (conforming to IS:7098 and specification) including Cable glands & Lugs etc.of following sizes in trenches/ excavated under ground trench /trays, pulling through pipes and its proper sealing, cutting of paved area, roads etc.
97.00 | 3.5x 120 mm2 A2XFY | 10.00 | Mtrs. |  | 950.00 | 9500.00 | 1000.00 | 10000.00 | 9500.00 | RAJ CONSTRUCTION
98.00 | 3.5x 95 mm2 A2XFY | 10.00 | Mtrs. |  | 850.00 | 8500.00 | 800.00 | 8000.00 | 8000.00 | NOPS INFRASTRUCTURE PVT. LTD.
99.00 | 3.5x 50 mm2 A2XFY | 5000.00 | Mtrs. |  | 550.00 | 2750000.00 | 700.00 | 3500000.00 | 2750000.00 | RAJ CONSTRUCTION
100.00 | 4x 25 mm2 A2XFY | 500.00 | Mtrs. |  | 450.00 | 225000.00 | 1200.00 | 600000.00 | 225000.00 | RAJ CONSTRUCTION
101.00 | 4x10 mm2 2XWY | 500.00 | Mtrs. |  | 720.00 | 360000.00 | 650.00 | 325000.00 | 325000.00 | NOPS INFRASTRUCTURE PVT. LTD.
102.00 | 4x 6 mm2 2XWY | 1250.00 | Mtrs. |  | 650.00 | 812500.00 | 450.00 | 562500.00 | 562500.00 | NOPS INFRASTRUCTURE PVT. LTD.
103.00 | 4x 2.5 mm2 2XWY | 20000.00 | Mtrs. |  | 250.00 | 5000000.00 | 300.00 | 6000000.00 | 5000000.00 | RAJ CONSTRUCTION
104.00 | Supply including packing and forwarding, transportation, delivery at storage of lighting fixtures complete with mounting bracket, flame proof/non flame proof, control gear box as per the type of fixture, lamps etc. including civil work with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects.
105.00 | Street lighting, integral flame proof well glass fixture (CMIFR approved for Zone-1/2 gas group IIA & IIB) with 72 W LED luminaire with flame proof control gear Model no. FLPW-1095 of Baliga make or equivalent) | 150.00 | Nos. |  | 8500.00 | 1275000.00 | 12000.00 | 1800000.00 | 1275000.00 | RAJ CONSTRUCTION
106.00 | Street lighting pole 6mtr high GI octagonal pole (Type BOP-6030 of Bajaj make or equivalent) complete with bracket, GI clamps for fixing flame proof control gear box as per standard drawing & specification. | 150.00 | Nos. |  | 16500.00 | 2475000.00 | 15000.00 | 2250000.00 | 2250000.00 | NOPS INFRASTRUCTURE PVT. LTD.
107.00 | UPS SYSTEM Design, supply, packing, forwarding, delivery by equipment supplier at site including commissioning spares as required of UPS systems as per specification, datasheet, block diagram of the following rating :
108.00 | 3KVA, 230 V Single phase, 50 Hz, single industrial type, UPS system suitable for input Power supply voltage of 320V-460V-TPN with healthy single-Phase Selection, Output 230V +/-1%, AC with Bypass supply, Battery Bank, ACDB (Incomer 32A DP MCB & Outgoing 10 Nos. 6A to 10A DP MCB) and 2.0 hrs. Battery backup (VRLA, 12V) and battery capacity shall not be less than 13.0 KVAh (where KVAH = battery AH x 12 V x No. of Batteries). As per enclosed Specification, Block diagram & Data sheet and shall be complete in all respect. Including All interconnecting cables among UPS, Rectifier, battery stand, ACDB etc (30 mtr shall be considered between battery bank and UPS panel, 30 mtr cable shall be considered between ACDB and UPS panel. | 25.00 | Set |  | 600000.00 | 15000000.00 | 475000.00 | 11875000.00 | 11875000.00 | NOPS INFRASTRUCTURE PVT. LTD.
109.00 | Supply,Transportation at site of following sizes of HDPE Pipe in required length fixed on steel, concrete or similar structure, laid in trenches, digging, construct conduit ductbank and buried in concrete including cutting, bending and similar works, supply of clamps, small iron structures, spacers and installation of seats, plugs, bushings etc., civil works and its materials, including all labour and materials complete as per approved drawings and directions of Engineer-In-Charge.
110.00 | 50 mm NB | 8000.00 | Mtrs |  | 170.00 | 1360000.00 | 500.00 | 4000000.00 | 1360000.00 | RAJ CONSTRUCTION
111.00 | 100 mm NB | 4000.00 | Mtrs |  | 450.00 | 1800000.00 | 600.00 | 2400000.00 | 1800000.00 | RAJ CONSTRUCTION
112.00 | Supply of following Hot Dip Galvanized Ladder/Perforated Type cable trays (as per IS 2629) including bends, tee, crosses,horizontal and vertical splices along with cable tray cover(Wherever required for Asthetic look ) etc. as required including supply of all G.I hardwares, all labour and material as required as per standard drawings, specification and direction of Engineer-in-charge
113.00 | Perforated type, made from 50mm height and 2.5 mm thick sheet steel & galvanized (86 microns) of following sizes.
114.00 | 150mm wide | 250.00 | Mtrs |  | 850.00 | 212500.00 | 450.00 | 112500.00 | 112500.00 | NOPS INFRASTRUCTURE PVT. LTD.
115.00 | 300mm wide | 250.00 | Mtrs |  | 1150.00 | 287500.00 | 650.00 | 162500.00 | 162500.00 | NOPS INFRASTRUCTURE PVT. LTD.
116.00 | Erection Material
117.00 | Supply of MS base frame support for switch gear and bracket for misc. electrical equipment,cable tray support out of roled MS section,pipes,plates etc including welding, bolting, reveting, supply of necessary anchor bolts and grouting etc supply of paints applying one coat of anti rust primer two finish coats of approved synthetic enamel paints including bracking walls, floors etc for structure as required including supply of all GI hardware materials including all labour and materials complete as required and the direction of Engineer-in-charge.
118.00 | For RO/DBS | 25.00 | Lumpsum |  | 18500.00 | 462500.00 | 10000.00 | 250000.00 | 250000.00 | NOPS INFRASTRUCTURE PVT. LTD.
119.00 | Supply of the following including the supply of necessary clamp, bolts, rawl plugs etc. breaking and making good of walls, if required , and including all labour and materials complete as per directions of Engineer-In-Charge, applicable standards and Indian Electricity rules.
120.00 | Shock hazard charts complete with frame and glass | 25.00 | Nos. |  | 1000.00 | 25000.00 | 2500.00 | 62500.00 | 25000.00 | RAJ CONSTRUCTION
121.00 | First Aid Boxes | 25.00 | Nos. |  | 4500.00 | 112500.00 | 6800.00 | 170000.00 | 112500.00 | RAJ CONSTRUCTION
122.00 | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark , Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate | 50.00 | Nos. |  | 7500.00 | 375000.00 | 8000.00 | 400000.00 | 375000.00 | RAJ CONSTRUCTION
123.00 | Caution boards (Danger, High Volatage) including supply of necessary clamps, bolts and other hardware. | 25.00 | Nos. |  | 2000.00 | 50000.00 | 3500.00 | 87500.00 | 50000.00 | RAJ CONSTRUCTION
124.00 | Single Line Diagram complete in glass frame. | 25.00 | Nos. |  | 1800.00 | 45000.00 | 4600.00 | 115000.00 | 45000.00 | RAJ CONSTRUCTION
125.00 | Supply of Insulating Mats 11kV grade (as per IS:15652 - 2006) of 1000mm width, required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per applicable Indian or International standards and Indian Electricity Rules. | 125.00 | Mtrs |  | 750.00 | 93750.00 | 1000.00 | 125000.00 | 93750.00 | RAJ CONSTRUCTION
126.00 | Supply of electrical accessories including, cable tags, cable tie ,Flexible pvc conduit,cable marker, nickle plated lugs, double compressed brass cable glands,brass adaptar/reducers/nipples, fixing of metallic anchor fasteners for supporting of cable trays and misc. electrical switchgear including all labour and materials complete as required and as per directions of Engineer-In-Charge.
127.00 | For RO/DBS | 25.00 | Lumpsum |  | 12500.00 | 312500.00 | 10000.00 | 250000.00 | 250000.00 | NOPS INFRASTRUCTURE PVT. LTD.
128.00 | Supply of required material for construction of Cable pit with pit cover (SFRC cover HD-20 of IS-12592) including civil works repair, concrete wall/brick wall & its materials, cable conduits interface & its water sealing, cable support structure including all labour and materials complete in all aspect as per approved drawings and directions of Engineer-In-Charge.
129.00 | 500X500(of inside clearance)X 600(Depth) | 125.00 | Nos. |  | 5500.00 | 687500.00 | 10000.00 | 1250000.00 | 687500.00 | RAJ CONSTRUCTION
130.00 | 750X750(of inside clearance)X800(Depth) | 125.00 | Nos. |  | 6500.00 | 812500.00 | 12000.00 | 1500000.00 | 812500.00 | RAJ CONSTRUCTION
131.00 | 1000X1000(of inside clearance)X1000(Depth) | 50.00 | Nos. |  | 7500.00 | 375000.00 | 15000.00 | 750000.00 | 375000.00 | RAJ CONSTRUCTION
132.00 | ELECTRICAL WORKS (Erection)
133.00 | ERECTION,TESTING AND COMMISSIONING
134.00 | Erection Testing and Commissioning of power distribution board (PDB):
135.00 | 415 V, 36 KA single front type indoor PDB to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no. MEC/Q7NT/05/E9/E/1081A & as per standard Specification. Single In-comer of 125 Amp (with Single phase preventer & VMR) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) . Outgoing with 01 no. 80 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Booster Compressor. Outgoing with 01 no. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for APFC panel. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C & S/C RELASE) for UPS and Static Bypass. Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB without Timer | 15.00 | Nos. |  | 25000.00 | 375000.00 | 50000.00 | 750000.00 | 375000.00 | RAJ CONSTRUCTION
136.00 | 415 V, 36 KA single front type indoor PDB to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no. MEC/Q7NT/05/E9/E/1081B & as per standard Specification. Single incomer of 100 Amp (with Single phase preventer & VMR) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) . Outgoing with 01 no. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Gas Driven Compressor. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C & S/C RELASE) for UPS and Static Bypass. Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 nos. 40A Fuse and 3 nos. 10A DP MCB without Timer | 10.00 | Nos. |  | 25000.00 | 250000.00 | 25000.00 | 250000.00 | 250000.00 | RAJ CONSTRUCTION, NOPS INFRASTRUCTURE PVT. LTD.
137.00 | Floor mounted APFC Panel of 10KVAR capacitor bank in steps of 4x2.5 KVAR capacitors consisting of bus bar chamber, cable alley incoming (MCCB), outgoing feeder (MCB) as specified in tender specification | 15.00 | Nos. |  | 10000.00 | 150000.00 | 3000.00 | 45000.00 | 45000.00 | NOPS INFRASTRUCTURE PVT. LTD.
138.00 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 150A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5 x 120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with RYB Indication, Voltmeter & Ammeter. | 15.00 | Nos. |  | 5000.00 | 75000.00 | 5000.00 | 75000.00 | 75000.00 | RAJ CONSTRUCTION, NOPS INFRASTRUCTURE PVT. LTD.
139.00 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 125A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5 x 120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with RYB Indication, Voltmeter & Ammeter etc. | 10.00 | Nos. |  | 5000.00 | 50000.00 | 5000.00 | 50000.00 | 50000.00 | RAJ CONSTRUCTION, NOPS INFRASTRUCTURE PVT. LTD.
140.00 | Erection Testing and Commissioning of the complete earthing and lightning protection system, earth electrodes/ pit, earth main ring, earthing of electrical equipments, instrument panels, field instruments, process equipments and pipes/ flanges including all associated civil work with all material (Like Bitumen coating) and labour as per specification and drawings approved by the company in with IS 3043.
141.00 | Earth Pits- GI PIPE Electrode with 6 mm thick chequered plate cover | 125.00 | Nos. |  | 1500.00 | 187500.00 | 2000.00 | 250000.00 | 187500.00 | RAJ CONSTRUCTION
142.00 | Earth Pits- Copper plate Electrode with 6 mm thick chequered plate cover | 25.00 | Nos. |  | 1800.00 | 45000.00 | 2500.00 | 62500.00 | 45000.00 | RAJ CONSTRUCTION
143.00 | GI Strip (50X6) mm | 2500.00 | Mtrs |  | 50.00 | 125000.00 | 125.00 | 312500.00 | 125000.00 | RAJ CONSTRUCTION
144.00 | GI Strip (25X3) mm | 5000.00 | Mtrs |  | 50.00 | 250000.00 | 100.00 | 500000.00 | 250000.00 | RAJ CONSTRUCTION
145.00 | Advance maintenance free earthing system with 3mtr earth electrode of low carbon steel with 250 micron copper coating with carbon based backfill compound as per IS 3043/IEEE-80. | 1.00 | Nos. |  | 1500.00 | 1500.00 | 2000.00 | 2000.00 | 1500.00 | RAJ CONSTRUCTION
146.00 | Arrangement for Earthing of LCV with Flexible green Cu wire (25 sqmm of approx 30 Meter length) ,Clamp (including bolting arrangement) ,Flexible PVC, crcodile clamps(2 nos.each) and other item etc. including MS enclosure box with door of sheet thk (2.00mm) color etc. | 25.00 | Sets |  | 500.00 | 12500.00 | 1000.00 | 25000.00 | 12500.00 | RAJ CONSTRUCTION
147.00 | Laying, Termination, Glanding, Testing and Commissioning of the 1.1kV grade XLPE insulated, PVC sheathed, FRLS power and control cables (conforming to IS:7098 and specification) including Cable glands & Lugs etc.of following sizes in trenches/ excavated under ground trench /trays, pulling through pipes and its proper sealing, cutting of paved area, roads etc.
148.00 | 3.5x 120 mm2 A2XFY | 10.00 | Mtrs. |  | 50.00 | 500.00 | 200.00 | 2000.00 | 500.00 | RAJ CONSTRUCTION
149.00 | 3.5x 95 mm2 A2XFY | 10.00 | Mtrs. |  | 50.00 | 500.00 | 150.00 | 1500.00 | 500.00 | RAJ CONSTRUCTION
150.00 | 3.5x 50 mm2 A2XFY | 5000.00 | Mtrs. |  | 50.00 | 250000.00 | 110.00 | 550000.00 | 250000.00 | RAJ CONSTRUCTION
151.00 | 4x 25 mm2 A2XFY | 500.00 | Mtrs. |  | 50.00 | 25000.00 | 70.00 | 35000.00 | 25000.00 | RAJ CONSTRUCTION
152.00 | 4x10 mm2 2XWY | 500.00 | Mtrs. |  | 50.00 | 25000.00 | 70.00 | 35000.00 | 25000.00 | RAJ CONSTRUCTION
153.00 | 4x 6 mm2 2XWY | 1250.00 | Mtrs. |  | 50.00 | 62500.00 | 60.00 | 75000.00 | 62500.00 | RAJ CONSTRUCTION
154.00 | 4x 2.5 mm2 2XWY | 20000.00 | Mtrs. |  | 50.00 | 1000000.00 | 50.00 | 1000000.00 | 1000000.00 | RAJ CONSTRUCTION, NOPS INFRASTRUCTURE PVT. LTD.
155.00 | Erection Testing and Commissioning of of lighting fixtures complete with mounting bracket, flame proof/non flame proof, control gear box as per the type of fixture, lamps etc. including civil work with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects.
156.00 | Street lighting, integral flame proof well glass fixture (CMIFR approved for Zone-1/2 gas group IIA & IIB) with 72 W LED luminaire with flame proof control gear Model no. FLPW-1095 of Baliga make or equivalent) | 150.00 | Nos. |  | 500.00 | 75000.00 | 1000.00 | 150000.00 | 75000.00 | RAJ CONSTRUCTION
157.00 | Street lighting pole 6mtr high GI octagonal pole (Type BOP-6030 of Bajaj make or equivalent) complete with bracket, GI clamps for fixing flame proof control gear box as per standard drawing & specification. | 150.00 | Nos. |  | 1250.00 | 187500.00 | 2000.00 | 300000.00 | 187500.00 | RAJ CONSTRUCTION
158.00 | UPS SYSTEM Erection Testing and Commissioning of including supervision of testing and commissioning by equipment supplier at site including commissioning spares as required of UPS systems as per specification, block diagram and following rating:
159.00 | 3KVA, 230 V Single phase, 50 Hz, single industrial type, UPS system suitable for input Power supply voltage of 320V-460V-TPN with healthy single-Phase Selection, Output 230V +/-1%, AC with Bypass supply, Battery Bank, ACDB (Incomer 32A DP MCB & Outgoing 10 Nos. 6A to 10A DP MCB) and 2.0 hrs. Battery backup (VRLA, 12V) and battery capacity shall not be less than 13.0 KVAh (where KVAH = battery AH x 12 V x No. of Batteries). As per enclosed Specification, Block diagram & Data sheet and shall be complete in all respect. Including All interconnecting cables among UPS, Rectifier, battery stand, ACDB etc (30 mtr shall be considered between battery bank and UPS panel, 30 mtr cable shall be considered between ACDB and UPS panel. | 25.00 | Set |  | 25000.00 | 625000.00 | 10000.00 | 250000.00 | 250000.00 | NOPS INFRASTRUCTURE PVT. LTD.
160.00 | Erection of following sizes of HDPE Pipe in required length fixed on steel, concrete or similar structure, laid in trenches, digging, construct conduit ductbank and buried in concrete including cutting, bending and similar works, supply of clamps, small iron structures, spacers and installation of seats, plugs, bushings etc., civil works and its materials, including all labour and materials complete as per approved drawings and directions of Engineer-In-Charge.
161.00 | 50 mm NB | 8000.00 | Mtrs |  | 50.00 | 400000.00 | 100.00 | 800000.00 | 400000.00 | RAJ CONSTRUCTION
162.00 | 100 mm NB | 4000.00 | Mtrs |  | 100.00 | 400000.00 | 150.00 | 600000.00 | 400000.00 | RAJ CONSTRUCTION
163.00 | Erection of following Hot Dip Galvanized Ladder/Perforated Type cable trays (as per IS 2629) including bends, tee, crosses,horizontal and vertical splices along with cable tray cover(Wherever required for Asthetic look ) etc. as required including Erection of all G.I hardwares, all labour and material as required as per standard drawings, specification and direction of Engineer-in-charge
164.00 | Perforated type, made from 50mm height and 2.5 mm thick sheet steel & galvanized (86 microns) of following sizes.
165.00 | 150mm wide | 250.00 | Mtrs |  | 100.00 | 25000.00 | 165.00 | 41250.00 | 25000.00 | RAJ CONSTRUCTION
166.00 | 300mm wide | 250.00 | Mtrs |  | 100.00 | 25000.00 | 210.00 | 52500.00 | 25000.00 | RAJ CONSTRUCTION
167.00 | Erection Material
168.00 | Erection, Fixing and Commissioning of MS base frame support for switch gear and bracket for misc. electrical equipment,cable tray support out of roled MS section,pipes,plates etc including welding, bolting, reveting, Erection of necessary anchor bolts and grouting etc Erection of paints applying one coat of anti rust primer two finish coats of approved synthetic enamel paints including bracking walls, floors etc for structure as required including Erection of all GI hardware materials including all labour and materials complete as required and the direction of Engineer-in-charge.
169.00 | For RO/DBS | 25.00 | Lumpsum |  | 3000.00 | 75000.00 | 5800.00 | 145000.00 | 75000.00 | RAJ CONSTRUCTION
170.00 | Erection Testing and Commissioning of the following including the Erection of necessary clamp, bolts, rawl plugs etc. breaking and making good of walls, if required , and including all labour and materials complete as per directions of Engineer-In-Charge, applicable standards and Indian Electricity rules.
171.00 | Shock hazard charts complete with frame and glass | 25.00 | Nos. |  | 500.00 | 12500.00 | 750.00 | 18750.00 | 12500.00 | RAJ CONSTRUCTION
172.00 | First Aid Boxes | 25.00 | Nos. |  | 200.00 | 5000.00 | 1350.00 | 33750.00 | 5000.00 | RAJ CONSTRUCTION
173.00 | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark , Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate | 50.00 | Nos. |  | 200.00 | 10000.00 | 1800.00 | 90000.00 | 10000.00 | RAJ CONSTRUCTION
174.00 | Caution boards (Danger, High Volatage) including Erection of necessary clamps, bolts and other hardware. | 25.00 | Nos. |  | 200.00 | 5000.00 | 1000.00 | 25000.00 | 5000.00 | RAJ CONSTRUCTION
175.00 | Single Line Diagram complete in glass frame. | 25.00 | Nos. |  | 200.00 | 5000.00 | 1000.00 | 25000.00 | 5000.00 | RAJ CONSTRUCTION
176.00 | Laying and Pasting of Insulating Mats 11kV grade (as per IS:15652 - 2006) of 1000mm width, required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per applicable Indian or International standards and Indian Electricity Rules. | 125.00 | Mtrs |  | 20.00 | 2500.00 | 100.00 | 12500.00 | 2500.00 | RAJ CONSTRUCTION
177.00 | Erection Fixing and Commissioning of electrical accessories including, cable tags, cable tie ,Flexible pvc conduit,cable marker, nickle plated lugs, double compressed brass cable glands,brass adaptar/reducers/nipples, fixing of metallic anchor fasteners for supporting of cable trays and misc. electrical switchgear including all labour and materials complete as required and as per directions of Engineer-In-Charge.
178.00 | For RO/DBS | 25.00 | Lumpsum |  | 1000.00 | 25000.00 | 10000.00 | 250000.00 | 25000.00 | RAJ CONSTRUCTION
179.00 | Construction of Cable pit with pit cover (SFRC cover HD-20 of IS-12592) including civil works repair, concrete wall/brick wall & its materials, cable conduits interface & its water sealing, cable support structure including all labour and materials complete in all aspect as per approved drawings and directions of Engineer-In-Charge.
180.00 | 500X500(of inside clearance)X 600(Depth) | 125.00 | Nos. |  | 150.00 | 18750.00 | 2649.00 | 331125.00 | 18750.00 | RAJ CONSTRUCTION
181.00 | 750X750(of inside clearance)X800(Depth) | 125.00 | Nos. |  | 200.00 | 25000.00 | 3404.00 | 425500.00 | 25000.00 | RAJ CONSTRUCTION
182.00 | 1000X1000(of inside clearance)X1000(Depth) | 50.00 | Nos. |  | 250.00 | 12500.00 | 4000.00 | 200000.00 | 12500.00 | RAJ CONSTRUCTION
183.00 | All works relating to statutory approvals of the installation from competent authority like Electrical Inspectorate, CEA, DGMS, SEB etc. including carrying out of all required modifications in design / Manufacturer / Installation to meet the requirement of Indian Electricity rules and other statutory regulations in force, carrying out necessary paper work and liasion with the authorities to obtain all necessary clearances for charging of installation as per relevant national standards. However the official fees towards the approvals shall be reimbursed by the client. | 25.00 | Lumpsum |  | 125000.00 | 3125000.00 | 30000.00 | 750000.00 | 750000.00 | NOPS INFRASTRUCTURE PVT. LTD.
184.00 | Total Amount excluding GST
185.00 | GST (CGST & SGST / UTGST or IGST) @ 18% of Net Total Amount mentioned at Sl. No. 184 above. (Enter rate of applicable GST) | 1.00 | percentage |  | 18.00 | 13181722.20 | 18.00 | 16443405.54 | 13181722.20 | RAJ CONSTRUCTION
| Total in Figures |  |  |  |  | 86413512.20 |  | 107795658.54
Lowest Amount Quoted BY: RAJ CONSTRUCTION(86413512.20)

## BOQ Summary
BOQ Summary Details Tender Title: MECHANICAL AND ELECTRICAL WORKS FOR CONSTRUCTION OF CNG STATIONS AT BHUBANESHWAR AND CUTTACK GEOGRAPHICAL AREAS 2 YEARS ARC Tender ID: 2023_GAIL_166479_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RAJ CONSTRUCTION | 86413512.20 | L1
| 2 | NOPS INFRASTRUCTURE PVT. LTD. | 107795658.54 | L2