## BoQ1
Government eProcurement System Created By: SIDDHARTH KUMAR Created Date/Time: 11-Dec-2023 12:06 PM Tender Title: MODIFICATION OF FIRE WATER NETWORK FROM UNDERGROUND TO ABOVE GROUND AT IPS MANSARAMPURA AND RT SANGANER AND GTI JAIPUR Tender ID: 2023_GAIL_170546_1
Tender Inviting Authority: SR. MANAGER (C&P)
Name of Work: MODIFICATION OF FIRE WATER NETWORK FROM UNDERGROUND TO ABOVE GROUND AT IPS MANSARAMPURA & RT SANGANER
Contract No: GAIL/JPR23SD074/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Petrofert Engineers (India)(GSTN-23BAWPS4051A1ZR) |  | M/s.Mitra Contractors(GSTN-NA) |  | Japsin Jacob Wire Drawing Pvt Ltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PIPING WORKS : Drawing work at IPS Mansarampura & RT Sanganer
2.00 | AT IPS Mansarampura
3.00 | Piping General Arreangement Drawing Preparation of piping GAD before start of fabrication work. The GAD shall have complete details for the section of Fire water network to be modified. This GAD shall also indicate the entire Fire water network of the station, however, complete section details shall not be required for the part of fire water network, not to be modified in this project. Contractor shall prepare the drawing and get it approved by EIC before start of fabrication work. | 1.00 | EA |  | 60000.00 | 70800.00 | 17899.00 | 21120.82 | 100000.00 | 118000.00 | 21120.82 | M/s.Mitra Contractors
4.00 | Piping General Arreangement Drawing (As Built) Correction of piping GAD after commissioning of modified fire water network, into as built drawing. The GAD prepared before fabrication work shall be used as reference for As built GAD. | 1.00 | EA |  | 50000.00 | 59000.00 | 17899.00 | 21120.82 | 35000.00 | 41300.00 | 21120.82 | M/s.Mitra Contractors
5.00 | Piping Layout Drawing of Fire water system GAIL Have an older version of piping layout drawing of fire water system (hard copy of this drawing shall be availed to contractor). Various changes has been made in the FWN after the piping layout drawing which has not been incorporated in the drawing. This SOR is dedicated for updation of the drawing incorporating all the changes made in the fire water network of station till completion of this project. | 1.00 | EA |  | 50000.00 | 59000.00 | 17899.00 | 21120.82 | 25000.00 | 29500.00 | 21120.82 | M/s.Mitra Contractors
6.00 | At RT Sanganer
7.00 | Piping General Arreangement Drawing Preparation of piping GAD before start of fabrication work. The GAD shall have complete details for the section of Fire water network to be modified. This GAD shall also indicate the entire Fire water network of the station, however, complete section details shall not be required for the part of fire water network, not to be modified in this project. Contractor shall prepare the drawing and get it approved by EIC before start of fabrication work. | 1.00 | EA |  | 60000.00 | 70800.00 | 17899.00 | 21120.82 | 25000.00 | 29500.00 | 21120.82 | M/s.Mitra Contractors
8.00 | Piping General Arreangement Drawing (As Built) Correction of piping GAD after commissioning of modified fire water network, into as built drawing. The GAD prepared before fabrication work shall be used as reference for As built GAD. | 1.00 | EA |  | 50000.00 | 59000.00 | 17899.00 | 21120.82 | 25000.00 | 29500.00 | 21120.82 | M/s.Mitra Contractors
9.00 | Piping Layout Drawing of Fire water system Preparation of fresh Piping Layout Drawing of Fire water system of station indicating entire FWN (modified as well as un-modified) | 1.00 | EA |  | 50000.00 | 59000.00 | 17899.00 | 21120.82 | 15000.00 | 17700.00 | 17700.00 | Japsin Jacob Wire Drawing Pvt Ltd
10.00 | MECHANICAL WORKS FOR FIRE WATER NETWORK SYSTEM
11.00 | SUPPLY & FABRICATION, ERECTION, INSTALLATION AND HYDRO TESTING OF FIRE WATER NETWORK PIPING
12.00 | Supply ,Fabrication ,Installation , Hydro Testing including procurement and transportation to worksite(s)/workshop(s) including loading, unloading and handling for the following materials to be supplied by Contractor as per the requirement of PMS, MRs, specifications, data-sheets, standards, instructions of Owner/ Engineer- in-Charge and other provisions of Contract for Installation Supply of all materials (except those specified subsequently in SOR), equipment, consumables as defined in Contractor's scope of supply and their transportation to the work site(s); contractor scope of work include the following:- 1. Performing all above ground/buried Fire water piping fabrication works including cutting, edge preparation (inclusive of grinding the edges of pipes, fittings, flanges etc. to match with the matching edges of uneven/ different thickness wherever required), fit up, bending, pre-heating wherever required, welding, threading etc.; 2. Erection of pipes of all types at all elevations; hook-up with equipment nozzles; all types of inline and online instruments such as safety valves, pressure gauges etc. (other than those covered separately), fittings of all sizes i.e. elbows, reducers, tees, 'o' lets, flanges, blind flanges, tappings for pressure gauges, thermowells, hoses and hose couplings of all sizes,if applicable, vents and drains required for process and hydrotesting purposes etc. including fixing of all types of gaskets, bolts, studs and nuts of all sizes; 3. Carrying out non-destructive testing & hydrotesting (excluding radiography covered subsequently in SOR). Hookup of the new above ground network with the existing facilities as per drawings wherever required; cleaning and flushing by water/ compressed air, carrying out hydrostatic test and any other type of testing as specified, cutting/ rebeveling (as required), clean-up and restoration of site, preparation of as built drawings, documents and project records; completing all works in all respects as per the IFC drawings, Piping General Arrangement drawings (GAD's), specifications, standards and other provisions of Contract and instruction of Engineer-in-Charge. Note :- a)Dismantling of existing Valves, Nozzles, Hose Pipe & Hose Cabinet etc. and any other equipment for reuse will be inclusive in SOR.No separate payment shall be made for dismentling except Cutting, grinding, buffing & edge preparation Of Pipe/fitting/flanges of existing FW network which will be paid as per SOR M1.5.1 b) All butt welded fittings end shall generally match with connecting pipe wall thickness. However, in case of misalignment, contractor shall have to do end preparation accordingly without any extra cost. c) All couplings, nipples etc. as required shall be supplied by contractor without any extra cost. d) All Gaskets & Nut-Bolts of adequate quantity shall be supplied and installed without any extra cost. Cost is deemed to be included in this item. e) Hydro test of New Laying Pipe line along with Valves without any extra cost. Cost is deemed to be included in this item.
13.00 | Size - 10.0 Inch, Thk/Sch - 6.3 mm , Material - IS-3589 Gr.410, BE, Welded, Material supply and acceptance at GAIL site store | 29.00 | M |  | 3960.00 | 135511.20 | 4649.00 | 159088.78 | 4000.00 | 136880.00 | 135511.20 | Petrofert Engineers (India)
14.00 | Size - 10.0 Inch, Thk/Sch - 6.3 mm , Material - IS-3589 Gr.410, BE, Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 29.00 | M |  | 1800.00 | 61596.00 | 1009.00 | 34527.98 | 1200.00 | 41064.00 | 34527.98 | M/s.Mitra Contractors
15.00 | Size - 8.0 Inch, Thk/Sch - 6.0 mm , Material - IS-3589 Gr.410, BE, Welded, Material supply and acceptance at GAIL site store | 1169.00 | M |  | 2700.00 | 3724434.00 | 3859.00 | 5323181.78 | 3600.00 | 4965912.00 | 3724434.00 | Petrofert Engineers (India)
16.00 | Size - 8.0 Inch, Thk/Sch - 6.0 mm , Material - IS-3589 Gr.410, BE,Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 1169.00 | M |  | 1500.00 | 2069130.00 | 809.00 | 1115950.78 | 800.00 | 1103536.00 | 1103536.00 | Japsin Jacob Wire Drawing Pvt Ltd
17.00 | Size - 6.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, Material supply and acceptance at GAIL site store | 83.00 | M |  | 1943.00 | 190297.42 | 3039.00 | 297639.66 | 2000.00 | 195880.00 | 190297.42 | Petrofert Engineers (India)
18.00 | Size - 6.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded,material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 83.00 | M |  | 1350.00 | 132219.00 | 509.00 | 49851.46 | 600.00 | 58764.00 | 49851.46 | M/s.Mitra Contractors
19.00 | Size - 4.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, Material supply and acceptance at GAIL site store | 168.00 | M |  | 1305.00 | 258703.20 | 2039.00 | 404211.36 | 1649.00 | 326897.76 | 258703.20 | Petrofert Engineers (India)
20.00 | Size - 4.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 168.00 | M |  | 900.00 | 178416.00 | 509.00 | 100904.16 | 450.00 | 89208.00 | 89208.00 | Japsin Jacob Wire Drawing Pvt Ltd
21.00 | Size - 3.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, Material supply and acceptance at GAIL site store | 7.00 | M |  | 903.00 | 7458.78 | 1059.00 | 8747.34 | 1159.00 | 9573.34 | 7458.78 | Petrofert Engineers (India)
22.00 | Size - 3.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 7.00 | M |  | 675.00 | 5575.50 | 309.00 | 2552.34 | 400.00 | 3304.00 | 2552.34 | M/s.Mitra Contractors
23.00 | Size - 2.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, Material supply and acceptance at GAIL site store | 62.00 | M |  | 564.00 | 41262.24 | 609.00 | 44554.44 | 724.00 | 52967.84 | 41262.24 | Petrofert Engineers (India)
24.00 | Size - 2.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 62.00 | M |  | 500.00 | 36580.00 | 209.00 | 15290.44 | 350.00 | 25606.00 | 15290.44 | M/s.Mitra Contractors
25.00 | Size - 1.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), PE, C.Welded, Material supply and acceptance at GAIL site store | 7.00 | M |  | 267.00 | 2205.42 | 309.00 | 2552.34 | 346.00 | 2857.96 | 2205.42 | Petrofert Engineers (India)
26.00 | Size - 1.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), PE, C.Welded, material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 7.00 | M |  | 500.00 | 4130.00 | 109.00 | 900.34 | 125.00 | 1032.50 | 900.34 | M/s.Mitra Contractors
27.00 | SUPPLY & INSTALLATION OF VALVES
28.00 | Supply & Instalaltion including procurement and transportation to work site(s)/workshop(s) including loading, unloading and handling for the following materials to be supplied by Contractor as per the requirement of PMS, MRs, specifications, data-sheets, standards, instructions of Owner/ Engineer- in-Charge and other provisions of Contract. For Installation Supply of all materials, equipment, consumables as defined in Contractor's scope of supply and its transportation to the work site(s);installation of valves, equipments including fixing of gaskets, bolts, studs, nuts wherever required, levelling, aligning, installation and assembly of accessories, if any, by bolting/threading or welding of pipes at all elevations, testing, completing all works in all respects as per drawings, specification, other provisions of Contract and directions of the Engineer-in-Charge.Dismantling of existing Valves, Nozzles, Hose Pipe & Hose Cabinet etc. and any other equipment for reuse will be inclusive in SOR.No separate payment shall be made for dismentling except Cutting, grinding, buffing & edge preparation Of Pipe/fitting/flanges of existing FW network which will be paid as per SOR M1.5.1
29.00 | Supply & Installation of above/bleow ground Flanged GATE Valves as per details given below:
30.00 | Size - 8.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL Material supply and acceptance at GAIL site store | 10.00 | Nos |  | 42000.00 | 495600.00 | 51459.00 | 607216.20 | 80000.00 | 944000.00 | 495600.00 | Petrofert Engineers (India)
31.00 | Size - 8.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , hydrotesting with pipeline network & hookup with existiong/new network. Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 10.00 | Nos |  | 6000.00 | 70800.00 | 4059.00 | 47896.20 | 1500.00 | 17700.00 | 17700.00 | Japsin Jacob Wire Drawing Pvt Ltd
32.00 | Size - 6.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 28000.00 | 132160.00 | 31459.00 | 148486.48 | 60000.00 | 283200.00 | 132160.00 | Petrofert Engineers (India)
33.00 | Size - 6.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEELmaterial handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , hydrotesting with pipeline network & hookup with existiong/new network. Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 4.00 | Nos |  | 6000.00 | 28320.00 | 4059.00 | 19158.48 | 1200.00 | 5664.00 | 5664.00 | Japsin Jacob Wire Drawing Pvt Ltd
34.00 | Size - 4.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL Material supply and acceptance at GAIL site store | 8.00 | Nos |  | 13400.00 | 126496.00 | 21029.00 | 198513.76 | 30000.00 | 283200.00 | 126496.00 | Petrofert Engineers (India)
35.00 | Size - 4.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , hydrotesting with pipeline network & hookup with existiong/new network. Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 8.00 | Nos |  | 3000.00 | 28320.00 | 2049.00 | 19342.56 | 800.00 | 7552.00 | 7552.00 | Japsin Jacob Wire Drawing Pvt Ltd
36.00 | Size - 3.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 12000.00 | 56640.00 | 14049.00 | 66311.28 | 20000.00 | 94400.00 | 56640.00 | Petrofert Engineers (India)
37.00 | Size - 3.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , hydrotesting with pipeline network & hookup with existiong/new network. Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 4.00 | Nos |  | 3000.00 | 14160.00 | 2049.00 | 9671.28 | 700.00 | 3304.00 | 3304.00 | Japsin Jacob Wire Drawing Pvt Ltd
38.00 | Size - 2.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 8500.00 | 40120.00 | 9049.00 | 42711.28 | 15000.00 | 70800.00 | 40120.00 | Petrofert Engineers (India)
39.00 | Size - 2.0 Inch, Rating - 150# FLGD, B-16.5, RF/125AARH, API-600, ASTM A 216 GR WCB, TRIM-13% CR STEEL material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , hydrotesting with pipeline network & hookup with existiong/new network. Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 4.00 | Nos |  | 2000.00 | 9440.00 | 1049.00 | 4951.28 | 500.00 | 2360.00 | 2360.00 | Japsin Jacob Wire Drawing Pvt Ltd
40.00 | Supply & Installation of above/bleow ground Socket welded Gate Valves as per details given below:
41.00 | Size - 1 Inch, Rating - 800# Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 3800.00 | 22420.00 | 5049.00 | 29789.10 | 5000.00 | 29500.00 | 22420.00 | Petrofert Engineers (India)
42.00 | Size - 1 Inch, Rating - 800# material handling, shifting, Errection, fabrication, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 5.00 | Nos |  | 1000.00 | 5900.00 | 1049.00 | 6189.10 | 500.00 | 2950.00 | 2950.00 | Japsin Jacob Wire Drawing Pvt Ltd
43.00 | Supply of Flanges & Fittings
44.00 | Supply,installation,Errection,fabrication & testing including procurement and transportation to worksite(s)/workshop(s) including loading, unloading and handling for the following materials to be supplied by Contractor as per the requirement of PMS, MRs, specifications, data-sheets, standards, instructions of Owner/ Engineer- in-Charge and other provisions of Contract. Dismantling of existing Valves, Nozzles, Hose Pipe & Hose Cabinet etc. and any other equipment for reuse will be inclusive in SOR. No separate payment shall be made for dismentling except Cutting, grinding, buffing & edge preparation Of Pipe/fitting/flanges of existing FW network which will be paid as per SOR M1.5.1
45.00 | Supply of Weld Neck Raised Face (WNRF) as per details given below
46.00 | Size- 8 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH Material supply and acceptance at GAIL site store | 28.00 | Nos |  | 3340.00 | 110353.60 | 4999.00 | 165166.96 | 4500.00 | 148680.00 | 110353.60 | Petrofert Engineers (India)
47.00 | Size- 8 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network.Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 28.00 | Nos |  | 500.00 | 16520.00 | 809.00 | 26729.36 | 800.00 | 26432.00 | 16520.00 | Petrofert Engineers (India)
48.00 | Size- 6 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 2500.00 | 14750.00 | 3549.00 | 20939.10 | 4000.00 | 23600.00 | 14750.00 | Petrofert Engineers (India)
49.00 | Size- 6 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network.Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 5.00 | Nos |  | 500.00 | 2950.00 | 609.00 | 3593.10 | 700.00 | 4130.00 | 2950.00 | Petrofert Engineers (India)
50.00 | Size- 4 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH Material supply and acceptance at GAIL site store | 40.00 | Nos |  | 1055.00 | 49796.00 | 1999.00 | 94352.80 | 2000.00 | 94400.00 | 49796.00 | Petrofert Engineers (India)
51.00 | Size- 4 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network.Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 40.00 | Nos |  | 400.00 | 18880.00 | 409.00 | 19304.80 | 700.00 | 33040.00 | 18880.00 | Petrofert Engineers (India)
52.00 | Size- 2 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH Material supply and acceptance at GAIL site store | 7.00 | Nos |  | 500.00 | 4130.00 | 1209.00 | 9986.34 | 2000.00 | 16520.00 | 4130.00 | Petrofert Engineers (India)
53.00 | Size- 2 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network.Supply and installation of suitable size and quantity of stud,bolt,fastener,gasket etc.of relevant standard as approved by EIC is inclusive in this SOR | 7.00 | Nos |  | 400.00 | 3304.00 | 209.00 | 1726.34 | 700.00 | 5782.00 | 1726.34 | M/s.Mitra Contractors
54.00 | Supply of Socket Weld Raised Face (SWRF) as per details given below
55.00 | Size- 1 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 350.00 | 2065.00 | 609.00 | 3593.10 | 2000.00 | 11800.00 | 2065.00 | Petrofert Engineers (India)
56.00 | Size- 1 inch, 150#, ASTM A-105, ASME B16.5, 150,RF/125AARH material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 5.00 | Nos |  | 100.00 | 590.00 | 109.00 | 643.10 | 300.00 | 1770.00 | 590.00 | Petrofert Engineers (India)
57.00 | Supply of Elbows as per details given below
58.00 | Size- 10.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 3850.00 | 18172.00 | 6999.00 | 33035.28 | 5000.00 | 23600.00 | 18172.00 | Petrofert Engineers (India)
59.00 | Size- 10.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 4.00 | Nos |  | 2000.00 | 9440.00 | 1009.00 | 4762.48 | 700.00 | 3304.00 | 3304.00 | Japsin Jacob Wire Drawing Pvt Ltd
60.00 | Size- 10.0 inch, 45 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 4890.00 | 28851.00 | 4049.00 | 23889.10 | 5000.00 | 29500.00 | 23889.10 | M/s.Mitra Contractors
61.00 | Size- 10.0 inch, 45 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 5.00 | Nos |  | 2000.00 | 11800.00 | 1009.00 | 5953.10 | 700.00 | 4130.00 | 4130.00 | Japsin Jacob Wire Drawing Pvt Ltd
62.00 | Size- 8.0 inch, 45 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 26.00 | Nos |  | 2000.00 | 61360.00 | 2529.00 | 77589.72 | 4500.00 | 138060.00 | 61360.00 | Petrofert Engineers (India)
63.00 | Size- 8.0 inch, 45 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 26.00 | Nos |  | 1800.00 | 55224.00 | 809.00 | 24820.12 | 350.00 | 10738.00 | 10738.00 | Japsin Jacob Wire Drawing Pvt Ltd
64.00 | Size- 8.0 inch, 75 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 6.00 | Nos |  | 2700.00 | 19116.00 | 2529.00 | 17905.32 | 4500.00 | 31860.00 | 17905.32 | M/s.Mitra Contractors
65.00 | Size- 8.0 inch, 75 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 6.00 | Nos |  | 1800.00 | 12744.00 | 809.00 | 5727.72 | 350.00 | 2478.00 | 2478.00 | Japsin Jacob Wire Drawing Pvt Ltd
66.00 | Size- 8.0 inch, 22.5* deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 7.00 | Nos |  | 1980.00 | 16354.80 | 2529.00 | 20889.54 | 4500.00 | 37170.00 | 16354.80 | Petrofert Engineers (India)
67.00 | Size- 8.0 inch, 22.5* deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 7.00 | Nos |  | 1500.00 | 12390.00 | 809.00 | 6682.34 | 500.00 | 4130.00 | 4130.00 | Japsin Jacob Wire Drawing Pvt Ltd
68.00 | Size- 8.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 44.00 | Nos |  | 2900.00 | 150568.00 | 4999.00 | 259548.08 | 4500.00 | 233640.00 | 150568.00 | Petrofert Engineers (India)
69.00 | Size- 8.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 44.00 | Nos |  | 1800.00 | 93456.00 | 809.00 | 42003.28 | 500.00 | 25960.00 | 25960.00 | Japsin Jacob Wire Drawing Pvt Ltd
70.00 | Size- 6.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 9.00 | Nos |  | 1780.00 | 18903.60 | 2999.00 | 31849.38 | 4000.00 | 42480.00 | 18903.60 | Petrofert Engineers (India)
71.00 | Size- 6.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 9.00 | Nos |  | 1400.00 | 14868.00 | 609.00 | 6467.58 | 500.00 | 5310.00 | 5310.00 | Japsin Jacob Wire Drawing Pvt Ltd
72.00 | Size- 4.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 31.00 | Nos |  | 780.00 | 28532.40 | 1159.00 | 42396.22 | 3500.00 | 128030.00 | 28532.40 | Petrofert Engineers (India)
73.00 | Size- 4.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 31.00 | Nos |  | 1000.00 | 36580.00 | 409.00 | 14961.22 | 350.00 | 12803.00 | 12803.00 | Japsin Jacob Wire Drawing Pvt Ltd
74.00 | Size- 2.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 12.00 | Nos |  | 300.00 | 4248.00 | 999.00 | 14145.84 | 2000.00 | 28320.00 | 4248.00 | Petrofert Engineers (India)
75.00 | Size- 2.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 12.00 | Nos |  | 200.00 | 2832.00 | 209.00 | 2959.44 | 300.00 | 4248.00 | 2832.00 | Petrofert Engineers (India)
76.00 | Size- 1.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, SW, 1.5D Material supply and acceptance at GAIL site store | 9.00 | Nos |  | 300.00 | 3186.00 | 609.00 | 6467.58 | 1000.00 | 10620.00 | 3186.00 | Petrofert Engineers (India)
77.00 | Size- 1.0 inch, 90 deg.,Sch.40, ASTM A 234 Gr. WPB-W, ASME B-16.9, SW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 9.00 | Nos |  | 100.00 | 1062.00 | 109.00 | 1157.58 | 200.00 | 2124.00 | 1062.00 | Petrofert Engineers (India)
78.00 | Supply of Equal Tee as per details given below
79.00 | 10" x 10", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 5800.00 | 27376.00 | 7009.00 | 33082.48 | 5000.00 | 23600.00 | 23600.00 | Japsin Jacob Wire Drawing Pvt Ltd
80.00 | 10" x 10", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 4.00 | Nos |  | 2500.00 | 11800.00 | 909.00 | 4290.48 | 500.00 | 2360.00 | 2360.00 | Japsin Jacob Wire Drawing Pvt Ltd
81.00 | 8" x 8", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 9.00 | Nos |  | 4900.00 | 52038.00 | 4009.00 | 42575.58 | 4000.00 | 42480.00 | 42480.00 | Japsin Jacob Wire Drawing Pvt Ltd
82.00 | 8" x 8", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 9.00 | Nos |  | 2500.00 | 26550.00 | 909.00 | 9653.58 | 400.00 | 4248.00 | 4248.00 | Japsin Jacob Wire Drawing Pvt Ltd
83.00 | 2" x 2", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 950.00 | 5605.00 | 1059.00 | 6248.10 | 2000.00 | 11800.00 | 5605.00 | Petrofert Engineers (India)
84.00 | 2" x 2", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 5.00 | Nos |  | 500.00 | 2950.00 | 309.00 | 1823.10 | 200.00 | 1180.00 | 1180.00 | Japsin Jacob Wire Drawing Pvt Ltd
85.00 | 1" x 1", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, SW Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 750.00 | 3540.00 | 509.00 | 2402.48 | 800.00 | 3776.00 | 2402.48 | M/s.Mitra Contractors
86.00 | 1" x 1", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, SW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 4.00 | Nos |  | 200.00 | 944.00 | 209.00 | 986.48 | 200.00 | 944.00 | 944.00 | Japsin Jacob Wire Drawing Pvt Ltd, Petrofert Engineers (India)
87.00 | Supply of Un-Equal Tee as per details given below
88.00 | 8" x 6", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 11.00 | Nos |  | 8000.00 | 103840.00 | 6009.00 | 77996.82 | 3000.00 | 38940.00 | 38940.00 | Japsin Jacob Wire Drawing Pvt Ltd
89.00 | 8" x 6", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 11.00 | Nos |  | 2500.00 | 32450.00 | 1509.00 | 19586.82 | 500.00 | 6490.00 | 6490.00 | Japsin Jacob Wire Drawing Pvt Ltd
90.00 | 8" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 31.00 | Nos |  | 6200.00 | 226796.00 | 6009.00 | 219809.22 | 3000.00 | 109740.00 | 109740.00 | Japsin Jacob Wire Drawing Pvt Ltd
91.00 | 8" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 31.00 | Nos |  | 2500.00 | 91450.00 | 1509.00 | 55199.22 | 350.00 | 12803.00 | 12803.00 | Japsin Jacob Wire Drawing Pvt Ltd
92.00 | Supply of Reducer as per details given below:
93.00 | 10" x 8", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 6.00 | Nos |  | 7980.00 | 56498.40 | 5009.00 | 35463.72 | 3000.00 | 21240.00 | 21240.00 | Japsin Jacob Wire Drawing Pvt Ltd
94.00 | 10" x 8", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 6.00 | Nos |  | 2500.00 | 17700.00 | 1009.00 | 7143.72 | 400.00 | 2832.00 | 2832.00 | Japsin Jacob Wire Drawing Pvt Ltd
95.00 | 6" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 11.00 | Nos |  | 3800.00 | 49324.00 | 3009.00 | 39056.82 | 2750.00 | 35695.00 | 35695.00 | Japsin Jacob Wire Drawing Pvt Ltd
96.00 | 6" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 11.00 | Nos |  | 1200.00 | 15576.00 | 609.00 | 7904.82 | 300.00 | 3894.00 | 3894.00 | Japsin Jacob Wire Drawing Pvt Ltd
97.00 | 4" x 3", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 5.00 | Nos |  | 2500.00 | 14750.00 | 2009.00 | 11853.10 | 2000.00 | 11800.00 | 11800.00 | Japsin Jacob Wire Drawing Pvt Ltd
98.00 | 4" x 3", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 5.00 | Nos |  | 1200.00 | 7080.00 | 409.00 | 2413.10 | 350.00 | 2065.00 | 2065.00 | Japsin Jacob Wire Drawing Pvt Ltd
99.00 | Supply & Erection of Osciliating Water Monitor as per details given below:
100.00 | Supply & Erection of Osciliating Water Monitor shall confirm to IS 8442.,Water powered self -oscillating mechanism made out stainless steel/ GM,permitting automatic adjustable ARC from 0-120 degree & 0-360 degree rotation +90 to (-) 45 degree manual vertical movement.,Alumininum alloy Nozzle suitable for a discharge minimum at least 1000 GPM at 7 kg/cm2 pressure Monitor shall have more then 65 meter horizontal throw in still air.Osciliating Water Monitor assembly shall hydro tested on 25 kg/cm2 with certifcate . Please refer the technical speceification document attached with the tender document for detailed specification of water monitor. Suply shall be strictly as per specifecation in technical specs of tender. | 2.00 | Nos |  | 50000.00 | 118000.00 | 169599.00 | 400253.64 | 125000.00 | 295000.00 | 118000.00 | Petrofert Engineers (India)
101.00 | Cutting, grinding, buffing & edge preparation Of Pipe/fitting/flanges of existing FW network
102.00 | Cutting (gas cutting or by cutting wheel as per requirement) of Pipe/fitting/flanges etc of any size and thereafter grinding of the cut out Pipe/fitting/flanges for making the one or both faces of cutout piece smooth (free from sharp edges, burs etc) and suitable for welding to new/existing Pipe/fitting/flanges, bavel preparation etc. including charges for material handling, consmables like gas (acetelyne & oxygen), grinding wheels etc (UOM is IMM i.e: inch dia X mm thk of pipe) .eg. cutting of 6 inch dia Pipe/fitting/flanges of pipe thickness of 4 mm at one place measured qty will be 6 inch dia x 4 mm i.e 24 IMM. Simillarly, Making hole of 6 Inch dia in any higher dia pipeline of 4mm thickness at one place measured qty will be 6 inch dia x 4 mm i.e 24 IMM | 7935.00 | IMM |  | 5.00 | 46816.50 | 9.00 | 84269.70 | 65.00 | 608614.50 | 46816.50 | Petrofert Engineers (India)
103.00 | RADIOGRAPHY & MPI
104.00 | Performance of radiographic inspection and/or Magnetic particle inspection (MPI) of piping of all types, sizes, thickness including providing or hiring of all necessary equipment, supply of all consumables including radiographic films and whatever else even though not expressly mentioned but required to perform the work as per specification and instructions of Engineer-in-Charge. Contractor to submit DPR, Inspection Report along with Radiography Report to Engineer-in-Charge. Radiography of piping joints as per details given below:
105.00 | Size - 10.0 Inch | 22.00 | Nos |  | 2000.00 | 51920.00 | 999.00 | 25934.04 | 1000.00 | 25960.00 | 25934.04 | M/s.Mitra Contractors
106.00 | Size - 8.0 Inch | 520.00 | Nos |  | 1800.00 | 1104480.00 | 709.00 | 435042.40 | 700.00 | 429520.00 | 429520.00 | Japsin Jacob Wire Drawing Pvt Ltd
107.00 | Size - 6.0 Inch | 58.00 | Nos |  | 1000.00 | 68440.00 | 609.00 | 41679.96 | 600.00 | 41064.00 | 41064.00 | Japsin Jacob Wire Drawing Pvt Ltd
108.00 | Size - 4.0 Inch | 137.00 | Nos |  | 1000.00 | 161660.00 | 509.00 | 82284.94 | 450.00 | 72747.00 | 72747.00 | Japsin Jacob Wire Drawing Pvt Ltd
109.00 | Size - 3.0 Inch | 4.00 | Nos |  | 500.00 | 2360.00 | 309.00 | 1458.48 | 400.00 | 1888.00 | 1458.48 | M/s.Mitra Contractors
110.00 | Size - 2.0 Inch | 40.00 | Nos |  | 400.00 | 18880.00 | 209.00 | 9864.80 | 400.00 | 18880.00 | 9864.80 | M/s.Mitra Contractors
111.00 | Size - 1.0 Inch | 21.00 | Nos |  | 200.00 | 4956.00 | 109.00 | 2701.02 | 400.00 | 9912.00 | 2701.02 | M/s.Mitra Contractors
112.00 | PIPE SUPPORTS
113.00 | Supply, fabrication and erection of pipe/ equipment supports (for all sizes/ thickness) including shoes, pipes, cross-ivers, platforms, ladders, railings etc. as required, cradles, turn buckles, T-posts for all types of guides, anchors, special supports for cold/hot insulated pipes etc. if applicable, all necessary equipment, consumables, labour etc. for completing all works including supply of bolts, nuts, washers, U-clamps, wooden blocks etc. as required for supporting, supply and application of paints and primers suitable for normal corrosive painting environment as defined in contract document and as per standard specification for painting specification, Drawings, Specification, Standards, other provisions of Contract and instruction of Engineer-in-Charge.
114.00 | CS Structural Steel | 15.53 | MT |  | 95000.00 | 1740913.00 | 71079.00 | 1302551.11 | 95000.00 | 1740913.00 | 1302551.11 | M/s.Mitra Contractors
115.00 | PAINTING / COATING
116.00 | Painting of all above ground piping including all fittings, valves, flanges etc. Supply of paints, solvents and primers, preparation of surfaces and application of primer and finish paints suitable for highly corrosive/corrosive/ normal corrosive painting environment as defined in contract document and on pipes as per standard specification for painting , identification, lettering/ numbering, colour coding etc. as specified including rub down and touch up of shop primer or scrapping of shop primer wherever required and providing of scaffolding for all heights, labour, materials, tools and tackles, consumables, supervision etc. to complete the work in all respect as per Specification, Drawings, Standards and instruction of Engineer-in- Charge. Note: The Coating thickness shall be as per the standard specification of Painting attached with the Tender document. Painting of steel Structure Painting of steel structure as per painting specification in tender document. | 1092.00 | M2 |  | 350.00 | 450996.00 | 399.00 | 514135.44 | 95.00 | 122413.20 | 122413.20 | Japsin Jacob Wire Drawing Pvt Ltd
117.00 | Supply of coal Tar Tape, solvents and primers and preparation of surfaces, application of primer, Coating of Below ground/above ground Carrier pipe including all fittings, valves, flanges etc. with coal tar tape. Coating of below ground carrier pipe shall be Coal Tar Tape coating as per technical specification provided with tender document. | 166.00 | M2 |  | 600.00 | 117528.00 | 499.00 | 97744.12 | 500.00 | 97940.00 | 97744.12 | M/s.Mitra Contractors
118.00 | CIVIL WORK FOR FIRE WATER NETWORK SYSTEM
119.00 | DEMOLITION OF R.C.C./BRICKS/STONE MASONRY/ROAD
120.00 | Site clearance by demolition of R.C.C./Brickwork/Stone Masonry/Stone Soling/road, Flexible pavements etc. along with removing the debris and disposal of unserviceable material to any lead and staking of serviceable materials, handing over serviceable material to concerned department if required as per technical specifications and direction of Engineer-in-charge. The cutting of road shall be required for laying underground pipeline or any other purpose as per site requirement for the tendered work. Note: 1. Rate includes cost of all labour, tools, tackles, hire charges, royalties, levies, leads, loading/unloading, transportation, water, electric power, illumination etc. complete in all respects as per scope of work, detailed construction drawings, technical specifications and direction of Engineer-in-charge. 2. Demolition of RCC/PCC/Brick Masonry/Road will be paid in NET CUM as demolished. | 692.00 | M3 |  | 800.00 | 653248.00 | 109.00 | 89005.04 | 2000.00 | 1633120.00 | 89005.04 | M/s.Mitra Contractors
121.00 | EARTH WORK IN FOUNDATION
122.00 | Earth work in Excavation below ground level for all kinds of works in ALL TYPES OF SOIL as classified in specification for a depth upto 1.5m including removal of vegetation, shrubs and debris, cutting and dressing of sides in slopes, levelling, grading and ramming of bottoms, dewatering of accumulated water from any source and keeping the surface dry for subsequent works and disposal or stacking of excavated material within a lead of 100m, as directed including providing temporary supports to existing service lines like water pipes, sewage pipes, electric overhead and underground cables etc. all complete. | 643.09 | M3 |  | 300.00 | 227653.86 | 279.00 | 211718.09 | 350.00 | 265596.17 | 211718.09 | M/s.Mitra Contractors
123.00 | Earth work in Excavation below ground level for all kinds of works in ALL TYPES OF SOIL as classified in specification for a depth beyond 1.5m and upto & inclusive of 3.0m including removal of vegetation, shrubs and debris, cutting and dressing of sides in slopes, levelling, grading and ramming of bottoms, dewatering of accumulated water from any source and keeping the surface dry for subsequent works and disposal or stacking of excavated material within a lead of 100m, as directed including providing temporary supports to existing service lines like water pipes, sewage pipes, electric overhead and underground cables etc. all complete. | 210.03 | M3 |  | 350.00 | 86742.39 | 299.00 | 74102.78 | 100.00 | 24783.54 | 24783.54 | Japsin Jacob Wire Drawing Pvt Ltd
124.00 | Backfilling after execution of the WORK to proper grade and level with selected materials from available excavated soil from spoil heaps, including re-excavating the deposited soil excavated earlier, breaking clods, laying at all depths and heights in layers of thickness not exceeding 15 Cms. watering, rolling and ramming by manual methods/ mechanical compactors to achieve 90% laboratory maximum dry density, dressing, trimming etc. in foundations, plinths, trenches, pits etc. all complete. | 1545.14 | M3 |  | 20.00 | 36465.30 | 79.00 | 144037.95 | 200.00 | 364653.04 | 36465.30 | Petrofert Engineers (India)
125.00 | Transporting and disposing the SURPLUS EARTH AND DEBRIS including shrubs and vegetations from construction area beyond the initial lead of 150M including re-excavating the deposited soil excavated earlier, transportation, loading, unloading, laying at all depths and heights, stacking, levelling and dressing both the area (viz. from where the earth is transported and where it is deposited) to required levels and slopes complete with all lifts as directed. For carting on the basis of truck measurements (volume of truck reduced by 30% for voids) | 308.62 | M3 |  | 400.00 | 145668.64 | 139.00 | 50619.85 | 100.00 | 36417.16 | 36417.16 | Japsin Jacob Wire Drawing Pvt Ltd
126.00 | PLAIN & REINFORCED CEMENT CONCRETE:
127.00 | Providing and laying PLAIN CEMENT CONCRETE for all depths below and upto plinth level in foundations,drains, fillings, non-suspended floors, pavements & ramps or any other works etc. including shuttering, tamping, ramming, vibrating, curing, shuttering etc. all as specified in any shape, position, thickness and finishing the top surface rough or smooth as specified and directed all complete for concrete of nominal mix 1:4:8 by volume (1 Cement: 4 Coarse Sand: 8 Crushed Stone Aggregates/Gravels with 40mm and down size graded crushed stone aggaregates. | 85.81 | M3 |  | 5000.00 | 506279.00 | 4259.00 | 431248.45 | 6000.00 | 607534.80 | 431248.45 | M/s.Mitra Contractors
128.00 | Concrete of nominal mix of 1:5:10 by volume (1 Cement :5 Coarse Sand : 10 Crushed Stone Aggaregates/Gravels). | 21.70 | M3 |  | 5000.00 | 128030.00 | 4159.00 | 106495.35 | 5000.00 | 128030.00 | 106495.35 | M/s.Mitra Contractors
129.00 | Providing and laying REINFORCED CEMENT CONCRETE OF M-30 GRADE with 20mm and down size graded crushed stone aggregates/gravel in SUB-STRUCTURE of all types e.g. foundations, footings, raft, beams, slabs, pile caps, retaining walls, jambs, counterforts, buttresses, trenches, manholes,pipe encasement, catchpits, drains, RCC pits, equipment/machine foundations, pedestals, pipe sleepers, columns, plinth beams, suspended floors, beams, staircases, landings, steps, brackets etc. (including single pour concreting upto 250m3), including cost of admixtures if used,providing pockets, openings, recesses, chamfering etc., wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. all complete (excluding the Cost of Reinforcement and Shuttering) for all depths below and upto plinth level in any shape, position and thickness etc. all complete as specified, shown and directed. | 145.80 | M3 |  | 7000.00 | 1204308.00 | 5459.00 | 939188.20 | 6500.00 | 1118286.00 | 939188.20 | M/s.Mitra Contractors
130.00 | Providing and laying REINFORCED CEMENT CONCRETE OF M-30 GRADE with 20mm and down size graded crushed stone aggregates/gravel in SUPER STRUCTURE in suspended floors, slabs, beams, columns, walls including counterforts, staircases, landings, steps, facias, fins, mouldings, gutters, shelves, windowsills, canopies, lintels, girders, ducts, brackets, chajjas with drip moulds, pedestals, posts, struts, equipment/machine foundations, ramps etc. (including single pour concreting upto 250m3) including cost of admixtures if used providing pockets, openings, recesses, chamfering wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. all complete (excluding the Cost of Reinforcement and Shuttering) for all heights above plinth level in any shape, position, thickness etc. all complete as specified, shown and directed. | 36.20 | M3 |  | 7500.00 | 320370.00 | 5459.00 | 233186.64 | 6500.00 | 277654.00 | 233186.64 | M/s.Mitra Contractors
131.00 | CENTERING AND SHUTTERING
132.00 | Providing and fixing CENTERING AND SHUTTERING in foundations, footings, raft beams, slabs, pile caps, retaining walls, jambs, counter-forts, buttresses, trenches, equipment/machine foundations, pedestals, abutments, pipe sleepers, columns, plinth beams, lintels, suspended slabs, beams, staircases, landings, steps, non-circular tunnels/bunkers/silos/ shafts/ hoppers/liquid storage structures etc. including shuttering for single pour concreting, strutting, bracing, propping etc., keeping the same in position during concreting and removal of the same after specified period etc. for Straight/ Inclined Shuttering, keeping necessary provision for inserts, projecting dowels, anchor bolts or any other fixture etc. all complete and as specified and directed.
133.00 | i) For all depths below and upto & inclusive of plinth level. | 1829.00 | M2 |  | 250.00 | 539555.00 | 189.00 | 407903.58 | 400.00 | 863288.00 | 407903.58 | M/s.Mitra Contractors
134.00 | REINFORCEMENT
135.00 | Supplying and placing in position HIGH STRENGTH DEFORMED STEEL BARS REINFORCEMENT (conforming to IS:1786, Grade Fe 415), for R.C.C. work including transporting the Steel, straightening, cleaning, decoiling, cutting, bending to required shapes and lengths as per details, binding with contractor's own 16 SWG black soft annealed binding wire at every intersection, supplying and placing with proper cover blocks, supports, chairs, overlaps, welding, spacers, fanhooks etc. for all heights and depths etc. all complete as directed. | 13.43 | MT |  | 85000.00 | 1347029.00 | 47599.00 | 754320.39 | 85000.00 | 1347029.00 | 754320.39 | M/s.Mitra Contractors
136.00 | CEMENT PLASTER IN COARSE SAND
137.00 | Cement plaster in coarse sand to thickness 20 mm in patches including cutting the patch & plastering the surface of the walls complete with 1:3 (1 cement :3 coarse sand) | 429.00 | M2 |  | 250.00 | 126555.00 | 219.00 | 110862.18 | 300.00 | 151866.00 | 110862.18 | M/s.Mitra Contractors
138.00 | INTERLOCKING BLOCK WORKS
139.00 | Providing and laying 60mm thick factory made concrete interlocking paver block of M-30 grade made by block making machine with strong vibratory compaction of Approved size ,design & sape . Laid in requried colour and pattern over & including 50 mm thick compacted bed of coarse sand, filling the jounts with fine sand all complete as per the direction of EIC | 429.00 | M2 |  | 800.00 | 404976.00 | 899.00 | 455091.78 | 800.00 | 404976.00 | 404976.00 | Japsin Jacob Wire Drawing Pvt Ltd, Petrofert Engineers (India)
140.00 | STRUCTURAL STEEL WORKS
141.00 | Supplying, transporting, storing, fabricating in position and testing/examining bolted and/or welded STRUCTURAL STEEL WORKS at all levels and locations including all builtup sections/compound sections made out of rolled sections and/or plates/bent plates in trusses, purlins, wind ties, wind girders, columns, portals, racks, frameworks, crane gantries, surge girders, bracings, floor beams, lifting beams, monorails, platforms, staircases (excluding chequered plates and gratings), ladders, stoppers, brackets, side runners, sagrods, supports for equipment and technological accesories and process piping, hand railings, posts, conveyor galleries, trestles, towers, masts, junction houses etc., cutting to required size, straightening/bending if required, edge preparation, cleaning, preheating, bolting/welding of joints, (including sealing the joints of box sections with continuous welding), finishing edges by grinding, fixing in line and level with temporary staging & bracing and removal of the same after erection, grouting with Ordinary Grout or premix free flow Nonshrink Grout as specified, including preparation and submission of detailed fabrication drawings and applying primer after fabrication as per specification (for normal corrosive environment), etc. all complete | 2.00 | MT |  | 120000.00 | 283200.00 | 76079.00 | 179546.44 | 100000.00 | 236000.00 | 179546.44 | M/s.Mitra Contractors
142.00 | MISCELLANEOUS STEEL WORKS
143.00 | Supplying, fabricating, fixing and keeping in position at all levels and locations THREADED ANCHOR BOLTS of all diameters and nomenclature including nuts, washers, anchor plates, pipe sleeves etc. in foundations, columns, pedestals, slabs, beams, walls etc. or any other place as directed including handling & transporting, straightening if required, turning from relevant size M.S. rounds to required diameter, threading, welding, providing necessary templates and auxilliary dummy structures, if any, necessary tying and welding with reinforcement, adjustment of shuttering & reinforcement/any other fixture, greasing exposed metal surfaces, covering bolts and packing the sleeves with jute cloth etc. all complete as specified and directed. | .23 | MT |  | 130000.00 | 35282.00 | 76079.00 | 20647.84 | 80000.00 | 21712.00 | 20647.84 | M/s.Mitra Contractors
144.00 | Supplying, fabricating and erecting in position at all levels and locations bolted, clamped and/or welded GRATING (fabricated as per standards) made out of M.S. flats/M.S. flats with M.S. rounds in walkways, platforms, stair treads etc. including cutting to required size, shape, making holes, notches, openings of required size, nosing, straightening if required, making the edges smooth, removing the burrs, fabricating clamps, fixing, welding, preparation and submission of fabrication drawings and preparing the surfaces for painting, surface cleaning, wire brushing, removal of mill scale, dust, rust, oil or grease and applying one shop coat of Red Oxide Zinc Chromate Primer after fabrication etc. all complete as specified and directed. | 1.00 | MT |  | 130000.00 | 153400.00 | 94444.73 | 111444.78 | 90000.00 | 106200.00 | 106200.00 | Japsin Jacob Wire Drawing Pvt Ltd
| Total in Figures |  |  |  |  | 19910500.25 |  | 17770989.69 |  | 21556156.81
Lowest Amount Quoted BY: M/s.Mitra Contractors(17770989.69)

## BoQ2
Government eProcurement System Created By: SIDDHARTH KUMAR Created Date/Time: 11-Dec-2023 12:06 PM Tender Title: MODIFICATION OF FIRE WATER NETWORK FROM UNDERGROUND TO ABOVE GROUND AT IPS MANSARAMPURA AND RT SANGANER AND GTI JAIPUR Tender ID: 2023_GAIL_170546_1
Tender Inviting Authority: SR. MANAGER (C&P)
Name of Work: MODIFICATION OF FIRE WATER NETWORK FROM UNDERGROUND TO ABOVE GROUND AT GTI JAIPUR
Contract No: GAIL/JPR23SD074/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Petrofert Engineers (India)(GSTN-23BAWPS4051A1ZR) |  | M/s.Mitra Contractors(GSTN-NA) |  | Japsin Jacob Wire Drawing Pvt Ltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PIPING WORKS : SUPPLY & FABRICATION, ERECTION, INSTALLATION AND HHYDRO TESTING OF FIRE WATER NETWORK PIPING
1.10 | Size - 6.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded, Material supply and acceptance at GAIL site store | 100.00 | M |  | 2000.00 | 236000.00 | 3039.00 | 358602.00 | 2565.00 | 302670.00 | 236000.00 | Petrofert Engineers (India)
1.20 | Size - 6.0 Inch, Thk/Sch - Hvy., Material - IS-1239 (Black), BE, C.Welded,material handling, shifting, Errection, installation of above ground/underground pipe at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) & hookup with existiong/new network. | 100.00 | M |  | 1500.00 | 177000.00 | 509.00 | 60062.00 | 900.00 | 106200.00 | 60062.00 | M/s.Mitra Contractors
2.00 | Supply of Elbows as per details given below
2.10 | Size- 6.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D Material supply and acceptance at GAIL site store | 6.00 | Nos |  | 2000.00 | 14160.00 | 2009.00 | 14223.72 | 4000.00 | 28320.00 | 14160.00 | Petrofert Engineers (India)
2.20 | Size- 6.0 inch, 90 deg., Sch.40,ASTM A 234 Gr. WPB-W, ASME B-16.9, BW, 1.5D material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 6.00 | Nos |  | 1500.00 | 10620.00 | 509.00 | 3603.72 | 2500.00 | 17700.00 | 3603.72 | M/s.Mitra Contractors
3.00 | Supply of Un-Equal Tee as per details given below
3.10 | 6" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW Material supply and acceptance at GAIL site store | 4.00 | Nos |  | 8000.00 | 37760.00 | 1409.00 | 6650.48 | 9000.00 | 42480.00 | 6650.48 | M/s.Mitra Contractors
3.20 | 6" x 4", M, ASTM A 234 Gr. WPB-W, ASME B-16.9, BW material handling, shifting, Errection, installation in above ground/underground pipline network at site, fit-up with existing /new network , fabrication, Carrying out non-destructive testing & hydrotesting (excluding radiography) with pipeline network & hookup with existiong/new network. | 4.00 | Nos |  | 5000.00 | 23600.00 | 509.00 | 2402.48 | 2500.00 | 11800.00 | 2402.48 | M/s.Mitra Contractors
4.00 | RADIOGRAPHY & Other testing
4.10 | Performance of radiographic inspection of piping of all types, sizes, thickness including providing or hiring of all necessary equipment, supply of all consumables including radiographic films and whatever else even though not expressly mentioned but required to perform the work as per specification and instructions of Engineer-in-Charge. Contractor to submit DPR, Inspection Report along with Radiography Report to Engineer-in-Charge. Radiography of piping joints as per details given below:Size - 6.0 Inch | 20.00 | Nos |  | 2500.00 | 59000.00 | 609.00 | 14372.40 | 1400.00 | 33040.00 | 14372.40 | M/s.Mitra Contractors
5.00 | PIPE SUPPORTS
5.10 | Supply, fabrication and erection of pipe/ equipment supports (for all sizes/ thickness) including shoes, pipes, cross-ivers, platforms, ladders, railings etc. as required, cradles, turn buckles, T-posts for all types of guides, anchors, special supports for cold/hot insulated pipes etc. if applicable, all necessary equipment, consumables, labour etc. for completing all works including supply of bolts, nuts, washers, U-clamps, wooden blocks etc. as required for supporting, supply and application of paints and primers suitable for normal corrosive painting environment as defined in contract document and as per standard specification for painting specification, Drawings, Specification, Standards, other provisions of Contract and instruction of Engineer-in-Charge. | 1.00 | MT |  | 150000.00 | 177000.00 | 75079.00 | 88593.22 | 130000.00 | 153400.00 | 88593.22 | M/s.Mitra Contractors
6.00 | PAINTING / COATING
6.10 | Painting of all above ground piping including all fittings, valves, flanges etc. Supply of paints, solvents and primers, preparation of surfaces and application of primer (01 coat) and finish paints (02 coats or more) suitable for highly corrosive/corrosive/ normal corrosive painting environment as defined in contract document and on pipes as per standard specification for painting , identification, lettering/ numbering, colour coding etc. as specified including rub down and touch up of shop primer or scrapping of shop primer wherever required and providing of scaffolding for all heights, labour, materials, tools and tackles, consumables, supervision etc. to complete the work in all respect as per Specification, Drawings, Standards and instruction of Engineer-in- Charge. Note: The Coating thickness shall be as per the standard specification of Painting attached with the Tender document. Painting with paint shade no.536 of IS:5 | 50.00 | M2 |  | 500.00 | 29500.00 | 399.00 | 23541.00 | 500.00 | 29500.00 | 23541.00 | M/s.Mitra Contractors
6.20 | Supply of coal Tar Tape, solvents and primers and preparation of surfaces, application of primer, Coating of Below ground/above ground Carrier pipe including all fittings, valves, flanges etc. with coal tar tape. Coating of below ground carrier pipe shall be Coal Tar Tape coating as per VCS-SS-PP-0035. | 10.00 | M2 |  | 500.00 | 5900.00 | 699.00 | 8248.20 | 550.00 | 6490.00 | 5900.00 | Petrofert Engineers (India)
7.00 | CIVIL WORK FOR FIRE WATER NETWORK SYSTEM
7.01 | EARTH WORK IN FOUNDATION
7.10 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m.All kinds of soil | 10.00 | M3 |  | 300.00 | 3540.00 | 299.00 | 3528.20 | 500.00 | 5900.00 | 3528.20 | M/s.Mitra Contractors
7.20 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 10.00 | M3 |  | 350.00 | 4130.00 | 169.00 | 1994.20 | 350.00 | 4130.00 | 1994.20 | M/s.Mitra Contractors
8.00 | PLAIN & REINFORCED CEMENT CONCRETE:
8.10 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | 2.00 | M3 |  | 7000.00 | 16520.00 | 4249.00 | 10027.64 | 8750.00 | 20650.00 | 10027.64 | M/s.Mitra Contractors
8.20 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) | 3.00 | M3 |  | 8500.00 | 30090.00 | 5559.00 | 19678.86 | 8000.00 | 28320.00 | 19678.86 | M/s.Mitra Contractors
9.00 | CENTERING AND SHUTTERING
9.10 | Providing and fixing CENTERING AND SHUTTERING in foundations, footings, raft beams, slabs, pile caps, retaining walls, jambs, counter-forts, buttresses, trenches, equipment/machine foundations, pedestals, abutments, pipe sleepers, columns, plinth beams, lintels, suspended slabs, beams, staircases, landings, steps, non-circular tunnels/bunkers/silos/ shafts/ hoppers/liquid storage structures etc. including shuttering for single pour concreting, strutting, bracing, propping etc., keeping the same in position during concreting and removal of the same after specified period etc. for Straight/ Inclined Shuttering, keeping necessary provision for inserts, projecting dowels, anchor bolts or any other fixture etc. all complete and as specified and directed.For all depths below and upto & inclusive of plinth level. | 50.00 | M2 |  | 300.00 | 17700.00 | 209.00 | 12331.00 | 450.00 | 26550.00 | 12331.00 | M/s.Mitra Contractors
10.00 | REINFORCEMENT
10.10 | Supplying and placing in position HIGH STRENGTH DEFORMED STEEL BARS REINFORCEMENT (conforming to IS:1786, Grade Fe 415), for R.C.C. work including transporting the Steel, straightening, cleaning, decoiling, cutting, bending to required shapes and lengths as per details, binding with contractor's own 16 SWG black soft annealed binding wire at every intersection, supplying and placing with proper cover blocks, supports, chairs, overlaps, welding, spacers, fanhooks etc. for all heights and depths etc. all complete as directed. | .20 | MT |  | 90000.00 | 21240.00 | 47549.00 | 11221.56 | 9000.00 | 2124.00 | 2124.00 | Japsin Jacob Wire Drawing Pvt Ltd
11.00 | Fire fighting Equipments
11.10 | Supply & Erection of Fire Hydrant with single Headed landing valve Gunmetal body, IS:318, 75mm NB fanged inlet, 63mm female inst. oblique outlet, with brass spindle and CI hand wheel, complete with ABS blank cap and chain, bearing IS:5290 mark, Flange Dimension: OD-200mm,PCD-160mm, four 19mm dia holes | 2.00 | EA |  | 15000.00 | 35400.00 | 9899.00 | 23361.64 | 9000.00 | 21240.00 | 21240.00 | Japsin Jacob Wire Drawing Pvt Ltd
11.20 | Supply & Erection of Hose box for housing 02 nos of 15 meter fire fighting delivery hoses. | 6.00 | EA |  | 4500.00 | 31860.00 | 11079.00 | 78439.32 | 14000.00 | 99120.00 | 31860.00 | Petrofert Engineers (India)
11.30 | SINGLE HEADED LANDING VALVES,65-MF-FS-03 | 6.00 | EA |  | 4500.00 | 31860.00 | 7079.00 | 50119.32 | 9000.00 | 63720.00 | 31860.00 | Petrofert Engineers (India)
11.40 | Hose reel Hose hose reel tubing with drum - 30mtrs.X 3/4" , Pressure rating - with drum HOSE REEL DRUM FOR PRESSURE HOSE REEL OF office building FIRE TENDER MOCMS, CAPACITY - 30 MTR Hose Reel Drum 1. MOC- MS, Capacity - 30 mtr 2. With Gear mechanism for rolling and unrolling of hose reel. | 4.00 | EA |  | 31500.00 | 148680.00 | 7079.18 | 33413.73 | 14000.00 | 66080.00 | 33413.73 | M/s.Mitra Contractors
| Total in Figures |  |  |  |  | 1111560.00 |  | 824414.69 |  | 1069434.00
Lowest Amount Quoted BY: M/s.Mitra Contractors(824414.69)

## BOQ Summary
BOQ Summary Details Tender Title: MODIFICATION OF FIRE WATER NETWORK FROM UNDERGROUND TO ABOVE GROUND AT IPS MANSARAMPURA AND RT SANGANER AND GTI JAIPUR Tender ID: 2023_GAIL_170546_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s.Mitra Contractors | 17770989.69 | L1
| 2 | Petrofert Engineers (India) | 19910500.25 | L2
| 3 | Japsin Jacob Wire Drawing Pvt Ltd | 21556156.81 | L3
BoQ2 | 1 | M/s.Mitra Contractors | 824414.69 | L1
| 2 | Japsin Jacob Wire Drawing Pvt Ltd | 1069434.00 | L2
| 3 | Petrofert Engineers (India) | 1111560.00 | L3