## BoQ1
Government eProcurement System Created By: Bharti . Created Date/Time: 07-Sep-2023 11:35 AM Tender Title: NCRTC/EARTHING/OT/100 Tender ID: 2023_IRCON_159410_1
Tender Inviting Authority: Chief General Manager / Electrical
Name of Work: Supply, Erection, Testing & Commissioning of Earthing System for Sarai Kale Khan RSS of Delhi – Ghaziabad – Meerut RRTS Corridor of NCRTC (Package-19 Lot 1)
Contract No: IRCON/ELECT/5037-5038/NCRTC/EARTHING/OT/100
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manav Energy Pvt Ltd(GSTN-27AAICM0503D1Z0) |  | JMV LPS Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Maintenance Free Earth Pits
1.01 | SITC of Maintenance free earthing system having copper bonded steel rod of 19 MM diameter and 3/4 meter length shall be UL listed and certified. The rod shall be suitable to withstand short ckt currrent of 26.24 KA at 1 Seconds CPRI Tested. The copper bonded rod shall meet the requirements of IEC 62561-2. | 45.00 | Nos |  | 1613.00 | 510450.30 | 2500.00 | 345150.00 | 345150.00 | JMV LPS Limited
1.02 | SITC of earth enhancement material having resistivity <0.12 ohm-m shall be used in the surrounding of the earthing rods to have better resistance value. A 50 kg compound per Pit shall be installed in a bore dia. of 150 MM and 10 feet plus depth. | 90.00 | Nos |  | 2620.00 | 363204.00 | 3600.00 | 488520.00 | 363204.00 | Manav Energy Pvt Ltd
2.00 | SITC of Earth Mats using copper bonded steel rod with exothermic welded joints
2.01 | SITC of Maintenance free earthing system having copper bonded steel rod of 19 MM diameter and 4 meter length. The rod shall be suitable to withstand short ckt currrent of 26.24 KA at 1 Seconds . The copper bonded rod shall meet the requirements of IEC 62561-2. | 850.00 | Nos |  | 544.00 | 1498482.00 | 650.00 | 1654950.00 | 1498482.00 | Manav Energy Pvt Ltd
2.02 | SITC of Earthing riser 50x6 MM made up of copper bonded steel material & 4mtr length. The riser shall be exothermically welded with main earthmat & riser to riser. Riser length to be of standard length not less than 4Mtr. | 1200.00 | Nos |  | 1100.00 | 2619600.00 | 900.00 | 1982400.00 | 1982400.00 | JMV LPS Limited
3.00 | SITC of Exothermic Joints AS PER BELOW MENTIONED JOINTS:(cost of moulds to be included)
3.10 | (i) Straight Joints : 2 way between 50x6 mm Copper bonded steel strip to 50x6 mm Copper bonded steel strip (ii) Straight Joints : 2 way between 19 mm dia. rod to 19 mm dia rod. (iii) L Joint : 2 way between 19 mm dia. rod to 19 mm dia rod (iv) TEE Joint : 2 way between 19 mm dia. rod to 19 mm dia rod (v) Cross Joint: 2 way between 19 mm dia. rod to 19 mm dia rod (vi) Tee Joint : Earthing risers joints with 19 mm dia. earth rod with 50x6 MM copper bonded steel rod. (vii) TEE JOINT: 50x6mm to 50x6mm flat/strip (viii) Or any other type of joints requires as per site situation | 800.00 | Nos |  | 960.00 | 2076800.00 | 2000.00 | 2360000.00 | 2076800.00 | Manav Energy Pvt Ltd
4.00 | SITC of 50X4MM Copper flat for 220KV GIS earthing as per drawing with Copper-Copper argon joints/thermic joints/or as shown in drawing with sufficient overlaps | 160.00 | Nos |  | 1857.00 | 475209.60 | 2000.00 | 472000.00 | 472000.00 | JMV LPS Limited
5.00 | SITC of Main Earth Terminal (MET) 750mm Long 75X6 mm Copper Bonded Steel including wall mounting arrangements/suitable support insulators | 15.00 | Nos |  | 1867.00 | 42957.90 | 2500.00 | 61950.00 | 42957.90 | Manav Energy Pvt Ltd
6.00 | SITC of 50x6mm GI strip for building structure reinforcement earthing and connection with main earthmat, providing cable brackets earthing riser with earthmat etc as per drawing including wall support cleats, Nut and bolt SS & GI as per requirement | 300.00 | Nos |  | 275.00 | 338070.00 | 270.00 | 272580.00 | 272580.00 | JMV LPS Limited
7.00 | SITC of Earth Pits as per approved drawing (Brick Pit Chamber/Precast/Polyplastic/or any other) | 45.00 | Nos |  | 930.00 | 182133.00 | 2000.00 | 159300.00 | 159300.00 | JMV LPS Limited
| Total in Figures |  |  |  |  | 8106906.80 |  | 7796850.00
Lowest Amount Quoted BY: JMV LPS Limited(7796850.00)

## BOQ Summary
BOQ Summary Details Tender Title: NCRTC/EARTHING/OT/100 Tender ID: 2023_IRCON_159410_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | JMV LPS Limited | 7796850.00 | L1
| 2 | Manav Energy Pvt Ltd | 8106906.80 | L2