## BoQ1
Government eProcurement System Created By: Bidyut Roy Created Date/Time: 20-Feb-2024 12:05 PM Tender Title: Development of Solapur Airport for VFR operations SH- SITC of 2 Nos. 320 KVA DG Sets and Associated works at Solapur Airport. Tender ID: 2024_AAI_180578_1
Tender Inviting Authority: Asst. GENERAL MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, KOLHAPUR AIRPORT, KOLHAPUR.
Name of Work : DEVELOPMENT OF SOLAPUR AIRPORT FOR VFR OPERATIONS SH: SITC OF 2 NOS. 320 KVA DG SETS & ASSOCIATED WORKS AT SOLAPUR AIRPORT
Contract No: 2024 _AAI_180578_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SARASWAT ENGINEERING SERVICES(GSTN-27AAZFS6239C1ZO) |  | Kalpaka Power Control(GSTN-27ACBPN3962D1ZQ) |  | VIJAYPOWER GENERATORS LIMITED(GSTN-07AAACV0191N1Z4) |  | Virtus Techno(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | "DIESEL GENERATOR SETS" Design, Supply, Installation, Testing and Commissiong of 'Silent Type' Diesel Generating set (suitable for outdoor installation along with acoustic enclosure)alongwith having Prime Power Rating 320 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor, power command control system (Standard Control panel with 630 A, 4P, MCCB with PS0602/PC3.3 including AMF logic or equivalent installed in the acoustic enclosure), cable termination boxes suitable for end terminations of upto 3.5 x 300 Sqmm. cable, first fill of lubricationg oil and diesel for testing and commissioning (The DG set shall comply CPCB - IV + norms) and consisting of the followings including providing necessary CEA approval, insurance, Packing, loading, unloading, transportation etc. as required: (a) Diesel Engine: Diesel engine 4 stroke radiator with fan cooled, floor mounted, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continous operation. The engine will be fitted complete with all the required accessories. (b) Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key, (ii) Water temperature indication, (iii) Lubrication oil pressure indication, (iv) Lubrication oil temperature indication, (v) Battery charging indication, (vi) RPM indication, (vii) Over speed indication, (viii) Low lub. Oil trip indication, (ix) Engine Hours indication. (c) Alternator : Synchronous alternator rated at 320 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having IP-23 protection, SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR suitable for parallel operation in synchronizing mode & AMF mode conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class - F/H insulation. (d) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation (1:2:4, M20 grade), foundation and vibration isolation arrangement as per recommendations of manufacturer. Vibration isolators (AVMs) should be provided to reduce vibration transmission to the surrounding structure. Foundation shall be designed considering safe bearing capacity of soil and approved structural engineers. Item includes cost of excavation, making of foundation etc. as required for mounting of DG set as per design, no additional payment shall be made. (e) Fuel Tank: Calibrated Day service fuel tank (Free standing type) suitable for outdoor installation of 990 Ltrs. capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications, level indications with calibrated scale, provision for electronic level sensor, flange connection for inlet with float valve and over flow for automatic fuel filing system and other accessories etc. as required as per specifications. Suitable foundation as per OEM recommendation and outdoor type suitable canopy enclosed on four sides with lockable arrangement made out of M.S. sheet/Mesh as per OEM recomendations needs to be provided. (f) Exhaust System: Dry exhaust mainfold with hospital grade exhaust silencer and catalytic convertor including supply & fixing of Stainless Steel Expansion joints, Corrugated bellows suitable for 320 KVA DG set to fit in exhaust pipe. The exhaust piping including silencer inside and outside acoustic enclosure shall be thermal insulated. The exhaust pipe shall be minimum 05 mtr. above building height. The complete exhaust piping and structure shall be included in the quoted rate. (g) Starting System: 24V DC starting system (or as per manufacturer/OEM standards) comprising of starter motors, voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand, external battery charging unit etc. as required as per OEM standards. (h) Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications, meeting the latest CPCB IV+ norms. Acoustic enclosure should be type tested for Noise at the climatic conditions as per latest CPCB norms through authorized laboratory. (i) The work shall be executed as per Central Electrical Authority and Central Pollution Control Board - IV+ or latest norms as specified in tender specifications. (j) DG command control panel (PCC 3.3 or equivalent as per OEM design) suitable for synchronization with RS 485. (k) Necessary control cable shall be provided between DG Sets and DG Panel as approved by OEM manufacturer. (l) Approvals : Prepration of necessary drawing, Co-ordination and approval from Central Electrical Authority (CEA) and CPCB, Pollution control board standards as per requirement. | 2.00 | SET |  | 3667761.00 | 7335522.00 | 2834150.00 | 5668300.00 | 3147000.00 | 6294000.00 | 3306250.00 | 6612500.00 | 5668300.00 | Kalpaka Power Control
2.00 | "AMF PANEL" Design, Supply, Installation, Testing & Commissioning of automatic mains failure control including auto by-pass panel, suitable for 320 KVA silent type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine (upto 50 mtrs.) and elsewhere if required, all complete and inter locking including the following : (a) 2 nos. 4 Pole, 630 A Power Contactors (b) 2 nos. 4 Pole, 630 A, 50 KA, Ics=100% Icu, Microprocessor based MCCB (with O/L, S/C & E/F protection) AND 630 A, 4 Pole manual Change over switch to Bypass the AMF operation i/c connections & interlocking. (c) Auto/Manual/Test/Off selector switch (d) Microprocessor based latest model AMF module (of reputed make viz., Siemens /ABB /Schneider or equivalent) with provision of over load, short circuit, restricted earth fault, under frequency etc. (e) 3 Sets of current transformers 15 P 10 accuracy for protection and 15 VA class-I for metering (f) Digital VAF meter to indicate current, voltage, frequency, power factor and KWH (g) Phase Indicating lamps (R, Y, B), indicating lamps for load on mains and load on set, Battery Charger ON (h) Fuse for instruments (i) Battery charger, complete with transformer/ rectifier, D.C. voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment. (j) Control unit with three impulse automatic engine start/stop and failure to start lockout. (k) Impulse counter with locking and reset facility. (l) ON/OFF/Control circuit switch with (m) Audio/Video annunciation for (i) High water temperature (ii) Low lubricating oil pressure (iii) Engine over speed (iv) Engine fails to start (v) Full load/maximum load warning All other accessories i/c wiring, relays, MCBs, Contactors, switches, etc. required for AMF operation as per Technical Specifications deemed to be included in the item. | 2.00 | Job |  | 735804.00 | 1471608.00 | 705650.00 | 1411300.00 | 715200.00 | 1430400.00 | 391000.00 | 782000.00 | 782000.00 | Virtus Techno
3.00 | "MAIN LT ESSENTIAL PANEL" Design, Supply, installation, testing & commissioning of cubicle TTA type, indoor LT panel as per IEC 61439, IS 8623:1993, IP 42 suitable for 415 V, 3 Phase, 4 Wire, 50 Hz, AC supply system fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates for top & Bottom entry, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN aluminium alloy bus bars with 100% neutral bus as that of phase bus capacity of hight conductivity, supported with SMC bus bar supports, with short circuit withstand capacity as per design, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/flexible copper connections from main earth bus bar to switch gears with required size of Copper conductors/bus bars and control wiring with 2.5 sq. mm. FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two half, i/c contol & interlocking of incomers, bus coupler and providing Surge Protection Devices (SPDs) including following switch gears, accessories as per specifications: All MCCBs should be provided with front operated extended rotary handle and spreader links. The electrical panel shall be fully ventilated to maintain intemal body temp. < 40 deg 'C' when room amb. temp. is equal of less than 35 deg 'C'. Required ventilation fans shall be provided and tested. All back access panel shall be housed with encapsulated spark gap based Type-1/Class A SPD wih inbuilt fuse for each incomer at each bus section of 100 kA, 10/350 mS as per IS/IEC 62305-3LPL-I. All front operated panel/sub panels shall be housed with MOV (Metal Oxide Varistor) based Type-2/Class B SPD wih inbuilt fuse for each incomer at each bus section of In 1 & Irms 20 kA, 5/20 mS, as per IS/IEC 62305-3 LPL-I. Each panel shall be equipped with Automatic Fire Suppression system, having linear pneumatic heat detection tube based with Novec 1230. The system shall be LPCB approved & coordination with Fire alarm system etc. suitable for the panel size accordane with specifications, NEC-2011, NBC ammended upto date. Incomer: (a) 630 A, 4P MCCB, Microprocessor based release (lcs = Icu = 50kA) with inbuilt O/L , S/C & E/F protection as per specification - 2 Nos (b) R, Y, B phase indicating LED lamps with 2 amp back up MCB - 2 Set (c) 96 x 96 sqmm digital MFM meter and 3 Nos cast resin CTs of ratio 630/5 A, class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI & Individual Odd Harmonics Iow voltage and current including THD upto 31st Order with RS-485 port - 2 Set (d) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 2 Set Buscoupler: (a) 630A 4P MCCB, Microprocessor based release (lcs = Icu = 50 kA) with inbuilt O/L , S/C & E/F protection as per specification - 1 No. (b) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 1 Set (c) Electrical & Mechanical interlocking between both incomers and Bus coupler Busbars: 4P aluminium busbars of 1600 A capacity with heat shrinkable coloured sleeves incl. SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 50 KA for 1 sec. Outgoing: (a) 04 Nos. 250 A, 4P MCCB with built in Microprocessor based release with adjustable thermal setting (lcs = Icu =35 KA) (b) 06 Nos. 160 A, 4P MCCB with built in thermal magnetic release with adjustable thermal setting (lcs = Icu =35 KA) (c) 08 Nos. 125A, 4P MCCB with built in thermal magnetic release with adjustable thermal setting (lcs = Icu =35 KA) (d) 10 Nos. 63 A, 4P MCCB with built in thermal magnetic release with adjustable thermal setting (lcs = Icu =35 KA) Each outgoing MCCB/Feeder should be provided with: (i) 1 Set of ON, OFF indicating lamp with 2 A MCB for protection along with wiring as required. | 1.00 | JOB |  | 1615343.00 | 1615343.00 | 1661000.00 | 1661000.00 | 1431000.00 | 1431000.00 | 994500.00 | 994500.00 | 994500.00 | Virtus Techno
4.00 | "MAIN LT NON-ESSENTIAL PANEL" Design, Supply, installation, testing & commissioning of cubicle TTA type, indoor LT panel as per IEC 61439, IS 8623:1993, IP 42 suitable for 415 V, 3 Phase, 4 Wire, 50 Hz, AC supply system fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates for top & Bottom entry, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN aluminium alloy bus bars with 100% neutral bus as that of phase bus capacity of hight conductivity, supported with SMC bus bar supports, with short circuit withstand capacity as per design, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/flexible copper connections from main earth bus bar to switch gears with required size of Copper conductors/bus bars and control wiring with 2.5 sq. mm. FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two half, i/c contol & interlocking of incomers, bus coupler and providing Surge Protection Devices (SPDs) including following switch gears, accessories as per specifications: All MCCBs should be provided with front operated extended rotary handle and spreader links. The electrical panel shall be fully ventilated to maintain intemal body temp. < 40 deg 'C' when room amb. temp. is equal of less than 35 deg 'C'. Required ventilation fans shall be provided and tested. All back access panel shall be housed with encapsulated spark gap based Type-1/Class A SPD wih inbuilt fuse for each incomer at each bus section of 100 kA, 10/350 mS as per IS/IEC 62305-3LPL-I. All front operated panel/sub panels shall be housed with MOV (Metal Oxide Varistor) based Type-2/Class B SPD wih inbuilt fuse for each incomer at each bus section of In 1 & Irms 20 kA, 5/20 mS, as per IS/IEC 62305-3 LPL-I. Each panel shall be equipped with Automatic Fire Suppression system, having linear pneumatic heat detection tube based with Novec 1230. The system shall be LPCB approved & coordination with Fire alarm system etc. suitable for the panel size accordane with specifications, NEC-2011, NBC ammended upto date. INCOMERS: (a) 630 A, 4P MCCB with built in Microprocessor based release with adjustable thermal setting (lcs = Icu =50 KA) with inbuilt O/L , S/C & E/F protection as per specification - 2 Nos. (b) R, Y, B phase indicating LED lamps with 2 amp back up MCB - 2 Set (c) 96 x 96 sqmm digital MFM meter and 3 Nos cast resin CTs of ratio 630/5 A, class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI & Individual Odd Harmonics Ior voltage and current including THD upto 31st Order with RS-485 port - 2 Set. (d) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 2 Set BUSCOUPLER: (a) 630A 4P MCCB, Microprocessor based release (lcs = Icu = 50 kA) with inbuilt O/L , S/C & E/F protection as per specification - 1 No. (b) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 1 Set (c) Electrical & Mechanical interlocking between both incomers and Bus coupler BUSBARS: 4P aluminium busbars of 1600 A capacity with heat shrinkable coloured sleeves incl. SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 50 KA for 1 sec. OTGOING: (a) 02 Nos. 630 A, 4P MCCB with built in Microprocessor based release with adjustable thermal setting (lcs = Icu = 35 KA) (b) 02 Nos. 250 A, 4P MCCB with built inMicroprocessor based release with adjustable thermal setting (lcs = Icu =35 KA) (c) 02 Nos. 125A, 4P MCCB with built in thermal magnetic release with adjustable thermal setting (lcs = Icu =35 KA) Each outgoing MCCB/Feeder should be provided with: (i) 1 Set of ON, OFF indicating lamp with 2 A MCB for protection along with wiring as required. | 1.00 | JOB |  | 1061581.00 | 1061581.00 | 1006500.00 | 1006500.00 | 8670000.00 | 8670000.00 | 731250.00 | 731250.00 | 731250.00 | Virtus Techno
5.00 | Dismantling of Exisitng 125 KVA DG set along with AMF panels terminations, cable connections, Diesel Tanks including shifting to store or as directed by E-I-C etc. complete as required. | 1.00 | Job |  | 34650.00 | 34650.00 | 30000.00 | 30000.00 | 210000.00 | 210000.00 | 17550.00 | 17550.00 | 17550.00 | Virtus Techno
6.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, MCCB incomer TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs/MCCB (but without outgoing MCBs and MCCB incomer) as required. 8 way (4 + 24), Double door | 2.00 | EACH |  | 13183.00 | 26366.00 | 14798.00 | 29596.00 | 8910.00 | 17820.00 | 14625.00 | 29250.00 | 17820.00 | VIJAYPOWER GENERATORS LIMITED
7.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/ Isolator) 8 way (4 + 24), Double door | 2.00 | EACH |  | 9279.00 | 18558.00 | 8252.00 | 16504.00 | 4500.00 | 9000.00 | 6844.50 | 13689.00 | 9000.00 | VIJAYPOWER GENERATORS LIMITED
8.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way, Double door | 2.00 | EACH |  | 7592.00 | 15184.00 | 2561.00 | 5122.00 | 1701.00 | 3402.00 | 3451.50 | 6903.00 | 3402.00 | VIJAYPOWER GENERATORS LIMITED
9.00 | Supplying and fixing Cable End Box (Loose wire box) (IP 43) suitable for following single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with testing and commissioning etc. as required. For 8 way, Double door SPN MCBDB | 2.00 | EACH |  | 3494.00 | 6988.00 | 1452.00 | 2904.00 | 711.00 | 1422.00 | 1345.50 | 2691.00 | 1422.00 | VIJAYPOWER GENERATORS LIMITED
10.00 | Supplying and fixing Cable End Box (Loose wire box) (IP 43) suitable for following triple pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with testing and commissioning etc. as required. For 8 way, Double door TPN MCBDB | 2.00 | EACH |  | 5244.00 | 10488.00 | 836.00 | 1672.00 | 1212.00 | 2424.00 | 2515.50 | 5031.00 | 1672.00 | Kalpaka Power Control
11.00 | Supplying and fixing Cable End Box (Loose wire box) suitable for triple pole and neutral, sheet steel, Vertical MCB distribution board, 415 V, on surface/ recess, complete with testing and commissioning etc. as required. | 2.00 | EACH |  | 5244.00 | 10488.00 | 983.00 | 1966.00 | 2220.00 | 4440.00 | 3393.00 | 6786.00 | 1966.00 | Kalpaka Power Control
12.00 | Supplying and fixing 6 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 76.00 | EACH |  | 240.00 | 18240.00 | 242.00 | 18392.00 | 234.00 | 17784.00 | 144.78 | 11003.28 | 11003.28 | Virtus Techno
13.00 | Supplying and fixing 6 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Double pole | 2.00 | EACH |  | 642.00 | 1284.00 | 595.00 | 1190.00 | 504.00 | 1008.00 | 465.54 | 931.08 | 931.08 | Virtus Techno
14.00 | Supplying and fixing 6 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple pole | 32.00 | EACH |  | 973.00 | 31136.00 | 881.00 | 28192.00 | 796.00 | 25472.00 | 753.48 | 24111.36 | 24111.36 | Virtus Techno
15.00 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 amps | 2.00 | EACH |  | 486.00 | 972.00 | 405.00 | 810.00 | 450.00 | 900.00 | 285.25 | 570.50 | 570.50 | Virtus Techno
16.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 amps | 1.00 | EACH |  | 871.00 | 871.00 | 790.00 | 790.00 | 879.00 | 879.00 | 535.16 | 535.16 | 535.16 | Virtus Techno
17.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 amps | 1.00 | EACH |  | 1000.00 | 1000.00 | 844.00 | 844.00 | 954.00 | 954.00 | 670.06 | 670.06 | 670.06 | Virtus Techno
18.00 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 amps | 8.00 | EACH |  | 2541.00 | 20328.00 | 2369.00 | 18952.00 | 2106.00 | 16848.00 | 1988.65 | 15909.20 | 15909.20 | Virtus Techno
19.00 | Providing and fixing following rating and breaking capacity MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel/MCCB Distribution board including connections, testing, commissioning etc. as required. 100 A, FP, 25 KA, (Ics=Icu=100%) | 2.00 | EACH |  | 5775.00 | 11550.00 | 4202.00 | 8404.00 | 1449.00 | 2898.00 | 6379.78 | 12759.56 | 2898.00 | VIJAYPOWER GENERATORS LIMITED
20.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 200.00 | METRE |  | 809.00 | 161800.00 | 634.00 | 126800.00 | 1284.00 | 256800.00 | 409.50 | 81900.00 | 81900.00 | Virtus Techno
21.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 300 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | METRE |  | 1179.00 | 117900.00 | 794.00 | 79400.00 | 1617.00 | 161700.00 | 614.25 | 61425.00 | 61425.00 | Virtus Techno
22.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 450 mm width X 50 mm depth X 2.0 mm thickness | 60.00 | METRE |  | 1830.00 | 109800.00 | 952.00 | 57120.00 | 1998.00 | 119880.00 | 848.25 | 50895.00 | 50895.00 | Virtus Techno
23.00 | Supply of following sizes LT power cable of 1.1 KV grade of following sizes aluminum conductor XLPE insulated PVC sheathed armored cable confirming to IS 7098/1/1988 with upto date amendment as required. 3.5 x 300 sq.mm. Al Aromured XLPE cable | 2680.00 | METRE |  | 1081.00 | 2897080.00 | 1250.00 | 3350000.00 | 1167.00 | 3127560.00 | 1145.07 | 3068787.60 | 2897080.00 | SARASWAT ENGINEERING SERVICES
24.00 | Supply of following sizes LT power cable of 1.1 KV grade of following sizes aluminum conductor XLPE insulated PVC sheathed armored cable confirming to IS 7098/1/1988 with upto date amendment as required. 3.5 x 50 sq.mm. Al Aromured XLPE cable | 500.00 | METRE |  | 224.00 | 112000.00 | 300.00 | 150000.00 | 240.00 | 120000.00 | 591.90 | 295950.00 | 112000.00 | SARASWAT ENGINEERING SERVICES
25.00 | Supply of following sizes LT power cable of 1.1 KV grade of following sizes aluminum conductor XLPE insulated PVC sheathed armored cable confirming to IS 7098/1/1988 with upto date amendment as required. 3.5 x 35 sq.mm. Al Aromured XLPE cable | 500.00 | METRE |  | 167.00 | 83500.00 | 250.00 | 125000.00 | 180.00 | 90000.00 | 179.83 | 89915.00 | 83500.00 | SARASWAT ENGINEERING SERVICES
26.00 | Supply of following sizes LT power cable of 1.1 KV grade of following sizes aluminum conductor XLPE insulated PVC sheathed armored cable confirming to IS 7098/1/1988 with upto date amendment as required. 3.5 x 25 sq.mm. Al Aromured XLPE cable | 500.00 | METRE |  | 135.00 | 67500.00 | 200.00 | 100000.00 | 144.00 | 72000.00 | 145.56 | 72780.00 | 67500.00 | SARASWAT ENGINEERING SERVICES
27.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL / HDPE pipe as required. Upto 35 sq. mm | 70.00 | METRE |  | 46.00 | 3220.00 | 100.00 | 7000.00 | 50.00 | 3500.00 | 35.10 | 2457.00 | 2457.00 | Virtus Techno
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL / HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 70.00 | METRE |  | 58.00 | 4060.00 | 100.00 | 7000.00 | 70.00 | 4900.00 | 64.35 | 4504.50 | 4060.00 | SARASWAT ENGINEERING SERVICES
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL / HDPE pipe as required. Above 185 sq. mm and upto 400 sq. mm | 2410.00 | METRE |  | 98.00 | 236180.00 | 150.00 | 361500.00 | 99.00 | 238590.00 | 128.70 | 310167.00 | 236180.00 | SARASWAT ENGINEERING SERVICES
30.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Upto 35 sq. mm | 80.00 | METRE |  | 46.00 | 3680.00 | 100.00 | 8000.00 | 30.00 | 2400.00 | 40.95 | 3276.00 | 2400.00 | VIJAYPOWER GENERATORS LIMITED
31.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 80.00 | METRE |  | 76.00 | 6080.00 | 100.00 | 8000.00 | 36.00 | 2880.00 | 64.35 | 5148.00 | 2880.00 | VIJAYPOWER GENERATORS LIMITED
32.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 180.00 | METRE |  | 99.00 | 17820.00 | 150.00 | 27000.00 | 51.00 | 9180.00 | 99.45 | 17901.00 | 9180.00 | VIJAYPOWER GENERATORS LIMITED
33.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 400.00 | METRE |  | 46.00 | 18400.00 | 100.00 | 40000.00 | 57.00 | 22800.00 | 40.95 | 16380.00 | 16380.00 | Virtus Techno
34.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 800.00 | METRE |  | 83.00 | 66400.00 | 100.00 | 80000.00 | 75.00 | 60000.00 | 81.90 | 65520.00 | 60000.00 | VIJAYPOWER GENERATORS LIMITED
35.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 90.00 | METRE |  | 116.00 | 10440.00 | 150.00 | 13500.00 | 105.00 | 9450.00 | 140.40 | 12636.00 | 9450.00 | VIJAYPOWER GENERATORS LIMITED
36.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 X 300 sq. mm (70 mm) | 24.00 | SET |  | 1945.00 | 46680.00 | 1500.00 | 36000.00 | 1200.00 | 28800.00 | 936.00 | 22464.00 | 22464.00 | Virtus Techno
37.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 x 70 Sqmm (38 mm) | 10.00 | SET |  | 712.00 | 7120.00 | 900.00 | 9000.00 | 702.00 | 7020.00 | 526.50 | 5265.00 | 5265.00 | Virtus Techno
38.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 x 35 Sqmm (32 mm) | 10.00 | SET |  | 510.00 | 5100.00 | 700.00 | 7000.00 | 600.00 | 6000.00 | 351.00 | 3510.00 | 3510.00 | Virtus Techno
39.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 x 25 Sqmm (28 mm) | 10.00 | SET |  | 452.00 | 4520.00 | 600.00 | 6000.00 | 510.00 | 5100.00 | 234.00 | 2340.00 | 2340.00 | Virtus Techno
40.00 | Supplying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 2500.00 | METRE |  | 119.00 | 297500.00 | 200.00 | 500000.00 | 180.00 | 450000.00 | 140.40 | 351000.00 | 297500.00 | SARASWAT ENGINEERING SERVICES
41.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 2500.00 | METRE |  | 173.00 | 432500.00 | 200.00 | 500000.00 | 105.00 | 262500.00 | 111.15 | 277875.00 | 262500.00 | VIJAYPOWER GENERATORS LIMITED
42.00 | Providing, laying and fixing pf following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc as required. 150 mm Dia. | 50.00 | METRE |  | 2539.00 | 126950.00 | 3368.00 | 168400.00 | 1980.00 | 99000.00 | 1755.00 | 87750.00 | 87750.00 | Virtus Techno
43.00 | Providing, laying and fixing pf following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc as required. 80 mm Dia. | 30.00 | METRE |  | 1094.00 | 32820.00 | 1600.00 | 48000.00 | 900.00 | 27000.00 | 857.61 | 25728.30 | 25728.30 | Virtus Techno
44.00 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. (a) 300 mm dia | 30.00 | METRE |  | 706.00 | 21180.00 | 1320.00 | 39600.00 | 702.00 | 21060.00 | 994.50 | 29835.00 | 21060.00 | VIJAYPOWER GENERATORS LIMITED
45.00 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 5.00 | CUM |  | 578.00 | 2890.00 | 500.00 | 2500.00 | 1200.00 | 6000.00 | 526.50 | 2632.50 | 2500.00 | Kalpaka Power Control
46.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres | 10.00 | CUM |  | 2310.00 | 23100.00 | 500.00 | 5000.00 | 1800.00 | 18000.00 | 994.50 | 9945.00 | 5000.00 | Kalpaka Power Control
47.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in crossings, trenches etc. including form work as required. | 10.00 | CUM |  | 8663.00 | 86630.00 | 12000.00 | 120000.00 | 7500.00 | 75000.00 | 5265.00 | 52650.00 | 52650.00 | Virtus Techno
48.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 6.00 | SET |  | 12472.00 | 74832.00 | 15000.00 | 90000.00 | 6600.00 | 39600.00 | 6201.00 | 37206.00 | 37206.00 | Virtus Techno
49.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | SET |  | 22995.00 | 91980.00 | 20000.00 | 80000.00 | 17400.00 | 69600.00 | 13806.00 | 55224.00 | 55224.00 | Virtus Techno
50.00 | Providing and fixing earth bus of 50 mm x 5 mm copper strip on surface for connection etc. as required. | 2.00 | METRE |  | 3187.00 | 6374.00 | 2000.00 | 4000.00 | 2709.00 | 5418.00 | 2237.63 | 4475.26 | 4000.00 | Kalpaka Power Control
51.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | METRE |  | 1818.00 | 54540.00 | 2000.00 | 60000.00 | 1593.00 | 47790.00 | 1118.81 | 33564.30 | 33564.30 | Virtus Techno
52.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 90.00 | METRE |  | 734.00 | 66060.00 | 850.00 | 76500.00 | 453.00 | 40770.00 | 111.15 | 10003.50 | 10003.50 | Virtus Techno
53.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | METRE |  | 1312.00 | 26240.00 | 1470.00 | 29400.00 | 1254.00 | 25080.00 | 1118.81 | 22376.20 | 22376.20 | Virtus Techno
54.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 40.00 | METRE |  | 189.00 | 7560.00 | 354.00 | 14160.00 | 204.00 | 8160.00 | 111.15 | 4446.00 | 4446.00 | Virtus Techno
55.00 | Providing and fixing 6 SWG dia GI wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/cable as required. | 3000.00 | METRE |  | 35.00 | 105000.00 | 16.00 | 48000.00 | 12.00 | 36000.00 | 18.72 | 56160.00 | 36000.00 | VIJAYPOWER GENERATORS LIMITED
56.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 4.00 | Each |  | 814.00 | 3256.00 | 500.00 | 2000.00 | 360.00 | 1440.00 | 585.00 | 2340.00 | 1440.00 | VIJAYPOWER GENERATORS LIMITED
57.00 | Providing and fixing carbon dioxide (CO2) type fire extinguishers confi rming to IS 2878 : 1976 and cylinders fully charged of following capacity. (a) 4.5 KG | 10.00 | Each |  | 7583.00 | 75830.00 | 8000.00 | 80000.00 | 7500.00 | 75000.00 | 4446.00 | 44460.00 | 44460.00 | Virtus Techno
58.00 | Supply and fixing of foam fire extinguishers, Portable type 9 lit capacity hanged on wall with bracket complete as required. | 10.00 | Each |  | 4083.00 | 40830.00 | 11000.00 | 110000.00 | 7500.00 | 75000.00 | 1170.00 | 11700.00 | 11700.00 | Virtus Techno
59.00 | Supply and fixing safety instruction chart written in English, Hindi and local language in word duly framed with 5 mm thick glass as required. (Approx. from area 1.20 Sq.mt). | 2.00 | Each |  | 1164.00 | 2328.00 | 4000.00 | 8000.00 | 1800.00 | 3600.00 | 2164.50 | 4329.00 | 2328.00 | SARASWAT ENGINEERING SERVICES
60.00 | Providing of set of 4 Nos. 9.5 Litre capacity G.I. bucket painted in post office red colour with prior coat of red oxide paint and written with white paint 'FIRE' and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. | 2.00 | SET |  | 4545.00 | 9090.00 | 5000.00 | 10000.00 | 2700.00 | 5400.00 | 3042.00 | 6084.00 | 5400.00 | VIJAYPOWER GENERATORS LIMITED
61.00 | Providing of First aid box as approved by St. John Ambulance Brigade /Indian Red Cross conforming to IS:2217 - 1963. (Wall mounting type Metal Box suitable for workplace with lock & key arrangement) | 1.00 | Each |  | 1398.00 | 1398.00 | 8500.00 | 8500.00 | 1200.00 | 1200.00 | 1170.00 | 1170.00 | 1170.00 | Virtus Techno
62.00 | Supply and fixing Shock treatment chart written in English, Hindi and local language in word duly framed with 5 mm thick glass as required. (Approx. from area 1.20 Sq.mt). | 2.00 | Each |  | 1164.00 | 2328.00 | 3000.00 | 6000.00 | 1800.00 | 3600.00 | 2164.50 | 4329.00 | 2328.00 | SARASWAT ENGINEERING SERVICES
63.00 | Providing & fixing in position 1000 mm wide, Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable upto 3.3 KV, fire retardant, no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip, marking on top). | 30.00 | Metre |  | 901.00 | 27030.00 | 2000.00 | 60000.00 | 900.00 | 27000.00 | 643.50 | 19305.00 | 19305.00 | Virtus Techno
64.00 | Providing 1 inch dual directional cast iron heavy duty barrel Pump with steel discharge spout suitable for Transferring Oil/Diesel/Kerosene etc. complete as required. | 1.00 | Each |  | 6999.00 | 6999.00 | 20000.00 | 20000.00 | 1800.00 | 1800.00 | 4188.60 | 4188.60 | 1800.00 | VIJAYPOWER GENERATORS LIMITED
| Total in Figures |  |  |  |  | 17296682.00 |  | 16600818.00 |  | 23914229.00 |  | 14620637.96
Lowest Amount Quoted BY: Virtus Techno(14620637.96)

## BOQ Summary
BOQ Summary Details Tender Title: Development of Solapur Airport for VFR operations SH- SITC of 2 Nos. 320 KVA DG Sets and Associated works at Solapur Airport. Tender ID: 2024_AAI_180578_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Virtus Techno | 14620637.96 | L1
| 2 | Kalpaka Power Control | 16600818.00 | L2
| 3 | SARASWAT ENGINEERING SERVICES | 17296682.00 | L3
| 4 | VIJAYPOWER GENERATORS LIMITED | 23914229.00 | L4