## BoQ1
Government eProcurement System Created By: Madan Mohan Agrawal Created Date/Time: 14-Feb-2024 04:36 PM Tender Title: Establishment of MET park at Surat Airport. Sub Head.Supply and laying of LT Cable , OFC cable and associated electrical works. Tender ID: 2024_AAI_180989_1
Tender Inviting Authority: AGM (E-E), AAI, Surat Airport, Surat
Name of Work :"Establishment of MET park at Surat Airport. SH: Supply & laying of LT Cable , OFC cable and associated electrical works."
Contract No: Tender ID 2024_AAI_180989_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | Ascent Electrification Engineers(GSTN-24AAOFA2574R1ZU) |  | Mayur Electric Works(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of online UPS with minimum 2kVA capacity, single phase in & single phase out with double conversion, IGBT based techenology at inverter and rectifier , as per technical specifications/data sheet enclosed. The UPS shall have standard features like in built automatic 100% rated static by pass, maintenance by pass, active input power factor correction, phase sequence corrector, pure sine wave output, input-output isolation switch , in built isolation transformer at output, compatibility with generator supply, cold start capability, EMI/RFI noise filter, user friendly LCD display, suitable to operate at 230V, 50Hz, single Phase AC supply and necessary safety protection. The job also includes supply and connecting the suitable required number of 12V, SMF batteries of suitable amp hour, for the UPS to give a backup time of minimum 15 minutes at the rated full load integrated with UPS, battery rack, connectors, wiring, cabling between battery bank and UPS with insulated copper conductor of required size, termination as per site condition etc. complete as required, housed in a weather proof encloser having free air flow arrangement and insect trap mesh with mounting stand etc. having following a) 20 amps MCB for incoming power – 1no. b) 5 amps MCB for output power -3Nos. c) 10 amps MCB for output power – 1no. d) Power distribution board with 5 amps socket - 5nos. Complete as required | 1.00 | Job |  | 100000.00 | 100000.00 | 250000.00 | 250000.00 | 150000.00 | 150000.00 | 250000.00 | 250000.00 | 100000.00 | CENTRE TAP ENGINEERING
2.00 | Supply of 4 x 35 sqmm sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date. | 1200.00 | Meter |  | 300.00 | 360000.00 | 500.00 | 600000.00 | 225.00 | 270000.00 | 300.00 | 360000.00 | 270000.00 | Ascent Electrification Engineers
3.00 | Supply of Armoured Single Mode 6 core 9/125mm Optical Fibre Cable confirming to required IS with up to date amendments and as per technical specification etc. complete as required. | 1200.00 | Meter |  | 40.00 | 48000.00 | 150.00 | 180000.00 | 68.75 | 82500.00 | 60.00 | 72000.00 | 48000.00 | CENTRE TAP ENGINEERING
4.00 | Supply , installation , testing and commissioning of 24 Port outdoor LIU ( Patch panel) for Optical Fibre cable Rack mountable/ Wall mountable complete with splice tray, cable spool, Duplex Adaptor Module panel, Adaptor SC Duplex, SC Duplex Pigtail 1 meter. Job include splicing of core, fixing, testing for reflection and attennuation (db) with OTDR etc complete as required | 2.00 | Job |  | 25000.00 | 50000.00 | 125000.00 | 250000.00 | 25500.00 | 51000.00 | 45000.00 | 90000.00 | 50000.00 | CENTRE TAP ENGINEERING
5.00 | Supplying and Fixing of 2 Port Dual Fiber Media Converter with RJ 45 required for OFC complete as required. | 4.00 | Job |  | 3000.00 | 12000.00 | 31500.00 | 126000.00 | 6500.00 | 26000.00 | 15000.00 | 60000.00 | 12000.00 | CENTRE TAP ENGINEERING
6.00 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/recessed steel/ PVC conduit as required. | 160.00 | Meter |  | 50.00 | 8000.00 | 185.00 | 29600.00 | 100.00 | 16000.00 | 80.00 | 12800.00 | 8000.00 | CENTRE TAP ENGINEERING
7.00 | Wiring for light/ power plug with 2X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit (FRLS) alongwith 1 No 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 20.00 | Meter |  | 250.00 | 5000.00 | 300.00 | 6000.00 | 187.20 | 3744.00 | 200.00 | 4000.00 | 3744.00 | Ascent Electrification Engineers
8.00 | Wiring for light/ power plug with 4X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit (FRLS) alongwith 2 Nos 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 10.00 | Meter |  | 400.00 | 4000.00 | 600.00 | 6000.00 | 302.40 | 3024.00 | 250.00 | 2500.00 | 2500.00 | Mayur Electric Works
9.00 | Supplying and fixing suitable size surface PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 6.00 | Each |  | 450.00 | 2700.00 | 300.00 | 1800.00 | 350.00 | 2100.00 | 850.00 | 5100.00 | 1800.00 | jaydeep agency corporation
10.00 | Supplying and fixing suitable size surface PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 6.00 | Each |  | 500.00 | 3000.00 | 500.00 | 3000.00 | 550.00 | 3300.00 | 1250.00 | 7500.00 | 3000.00 | CENTRE TAP ENGINEERING, jaydeep agency corporation
11.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
11.01 | 20 mm | 160.00 | Meter |  | 100.00 | 16000.00 | 65.00 | 10400.00 | 45.00 | 7200.00 | 50.00 | 8000.00 | 7200.00 | Ascent Electrification Engineers
11.02 | 25 mm | 160.00 | Meter |  | 150.00 | 24000.00 | 75.00 | 12000.00 | 45.00 | 7200.00 | 65.00 | 10400.00 | 7200.00 | Ascent Electrification Engineers
12.00 | Supply of 40 mm nominal dia PLB HDPE pipe, conforming to TEC, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., complete in all respect as per direction of Engineer-in-Charge. required. | 2200.00 | Meter |  | 50.00 | 110000.00 | 325.00 | 715000.00 | 609.00 | 1339800.00 | 100.00 | 220000.00 | 110000.00 | CENTRE TAP ENGINEERING
13.00 | Supply of 90mm (OD-90mm, PN 8, PE 80) ISI marked HDPE pipe, conforming to IS 4984, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., etc. complete in all respect as per direction of Engineer-in-Charge. required. | 200.00 | Meter |  | 300.00 | 60000.00 | 525.00 | 105000.00 | 1177.00 | 235400.00 | 250.00 | 50000.00 | 50000.00 | Mayur Electric Works
14.00 | Laying of 40 mm dia. PLB HDPE pipe, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., by HDD trenchless method direct in ground in all type of soil (upto 3 Mtrs) etc. complete in all respect as per direction of Engineer-in-Charge. required. | 1900.00 | Meter |  | 720.00 | 1368000.00 | 300.00 | 570000.00 | 100.00 | 190000.00 | 500.00 | 950000.00 | 190000.00 | Ascent Electrification Engineers
15.00 | Laying of 90mm (OD-90mm, PN 8, PE 80) ISI marked HDPE pipe, along with all acessories like socket, bend, couplers, suitable size PP rope as required including fitting, cutting, jointing etc with HDD trenchless method direct in ground ( 6 mtrs below ground level ) in all type of soil etc. complete in all respect as per direction of Engineer-in-Charge. required. | 200.00 | Meter |  | 2000.00 | 400000.00 | 300.00 | 60000.00 | 100.00 | 20000.00 | 500.00 | 100000.00 | 20000.00 | Ascent Electrification Engineers
16.00 | Laying of 40 mm dia PLB HDPE pipe, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., direct in ground (75 cm below ground level, width of the trench 25 cm) including excavation & refilling the trench with same excavated earth but excluding sand cushioning and protective covering etc., complete as required. | 100.00 | Meter |  | 150.00 | 15000.00 | 70.00 | 7000.00 | 50.00 | 5000.00 | 200.00 | 20000.00 | 5000.00 | Ascent Electrification Engineers
17.00 | Laying of 40 mm dia PLB HDPE pipe, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., direct in ground (100 cm below ground level, width of the trench 25 cm) including excavation & refilling the trench with same excavated earth but excluding sand cushioning and protective covering etc., complete as required. | 100.00 | Meter |  | 150.00 | 15000.00 | 85.00 | 8500.00 | 50.00 | 5000.00 | 250.00 | 25000.00 | 5000.00 | Ascent Electrification Engineers
18.00 | Fixing 40 mm dia PLB HDPE pipe, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc. on wall surface complete in all respect as per direction of Engineer-in-Charge. required. | 100.00 | Meter |  | 50.00 | 5000.00 | 40.00 | 4000.00 | 50.00 | 5000.00 | 350.00 | 35000.00 | 4000.00 | jaydeep agency corporation
19.00 | Supply and fixing of full round type prefabricated RCC joint chamber with diameter of 85cm(ID) and height of 100cm and thikness of 7.5cm round top cover with diameter of 100cm and thickness of 5cm etc complete as required. | 12.00 | Job |  | 10000.00 | 120000.00 | 5430.00 | 65160.00 | 1500.00 | 18000.00 | 15000.00 | 180000.00 | 18000.00 | Ascent Electrification Engineers
20.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of upto 35 sq. mm size on wall surface as required. | 50.00 | Meter |  | 50.00 | 2500.00 | 45.00 | 2250.00 | 25.00 | 1250.00 | 80.00 | 4000.00 | 1250.00 | Ascent Electrification Engineers
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of upto 35 sq. mm size/ OFC in the existing RCC/ HUME/ METAL/trenched HDPE pipe as required | 2300.00 | Meter |  | 30.00 | 69000.00 | 35.00 | 80500.00 | 25.00 | 57500.00 | 80.00 | 184000.00 | 57500.00 | Ascent Electrification Engineers
22.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4 X 35 sq. mm (32 mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Set |  | 500.00 | 1000.00 | 400.00 | 800.00 | 350.00 | 700.00 | 450.00 | 900.00 | 700.00 | Ascent Electrification Engineers
23.00 | Providing and fixing 6 SWG dia G.l. wire on surface or in recess or on cable tray for loop earthing along with existing cable as required. | 1200.00 | Meter |  | 50.00 | 60000.00 | 28.00 | 33600.00 | 25.00 | 30000.00 | 27.00 | 32400.00 | 30000.00 | Ascent Electrification Engineers
24.00 | SITC of maintenance free chemical earthing system in CROWFOT method with all suitable components / accessories and using 3" Dia & 0.12" thick copper tube of 8 feet length and 04 nos. 16 mm dia SS road of 8 feet length each and the earth pit being treated with chemical gel so as to achieve earth resistance interconnected using 25x3mm copper strip (max. 6mtrs) backfilled with ISOGEL earth enhancing compound of 60kgs. heavy duty plastic inspection chamber (01 No.) along with excavation & refilling etc as required including extra materials if required to achieve earth resistance less that 0.5 ohms. | 2.00 | Set |  | 100000.00 | 200000.00 | 19850.00 | 39700.00 | 15000.00 | 30000.00 | 25000.00 | 50000.00 | 30000.00 | Ascent Electrification Engineers
25.00 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 50.00 | Meter |  | 500.00 | 25000.00 | 285.00 | 14250.00 | 350.00 | 17500.00 | 1500.00 | 75000.00 | 14250.00 | jaydeep agency corporation
| Total in Figures |  |  |  |  | 3083200.00 |  | 3180560.00 |  | 2577218.00 |  | 2808600.00
Lowest Amount Quoted BY: Ascent Electrification Engineers(2577218.00)

## BOQ Summary
BOQ Summary Details Tender Title: Establishment of MET park at Surat Airport. Sub Head.Supply and laying of LT Cable , OFC cable and associated electrical works. Tender ID: 2024_AAI_180989_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ascent Electrification Engineers | 2577218.00 | L1
| 2 | Mayur Electric Works | 2808600.00 | L2
| 3 | CENTRE TAP ENGINEERING | 3083200.00 | L3
| 4 | jaydeep agency corporation | 3180560.00 | L4