## BoQ1
Government eProcurement System Created By: ANANTHASUBRAMANIAN P R Created Date/Time: 27-Mar-2024 12:09 PM Tender Title: Provision of perimeter lighting and Associated Electrical Works for FTO Site Tender ID: 2024_AAI_182415_1
Tender Inviting Authority: The Senior Manager (E-E), AAI, Kadapa Airport.
Name of Work: Provision of Perimeter Lighting and Associated Electrical Works for FTO Site at Kadapa Airport.
Contract No: 2024_AAI_182415_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s LEESHA ELECTRICALS (GSTN-27ABAPW8550C1ZK) BID ID -669975 |  | SHIVARAMINFRA(GSTN-NA)--672607
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Erection of GI Octogoal Street light pole along with Foundation Erection of hot dip Galvanized Octogonal street light poles of 130 mm bottom dia / 70 mm top dia , 3 mm thick, with base plate of size 200 mm X 200 mm X 12 mm thickness of below length poles , by using J-bolts & template, in reinforced foundation of 0.4 x 0.4 x 1.2 mts (L x W x H) dimensions using Concrete of M25 grade & Steel reinforcement bars of (i) 6mm dia X 7 nos X 1.6 mts & (ii) 10mm dia X 8 nos X 1.3 mts, including straightening, cutting, bending, placing in position and binding on a bed of 0.6 x 0.6 x 0.1 mts(L x W x H) of 1:3:6 grade PCC , all complete upto plinth level for foundation, cost of shuttering & removal of form works for foundation ,excavation and refilling etc,. comlete as required. (i) Above 4.0 metre and upto 6.5 metre | 36.00 | Job |  | 4000.00 | 144000.00 | 8750.00 | 315000.00 | 144000.00 | M/s LEESHA ELECTRICALS
2.00 | Embedding DWC in Foundation Supplying and embedding 63 mm dia (OD 63 mm & ID 51 mm nominal) DWC HDPE pipe ISI marked conforming to IS 14930, Part Il complete in foundation (during casting) for cable entry including bending the pipe to the required shape complete as required. | 36.00 | Job |  | 200.00 | 7200.00 | 200.00 | 7200.00 | 7200.00 | M/s LEESHA ELECTRICALS, SHIVARAMINFRA
3.00 | Supply and Laying DWC direct in Ground Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part Il complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD- 63 mm & ID 51 mm nominal) | 2600.00 | Metre |  | 200.00 | 520000.00 | 140.00 | 364000.00 | 364000.00 | SHIVARAMINFRA
4.00 | Supply of 4C x 16 sq.mm Cable Supply of XLPE/PVC insualated PVC sheathed, armoured alluminium conductor power cable of 1.1kV grade of 4C X 16 sq.mm cable size etc., as per IS 7098 Part - 1 1988 with uptodate ammendments etc complete as required. | 1200.00 | Metres |  | 170.00 | 204000.00 | 160.00 | 192000.00 | 192000.00 | SHIVARAMINFRA
5.00 | Supply of 3C x 16 sq.mm Cable Supply of XLPE/PVC insualated PVC sheathed, armoured aluminium conductor power cable of 1.1kV grade of 3C X 16 sq.mm cable size etc., as per IS 7098 Part - 1 1988 with uptodate ammendments etc complete as required. | 1500.00 | Metres |  | 140.00 | 210000.00 | 150.00 | 225000.00 | 210000.00 | M/s LEESHA ELECTRICALS
6.00 | Laying of 3C x 16 sq.mm & 4C x 16 sq.mm cable in pipe Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/DWC - HDPE/ METAL pipe as required. (a) Upto 35 sq.mm | 2700.00 | Metres |  | 30.00 | 81000.00 | 40.00 | 108000.00 | 81000.00 | M/s LEESHA ELECTRICALS
7.00 | Termination of loop cables by Supply , fixing of 4 pole heavy duty connector, 6A SP -MCB complete as required Termination of loopi-in & loop-out cables by supply, fixing 01 no. 4 pole heavy duty connector, 01 no. Single Pole 6A rating 240V, min 6kA, "B" Curve MCB suitable for LED lighting loads, in existing Octogonal Street light pole suitable for 4C X 16 sq.mm PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade complete with connections using suitable lugs & terminal / thimbles for SP- MCB I/C, testing and commissioning to the satisfaction of E.I.C etc complete as required. | 36.00 | Job |  | 400.00 | 14400.00 | 300.00 | 10800.00 | 10800.00 | SHIVARAMINFRA
8.00 | Supply & End termination of 4C X 16 sq.mm cable Supplying and making end terminations with brass gland and aluminium lugs for following size (4C X 16 sq.mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 2.00 | Each |  | 250.00 | 500.00 | 350.00 | 700.00 | 500.00 | M/s LEESHA ELECTRICALS
9.00 | Supply & End termination of 3C X 16 sq.mm cable Supplying and making end terminations with brass gland and aluminium lugs for following size (3C X 16 sq.mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 2.00 | Each |  | 250.00 | 500.00 | 320.00 | 640.00 | 500.00 | M/s LEESHA ELECTRICALS
10.00 | Supply of J bolts and other hardwares like Nuts, washers etc as required for erection of poles Supply of 4 nos. of M16 X 450mm J- type, EN 8 Grade foundation bolts suitable for existing Surya Make 4 mtr high hot dip galvanised Octogonal poles with 130 mm bottom dia & 70 mm top dia, 3mm thick sheet etc complete as required., | 20.00 | Nos |  | 950.00 | 19000.00 | 4500.00 | 90000.00 | 19000.00 | M/s LEESHA ELECTRICALS
11.00 | Supply and Installation of LED Street lights and associated accessories Complete as required. Supply & installation of LED Street Light with , min system lumen output of min 110 lms per watt with overall lumens output of min 2200 lms, 5700-6500K colour temperature CCT , Life of atleast 50,000 hours at 70% lumen maintenance, surge protection of >4 KV, Fixture made of High Pressure die-cast aluminum,/ Standard alloy for outdoor application Engraved / Embossed mfg. Name / Logo or on Al-plate lables or screen printing on housing / body , IP66 Class-I protection, suitable for mounting on to arm / branch pipe (Supply of arm branch is in AAI Scope) of 50 mm dia. OD or on 50mm to 35mm dia OD Reducer kit provided by AAI, complete incl. minor hardware required for satisfactory installation & commisiioning as per specification to the satisfaction of E.I.C complete as per site requirement. | 40.00 | job |  | 2950.00 | 118000.00 | 7000.00 | 280000.00 | 118000.00 | M/s LEESHA ELECTRICALS
12.00 | Wiring for Street light LED fixture from MCB of LED Fitting incl. testing Commissioning etc Wiring for LED Street light with 3C x 1.5 sq.mm PVC insulated copper conductor cable in recessed steel i.e., Octogonal street light pole of 4.5 mtrs height and termination at 6A SP - MCB, 4 pole heavy duty Connector, LED fixture and earthing the point with one of the core of 3C x 1.5 sq.mm conductor cable etc for successful testing and commissioning of LED fitting to the satisfaction of E.I.C etc complete as required | 36.00 | job |  | 400.00 | 14400.00 | 500.00 | 18000.00 | 14400.00 | M/s LEESHA ELECTRICALS
13.00 | Supply and Fixing 6 way Double door MCB- DB for Security Huts Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB / RCCB / lsolator ) (DSR_Elec 2.3.1) (i) 6 Way, Double door | 3.00 | each |  | 1500.00 | 4500.00 | 5000.00 | 15000.00 | 4500.00 | M/s LEESHA ELECTRICALS
14.00 | Supply and Fixing SPN MCB in existing DB box Supplying and fixing 5A to 32A rating, 240/415 volts, 10 kA, "C"curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. (i) Single pole and neutral | 3.00 | each |  | 500.00 | 1500.00 | 4500.00 | 13500.00 | 1500.00 | M/s LEESHA ELECTRICALS
15.00 | Supply and Fixing SP MCB in existing DB box Supplying and fixing 5A to 32A rating, 240/415 volts, 10 kA, "C"curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. (i) Single pole | 10.00 | each |  | 150.00 | 1500.00 | 1500.00 | 15000.00 | 1500.00 | M/s LEESHA ELECTRICALS
16.00 | Wiring for Circuit / Submain Wiring Wiring for circuitl submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 20.00 | Meters |  | 350.00 | 7000.00 | 500.00 | 10000.00 | 7000.00 | M/s LEESHA ELECTRICALS
17.00 | Point wiring Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class FR-PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | 15.00 | Point |  | 1200.00 | 18000.00 | 700.00 | 10500.00 | 10500.00 | SHIVARAMINFRA
18.00 | Supplying and fixing 6/16 A modular Switch / Socket along with all accesories and wiring Supplying and fixing 6/16 A modular switch & 6/16 A socket on modular plate & switch box including wiring for power plug with 2x4 sq.mm FRLS PVC insulated Cu - Conductor single core in recess conduit alongwith 1 no 4 sq.mm FRLS PVC insulated Cu- condutor cable for earthing etc. as required. | 6.00 | Job |  | 550.00 | 3300.00 | 800.00 | 4800.00 | 3300.00 | M/s LEESHA ELECTRICALS
19.00 | SITC of LED type Aviation obstruction light Supply, Installation, testing and commissioning of min 10W LED Aviation Obstruction light incl. connection and all accessories complete as required for Security huts . | 3.00 | each |  | 4500.00 | 13500.00 | 4000.00 | 12000.00 | 12000.00 | SHIVARAMINFRA
20.00 | SITC of LED Batten bulb Supply, Installation, testing and commissioning of 240 V 50Hz operated LED batten with min lumen output of 2000 lumens, system efficacacy of min 100 lumens / watt, CCT 5700K - 6500K, CRI>=80,min IP 20 rating,THD <= 10%, PF >= 0.95, Sureg protection >=2KV, SDCM < 5, etc complete with 5 years warranty and complying to IS 10322 with upto date ammendments, to the satisfaction of EIC, etc complete as required | 5.00 | each |  | 650.00 | 3250.00 | 500.00 | 2500.00 | 2500.00 | SHIVARAMINFRA
21.00 | Supply of Pedestal fan for Security Huts Supply of 230 V 50Hz operated pedestal fan with min three step speed control and Oscillation control with min 400mm blade width, 1800 rpm, air flow of 90 cum / minute along with warranty card etc. | 5.00 | Each |  | 2500.00 | 12500.00 | 4000.00 | 20000.00 | 12500.00 | M/s LEESHA ELECTRICALS
22.00 | G.I Pipe Earthing Earthing with G.I earth pipe 4.5 metre long, 40mm dia, including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 8.00 | Each |  | 8000.00 | 64000.00 | 3000.00 | 24000.00 | 24000.00 | SHIVARAMINFRA
23.00 | G.I Wire along with Cable Providing and fixing 6 SWG dia G.I. wire in recess for loop earthing along with existing surface/ recessed pipe/ submain wiring/cable as required . | 1500.00 | Metre |  | 30.00 | 45000.00 | 10.00 | 15000.00 | 15000.00 | SHIVARAMINFRA
24.00 | Earth wire in GI Pipe Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. . | 16.00 | Metre |  | 250.00 | 4000.00 | 12.00 | 192.00 | 192.00 | SHIVARAMINFRA
| Total in Figures |  |  |  |  | 1511050.00 |  | 1753832.00
Lowest Amount Quoted BY: M/s LEESHA ELECTRICALS(1511050.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of perimeter lighting and Associated Electrical Works for FTO Site Tender ID: 2024_AAI_182415_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s LEESHA ELECTRICALS | 1511050.00 | L1
| 2 | SHIVARAMINFRA | 1753832.00 | L2