## BoQ1
Government eProcurement System Created By: Sateesh Kr Kanaujiya Created Date/Time: 19-Mar-2024 12:12 PM Tender Title: Providing of Automatic Gas Fire Suppressor for NAV-AIDS Building at Aurangabad Airport. Tender ID: 2024_AAI_187743_1
Tender Inviting Authority: Senior Manager (Engg.-Electrical), Airports Authority of India, Aurangabad Airport, Aurangabad- 431007.
Name of Work: Providing of Automatic Gas Fire Suppressor for NAV-AIDS Building at Aurangabad Airport.
Contract No: 2024_AAI_187743_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PYROGUARD ENGINEERS PRIVATE LIMITED(GSTN-07AACCP9466E1Z7) |  | Nexus Fire And Security Systems(GSTN-07AAKFN7125K1ZY) |  | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | advent electric technologies pvt. ltd.(GSTN-07AAJCA2055K1ZN) |  | Vasu Infosec Pvt Ltd(GSTN-27AABCV6080D1ZE)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | Design, manufacuring, supply, installation, testing and commissioning of Automatic Gas Suppression System consisting of Cylinder PESO Approved, complete with UL / VDS / PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure, a pressure guage with a safety burst disc, electronic control head / Solenoid, pressure operated control head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos. of Nozzles (UL / VDS listed), Piping, Manifold, Gas Release Panel, Fire Alarm System, Aspiration Detector etc. complete as required. (Gas Quantity would be as per the volume given below and as per the UL / VDS certification.) CLEAN AGENT (FK-5-1-12) / Inert Gas with Zero Ozone Depletion Potential (ODP), has appearance / Colourless gas and odour less. Note: The Cylinder, Volume of Gas, Nos. of Nozzles, piping design and pressure calculations using manufacturer design software for a given dimension of room duly approved by manufacturer (OEM) shall be submitted prior to starting of the works. Gas suppression System for following rooms and given approximate volume. Glide path - 75.60 Cum (L = 7.0 m, B = 3.6, H = 3.0 m) | 1.00 | Job |  | 604140.00 | 604140.00 | 569624.00 | 569624.00 | 641025.00 | 641025.00 | 400000.00 | 400000.00 | 599937.00 | 599937.00 | 400000.00 | advent electric technologies pvt. ltd.
1.02 | Localizer - 72.45 Cum (L = 6.9 m, B = 3.5, H = 3.0 m) | 1.00 | Job |  | 599924.00 | 599924.00 | 564491.00 | 564491.00 | 630135.00 | 630135.00 | 400000.00 | 400000.00 | 590862.00 | 590862.00 | 400000.00 | advent electric technologies pvt. ltd.
1.03 | MSSR Equipment Room - 202.80 Cum (L = 6.5 m, B = 7.8, H = 4.0 m) | 1.00 | Job |  | 797030.00 | 797030.00 | 878869.00 | 878869.00 | 792000.00 | 792000.00 | 750000.00 | 750000.00 | 938300.00 | 938300.00 | 750000.00 | advent electric technologies pvt. ltd.
1.04 | MSSR UPS Room - 98.04 Cum (L = 4.3 m, B = 3.8, H = 6.0 m) | 1.00 | Job |  | 671795.00 | 671795.00 | 600016.00 | 600016.00 | 594000.00 | 594000.00 | 400000.00 | 400000.00 | 663184.00 | 663184.00 | 400000.00 | advent electric technologies pvt. ltd.
1.05 | MSSR Equipment Room 7th Floor - 67.5 Cum (L = 5.0 m, B = 4.5, H = 3.0 m) | 1.00 | Job |  | 592870.00 | 592870.00 | 545587.00 | 545587.00 | 608355.00 | 608355.00 | 400000.00 | 400000.00 | 578600.00 | 578600.00 | 400000.00 | advent electric technologies pvt. ltd.
1.06 | New DVOR Equipment Room - 53.11 Cum (L = 4.95 m, B = 3.7 m, H = 2.9 m) | 1.00 | Job |  | 568645.00 | 568645.00 | 505160.00 | 505160.00 | 643500.00 | 643500.00 | 400000.00 | 400000.00 | 512927.00 | 512927.00 | 400000.00 | advent electric technologies pvt. ltd.
1.07 | New DVOR UPS Room - 23.93 Cum (L=2.5 m, B = 3.3 m, H = 2.9 m) | 1.00 | Job |  | 516330.00 | 516330.00 | 438496.00 | 438496.00 | 346500.00 | 346500.00 | 400000.00 | 400000.00 | 425946.00 | 425946.00 | 346500.00 | CENTRE TAP ENGINEERING
| Total in Figures |  |  |  |  | 4350734.00 |  | 4102243.00 |  | 4255515.00 |  | 3150000.00 |  | 4309756.00
Lowest Amount Quoted BY: advent electric technologies pvt. ltd.(3150000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing of Automatic Gas Fire Suppressor for NAV-AIDS Building at Aurangabad Airport. Tender ID: 2024_AAI_187743_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | advent electric technologies pvt. ltd. | 3150000.00 | L1
| 2 | Nexus Fire And Security Systems | 4102243.00 | L2
| 3 | CENTRE TAP ENGINEERING | 4255515.00 | L3
| 4 | Vasu Infosec Pvt Ltd | 4309756.00 | L4
| 5 | PYROGUARD ENGINEERS PRIVATE LIMITED | 4350734.00 | L5