## BoQ1
Government eProcurement System Created By: Lakhan Pal Singh Solanki Created Date/Time: 01-Apr-2024 11:24 AM Tender Title: Finalization of site for CCR Room, Sub Station as well as renovation construction of VIP Room, Pilot/Crew Room for VVIP/VIP Movement, NSG Control Room and Anti-Hijack Control Room at Safdarjung Airport (SH- Electrical works) Tender ID: 2024_AAI_188653_1
Tender Inviting Authority: Asstt.Gen.Mgr., Airports Authority of India, Safdarjung Airport, New Delhi-110003
Name of Work: Finalization of site for CCR Room, Sub Station as well as renovation construction of VIP Room, Pilot/Crew Room for VVIP/VIP Movement, NSG Control Room and Anti-Hijack Control Room at Safdarjung Airport. (SH: Electrical works)
Contract No: AAI/SAP/Engg.(E)/Location/Substation/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | K B CONTRACT (P) LTD (GSTN-07AADCK6091P1ZX) BID ID -688981 |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)--688452
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I : LT Panels
2.00 | SAP TERMINAL BUILDING (OLD AIRPORT TERMINAL BUILDING) ESSENTIAL PANEL
3.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel indoor type , IP54 protection , 35 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 35 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor , cable alleys, cable gland plates in two half, i/c providing following switch gears :- Also, refer to General Notes and Specifications for Panels/ Feeder Pillers/Boards. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. SMC shrouds busbar supports shall be used. Padlocking facility shall be provided on all MCCB feeder doors and switch handles shall be lockable in OFF position. Sealing Arrangement:- PE Foam Rubber Gasket Bus Bars Supports - Non-Hygroscopic, Non Carbonising, Corrosion Resistant, SMC Supports 1Set of connector (Phase+Neutral) shall be provided in cable alley for all outgoing with interconnection wires between MCB and Connector. Minimum Air Clearances between bus bars; P-P=32mm, P-N=32mm,P-E=26mm and N-E=26mm Panel Power and control Wiring shall be with FRLS PVC insulated cable AC voltage circuit-1.5 sqmm Red,Yellow,Blue &Black Current circuit-2.5 sqmm Red,Yellow,Blue &Black AC Control circuit-1.5 sqmm White for Phase & Black for Neutral DC Control circuit-2.5 sqmm Grey, Power circuit- Red,Yellow,Blue for Phase &Black for Neutral, Labelling- Computerised Laminated Aluminium Name Plate with White letters on Blue/Black Background For Each Feeder and Panel Itself. All indicating lamps shall be LED type with 2 amp protection MCB All ammeter/ volt meter/MFM shall be digital type of size 96 mm x 96 mm Note: If mentioned fault rating is unavailable consider nearby upside rating. All outgoing MCCB shall be with adjustable O/L protection. All outgoing MCCB shall have 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. All incomers and Buscoupler breakers shall be electrical and mechanical interlocked with suitable accessories. 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. Suitable size insulation mat conforming to IS: 15652: 2006 shall be provided in front of the panels. | 1.00 | Job | 100.00 | 2250000.00 | 2250000.00 | 4414708.00 | 4414708.00 | 2250000.00 | K B CONTRACT (P) LTD
3.10 | A) INCOMER - i) 2 Nos 1000A, 4 Pole,EDO,Microprocessor ACB as Incomer from LT Cum Synch Essential Panel., ii) 02 nos. Energy Meter (CT type) of suitable rating. Each ACB above shall be provided with i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection, ii)1-Set of LED Phase Indicating Lights R,Y,B with 2A HRC fuses for protection. iii)1-Set of ON/OFF/Trip Indicating Lights with 2A HRC Fuses for Protection iv)1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-600A) with CTs & SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection. v)16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port
3.20 | B) Bus Bars 4 Nos 1000A Electrolytic Aluminium Bus-Bars of equal cross-section.
3.30 | C) BUS COUPLER i)1 Nos 1000A, 4 Pole,EDO, ACB as Bus Coupler with LSIG Trip. ii)1-Set of LED Phase Indicating Lights R,Y,B with 2A HRC fuses for protection.
3.40 | D) ACCESSORIES FOR ELECTRICAL INTERLOCKING. i) Electrical interlocking arrangement as per drawing and specifications among 2 nos. Incomers from LT Cum Synch Panel and 1 nos. Bus coupler including interconnections etc. as required.
3.50 | E) OUTGOINGS (I) 4 Nos. MCCB, 250A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each MCCB above shall be provided with; i) (0 - 250A) Ammeter (96x96mm) with CT's and S/S. ii) OFF/ON/Trip indicating LED lights with 2A HRC fuses. (II) 11 Nos. MCCB, 160A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each MCCB above shall be provided with; i) (0 - 160A) Ammeter (96x96mm) with CT's and S/S. ii) OFF/ON/Trip indicating LED lights with 2A HRC fuses. (III) 3 Nos. MCCB, 125A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each MCCB above shall be provided with; i) (0 - 125A) Ammeter (96x96mm) with CT's and S/S. ii) OFF/ON/Trip indicating LED lights with 2A HRC fuses. (IV) 8 Nos. MCCB, 100A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each MCCB above shall be provided with; i) Suitable rating Ammeter (96x96mm) with CT's and S/S. ii) OFF/ON/Trip indicating LED lights with 2A HRC fuses. (V) Space 2 Nos. 160A, 36 kA, Four Pole, with microprocessor based release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu).
4.00 | (EXTENSION OF EXISTING ESSENTIAL MAIN LT PANEL) Design, manufacture supply, installation, testing and commissioning of main LT Panel, cubicle & modular type, made of 2 mm thick sheet steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 42, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 nos. earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alley, cable gland plates in two half, the panel should be similar to the existing panle in order of colour, depth and height, interconnection with existing panel in respect of busbar, interlocking etc. including supply & installation of following items and as per technical specification: | 2.00 | Job | 100.00 | 630000.00 | 1260000.00 | 825000.00 | 1650000.00 | 1260000.00 | K B CONTRACT (P) LTD
4.10 | A) INCOMER : i) 1 Nos 1000A, 4 Pole, EDO, Microprocessor ACB as Incomer from LT Cum Synch Essential Panel. ii) 1 Nos 800A, 4 Pole, EDO, Microprocessor ACB as Incomer from LT Cum Synch Essential Panel. Each MCCB feeder above shall be provided with; i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection ii) 1-Set of LED Phase Indicating Lights R,Y,B with 2A HRC fuses for protection. iii) 1-Set of ON/OFF/Trip Indicating Lights with 2A HRC Fuses for Protection iv) 1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-600A) with CTs & SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection. v) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port
4.20 | B) Bus Bars 4 Nos 4000A Electrolytic Aluminium Bus-Bars of equal cross-section.
5.00 | Supplying, installation, testing and commissioning of 250 Amp Capacity distribution Panel indoor type with double door with following accessories complete as required. (Make:- Havells) i) 4 way double door G Frame panel board (Make: Havells Model No. IHVGF2500400 or equivallent) -1 No ii) Incomer 100 Amps. FP MCCB 25 KA with all spreader links and connections-1 No iii) Outgoings 63 Amps FP MCCB 25 KA with spreader links - 4 Nos iv) Cable alley 4 way double door 250 Amps (Suitable for above Panel board Make: Havells Model No. ISSBOU0698 or equivallent)-1 No. v) Digital meter module ( Ampere meter,Voltmeter with selector switch and LED indication lights-1 Set | 1.00 | Nos | 10.00 | 90000.00 | 90000.00 | 75000.00 | 75000.00 | 75000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supply, Installation, testing and Commissioning of Hybrid DRPC Panel (250 KVAr DRPC+ 150 Amps AHF) Design, supply, installation, testing & commissioning of cubicle type semi compartementalized floor mounted free standing type with configration of Dynamic Reactive Modules and Active harmonic filter (250Kvar+150Amp) ,415V, 50HZ, 3 phase 4 wire supply, moisture, dust and vermin proof IP-42 with cooling intrinsic design of voltage sourced IGBT based technology with multi modular design for parallel operation ,intelligent 3-Level topology with 12 IGBT Hybrid PFC panel with Programmable Microprocessor controller to maintain Power Factor, Harmonics & Unbalancing duly housed in epoxy powder coated 2mm thick CRCA sheet steel compatmentalised enclosure free standing type with all supports, accessories, switch gears, control gears, protections, wiring, interconnections, control MCBs and maintain PF,I-THD,V-THD as per IEEE 519-2014 etc. as required. Also Certification Standard IEC50178:1997 ,IEC 61000_6_2 CISPR11 Group 1,Class A , IGBT based modules series performance comply EN 50091-3/IEC 62040-3/AS ,62040 -3 VFISS111 , EN 61000-6-4 and CE certified , Environmental characteristics Operating :3C2 and 3S2 conforming to IEC 60721-3-3 complete in all respects & having its main components as bellow along with all other standard components, circuitry & specifications as required (Make : Selec/ Nexpo/ Vasu Power) | 1.00 | Nos | 10.00 | 2070000.00 | 2070000.00 | 1500000.00 | 1500000.00 | 1500000.00 | JCC ENGINEERS PRIVATE LIMITED
6.10 | A) INCOMMER i) 1 No. of 630 Amps. 415 Volts 4P. Type ACB. of 36KA with overload, S/C, O/C and earth fault protection. ii) 1 No. of Display meter with compatible RS 485 ports. iii) 3 No.of Phase Indicating & ON-OFF LED Lights 230 V. iv) 1 Set. of Ammeter - digital 3 Phase. v) 3 No. of MCB 6A-SP-10kA-C-Curve.
6.20 | B) BUS BARS 1000-Amps (neutral equal size) 3 phase 4 wire 415 volts 50 HZ aluminium bus bars with colour coded PVC heat shrinkable sleeves.
6.30 | C) OUTGOING Modular Active Filter (i) AHF 150Amp - 1 Nos. (IGBT based active technology with gate driver,interfacing,voltage sencing & control cards, heat inks,cooling fan,current tranducers,SMPS,SSR etc.) each have following: 1 No of 100 Amp AHF module and 1 no of 50 Amps (3 -Level Topology ,12 IGBT Circuit) 1 No. of Programmable HMI With 7inches LED Display Space future provision for 50 Amps module in the Panel. Configuration -3phase 4 wire Negative Sequence load current cancellation - It should work 1phase and 2 phase as well and Harmonics mitigation upto 51th Level. (ii) Dynamic Reactive Modules 250 Kvar-1Nos. The Dynamic Reactive Modules (DRPC), 250 Kvar with 100/50 Amps modular IGBT based design should be a power electronic device to be connected in parallel with the loads that require inductive and/or capacitive reactive powers, for their operation. The DRPC should be working as a controlled current source providing the inductive or capacitive currents in real-time. The DRPC should take the CT and PT feedbacks from the input line (could be of low voltage or medium voltage or high voltage or from back-up generators), and work to maintain the phase angle difference between the voltage and current, as per desired power factor programmed by the user, time-to-time. The DRPC is envisaged to have very fast reaction (less than few 100 micro seconds) and response times (less than 20 milli seconds) with stable and accurate power factor correction, overcoming the drawbacks of any pre-existing conventional solutions like fixed and/or switched capacitor/reactor banks. The DRPC should perform inductive/capacitive reactive power correction. The DRPC should mitigate the Harmonics level upto 15th order, The DRPC should maintain power factor >0.995. The DRPC should ioT enable The DRPC should have the capability to simulate cable capacitances and/or transformer/OH line inductances upstream to the CT and PT feedback, and deliver the corresponding extra reactive power, to achieve near-unity power factor at the point of actual billing by the electricity boards. The offered DRPC should be a complete system, designed in modular configuration (individual module size should less than 150kVAR) strictly as per attached specifications, in all respects. The individual DRPC modules should use 3-Level IGBT inverter configuration, housed in casing, with dedicated cooling, and all necessary protections.
6.40 | A 250 kVAR Dynamic Reactive Modules, in modular configuration (individual module size must be lower than 150kVAR), strictly as per attached specifications, as a complete system in all respect. The Static VAR Generator modules should consist of 3-Level IGBT inverter, housed in casing, with dedicated cooling, and necessary protections. The Static VAR Generator should perform inductive/capacitive reactive power correction, and capable to receive feedback from LT as well HT sides. Power losses shall be less than 1.5% or less than 1.5KW per 100KVAR module, This shall be designed for 50°C without derating. This shall have HMI displaying 3 phase active power, 3 phase apparent power, 3 phase displacement power factor, 3 line RMS voltage , 3 line current , 3 phase DRPC current, current shall be shown with different colors (Red, yellow, blue, black color) Each module shall have separate protection MCCB. For easy repairability the IGBT driver cards shall be separate for different phases, separate common control cards and these should be fitted on main PCB. DC capacitors shall not be mounted on PCB. DRPC shall used powder iron core instead of CRGO and LCL circuit to reduce noises created by switching frequency.. The DRPC shall also be suitable for unbalanced load usage. Supply, Installation, testing and Commissioning of 250 KVAR DRPC+ 150 Amp AHF Hybrid IGBT based APFC panel complete as required. The solution comply IEEE -519-2014 for Harmonics mitigation , Also comply IEC50178:1997 ,IEC 61000_6_2 CISPR11 Group 1,Class A , IGBT based modules series performance comply EN 50091-3/IEC 62040-3/AS ,62040 -3 VFISS111 , EN 61000-6-4 and CE certified , Environmental characteristics Operating :3C2 and 3S2 conforming to IEC 60721-3-3with details as described above and as per specifications. The Hybrid PQ Solution described as above complete in all respect as per specification enclosed, up to the entire satisfaction of engineer In Charge.To ensure safety, reliability and accountability of component co ordination, The DRPC and AHF modules of same OEM.
7.00 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable upto 3.3 KV, fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | 10.00 | Mtr | 10.00 | 3600.00 | 36000.00 | 1500.00 | 15000.00 | 15000.00 | JCC ENGINEERS PRIVATE LIMITED
8.00 | SH-II : Supply Cables & Trays
9.00 | Supply of following size of 1.1 kv grade multicore aluminium conductor, XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
9.01 | 4 core, 10 Sq.mm. | 500.00 | Mtr | 10.00 | 99.00 | 49500.00 | 130.00 | 65000.00 | 49500.00 | K B CONTRACT (P) LTD
9.02 | 3½ core X 35 Sq.mm. | 500.00 | Mtr | 10.00 | 180.00 | 90000.00 | 230.00 | 115000.00 | 90000.00 | K B CONTRACT (P) LTD
9.03 | 3½ core X 50 Sq.mm. | 500.00 | Mtr | 10.00 | 225.00 | 112500.00 | 250.00 | 125000.00 | 112500.00 | K B CONTRACT (P) LTD
9.04 | 3½ core X 95 Sq.mm. | 500.00 | Mtr | 10.00 | 405.00 | 202500.00 | 475.00 | 237500.00 | 202500.00 | K B CONTRACT (P) LTD
9.05 | 3½ core X 120 Sq.mm. | 500.00 | Mtr | 10.00 | 504.00 | 252000.00 | 600.00 | 300000.00 | 252000.00 | K B CONTRACT (P) LTD
9.06 | 3½ core X 400 Sq.mm. | 2700.00 | Mtr | 10.00 | 1440.00 | 3888000.00 | 1600.00 | 4320000.00 | 3888000.00 | K B CONTRACT (P) LTD
10.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
10.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 10.00 | Mtr | 10.00 | 1008.00 | 10080.00 | 700.00 | 7000.00 | 7000.00 | JCC ENGINEERS PRIVATE LIMITED
10.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 50.00 | Mtr | 10.00 | 1440.00 | 72000.00 | 1000.00 | 50000.00 | 50000.00 | JCC ENGINEERS PRIVATE LIMITED
10.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 200.00 | Mtr | 10.00 | 2520.00 | 504000.00 | 2000.00 | 400000.00 | 400000.00 | JCC ENGINEERS PRIVATE LIMITED
11.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
11.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each | 10.00 | 1170.00 | 1170.00 | 1387.00 | 1387.00 | 1170.00 | K B CONTRACT (P) LTD
11.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 2.00 | Each | 10.00 | 1890.00 | 3780.00 | 2387.00 | 4774.00 | 3780.00 | K B CONTRACT (P) LTD
11.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 20.00 | Each | 10.00 | 3600.00 | 72000.00 | 4450.00 | 89000.00 | 72000.00 | K B CONTRACT (P) LTD
12.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required
12.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each | 10.00 | 1557.00 | 1557.00 | 1665.00 | 1665.00 | 1557.00 | K B CONTRACT (P) LTD
12.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 1.00 | Each | 10.00 | 2520.00 | 2520.00 | 2865.00 | 2865.00 | 2520.00 | K B CONTRACT (P) LTD
12.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 10.00 | Each | 10.00 | 4770.00 | 47700.00 | 5340.00 | 53400.00 | 47700.00 | K B CONTRACT (P) LTD
13.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Cross member"(galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required
13.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each | 10.00 | 1980.00 | 1980.00 | 1942.00 | 1942.00 | 1942.00 | JCC ENGINEERS PRIVATE LIMITED
13.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 1.00 | Each | 10.00 | 3150.00 | 3150.00 | 3342.00 | 3342.00 | 3150.00 | K B CONTRACT (P) LTD
13.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 10.00 | Each | 10.00 | 5940.00 | 59400.00 | 6230.00 | 62300.00 | 59400.00 | K B CONTRACT (P) LTD
14.00 | Galvanised Iron cable tray "Reducer" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
14.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each | 10.00 | 2034.00 | 2034.00 | 1555.00 | 1555.00 | 1555.00 | JCC ENGINEERS PRIVATE LIMITED
14.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 1.00 | Each | 10.00 | 3600.00 | 3600.00 | 2675.00 | 2675.00 | 2675.00 | JCC ENGINEERS PRIVATE LIMITED
14.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 4.00 | Each | 10.00 | 3150.00 | 12600.00 | 4948.00 | 19792.00 | 12600.00 | K B CONTRACT (P) LTD
15.00 | SH-III : Cable Laying
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
16.01 | Upto 35 sq. mm | 25.00 | Mtr | 10.00 | 180.00 | 4500.00 | 200.00 | 5000.00 | 4500.00 | K B CONTRACT (P) LTD
16.02 | Above 35 sq. mm and upto 95 sq. mm | 25.00 | Mtr | 10.00 | 270.00 | 6750.00 | 200.00 | 5000.00 | 5000.00 | JCC ENGINEERS PRIVATE LIMITED
16.03 | Above 95 sq. mm and upto 185 sq. mm | 100.00 | Mtr | 10.00 | 360.00 | 36000.00 | 200.00 | 20000.00 | 20000.00 | JCC ENGINEERS PRIVATE LIMITED
16.04 | Above 185 sq. mm and upto 400 sq. mm | 100.00 | Mtr | 10.00 | 540.00 | 54000.00 | 200.00 | 20000.00 | 20000.00 | JCC ENGINEERS PRIVATE LIMITED
17.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/PVC pipe as required
17.01 | Upto 35 sq. mm | 50.00 | Mtr | 10.00 | 54.00 | 2700.00 | 10.00 | 500.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
17.02 | Above 35 sq. mm and upto 95 sq. mm | 50.00 | Mtr | 10.00 | 108.00 | 5400.00 | 10.00 | 500.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
17.03 | Above 95 sq. mm and upto 185 sq. mm | 150.00 | Mtr | 10.00 | 180.00 | 27000.00 | 10.00 | 1500.00 | 1500.00 | JCC ENGINEERS PRIVATE LIMITED
17.04 | Above 185 sq. mm and upto 400 sq. mm | 1350.00 | Mtr | 10.00 | 270.00 | 364500.00 | 10.00 | 13500.00 | 13500.00 | JCC ENGINEERS PRIVATE LIMITED
18.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
18.01 | Upto 35 sq. mm | 50.00 | Mtr | 10.00 | 54.00 | 2700.00 | 10.00 | 500.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
18.02 | Above 35 sq. mm and upto 95 sq. mm | 25.00 | Mtr | 10.00 | 108.00 | 2700.00 | 10.00 | 250.00 | 250.00 | JCC ENGINEERS PRIVATE LIMITED
18.03 | Above 95 sq. mm and upto 185 sq. mm | 25.00 | Mtr | 10.00 | 135.00 | 3375.00 | 10.00 | 250.00 | 250.00 | JCC ENGINEERS PRIVATE LIMITED
18.04 | Above 185 sq. mm and upto 400 sq. mm | 100.00 | Mtr | 10.00 | 180.00 | 18000.00 | 10.00 | 1000.00 | 1000.00 | JCC ENGINEERS PRIVATE LIMITED
19.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
19.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 400.00 | Mtr | 10.00 | 90.00 | 36000.00 | 10.00 | 4000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
19.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 400.00 | Mtr | 10.00 | 135.00 | 54000.00 | 10.00 | 4000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
19.03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 150.00 | Mtr | 10.00 | 180.00 | 27000.00 | 10.00 | 1500.00 | 1500.00 | JCC ENGINEERS PRIVATE LIMITED
19.04 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 500.00 | Mtr | 10.00 | 225.00 | 112500.00 | 10.00 | 5000.00 | 5000.00 | JCC ENGINEERS PRIVATE LIMITED
20.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
20.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 300.00 | Mtr | 10.00 | 90.00 | 27000.00 | 10.00 | 3000.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED
20.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 300.00 | Mtr | 10.00 | 135.00 | 40500.00 | 10.00 | 3000.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED
20.03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 50.00 | Mtr | 10.00 | 180.00 | 9000.00 | 10.00 | 500.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
20.04 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 800.00 | Mtr | 10.00 | 225.00 | 180000.00 | 10.00 | 8000.00 | 8000.00 | JCC ENGINEERS PRIVATE LIMITED
21.00 | Supplying and fixing cable route marker with 10cmx10cmx 5 mm thick GI Plate with inscription thereon , bolted/ welded to 35x35x6 mm angle iron of 60 cm long and fixing the same in ground as required. | 4.00 | Each | 10.00 | 900.00 | 3600.00 | 300.00 | 1200.00 | 1200.00 | JCC ENGINEERS PRIVATE LIMITED
22.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required.
22.01 | 4 core, 10/16/25 Sq. mm | 82.00 | Each | 10.00 | 108.00 | 8856.00 | 100.00 | 8200.00 | 8200.00 | JCC ENGINEERS PRIVATE LIMITED
22.02 | 3½ core, 25/ 35/ 50 Sq.mm. | 2.00 | Each | 10.00 | 180.00 | 360.00 | 250.00 | 500.00 | 360.00 | K B CONTRACT (P) LTD
22.03 | 3½ core x 70/ 95 Sq.mm | 2.00 | Each | 10.00 | 360.00 | 720.00 | 300.00 | 600.00 | 600.00 | JCC ENGINEERS PRIVATE LIMITED
22.04 | 3½ core X 120/ 150/ 185 Sq.mm. | 2.00 | Each | 10.00 | 540.00 | 1080.00 | 500.00 | 1000.00 | 1000.00 | JCC ENGINEERS PRIVATE LIMITED
22.05 | 3½ core X 240/ 300/ 400 Sq.mm. | 12.00 | Each | 10.00 | 810.00 | 9720.00 | 500.00 | 6000.00 | 6000.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
23.01 | 4 core, 10/16/25 Sq. mm | 2.00 | Each | 10.00 | 1350.00 | 2700.00 | 500.00 | 1000.00 | 1000.00 | JCC ENGINEERS PRIVATE LIMITED
23.02 | 3½ core, 25/ 35/ 50 Sq.mm. | 2.00 | Each | 10.00 | 1800.00 | 3600.00 | 1500.00 | 3000.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED
23.03 | 3½ core x 70/ 95 Sq.mm | 2.00 | Each | 10.00 | 2700.00 | 5400.00 | 2000.00 | 4000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
23.04 | 3½ core X 120/ 150/ 185 Sq.mm. | 2.00 | Each | 10.00 | 4500.00 | 9000.00 | 2500.00 | 5000.00 | 5000.00 | JCC ENGINEERS PRIVATE LIMITED
23.05 | 3½ core X 240/ 300/ 400 Sq.mm. | 2.00 | Each | 10.00 | 5400.00 | 10800.00 | 3000.00 | 6000.00 | 6000.00 | JCC ENGINEERS PRIVATE LIMITED
24.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
24.01 | 3½ core X 400 Sq.mm. | 8.00 | Each | 10.00 | 5400.00 | 43200.00 | 5000.00 | 40000.00 | 40000.00 | JCC ENGINEERS PRIVATE LIMITED
25.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc. as required
25.01 | 100 mm dia | 20.00 | Mtr | 10.00 | 1080.00 | 21600.00 | 1200.00 | 24000.00 | 21600.00 | K B CONTRACT (P) LTD
26.00 | Supply & Laying of following sizes DWC HDPE pipe ISI marked conforming to IS 14930, Part-II along with all acessories like socket, bend, couplers etc complete with fitting and cutting, jointing etc direct in ground (75 cm below ground level) including excavation & refilling the trench with same excavated earth but excluding sand cushioning and protective covering etc. , complete as required.
26.01 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 100.00 | Mtr | 10.00 | 108.00 | 10800.00 | 150.00 | 15000.00 | 10800.00 | K B CONTRACT (P) LTD
27.00 | Supply & Laying of 160 mm (OD) / 135 mm (ID) (nominal) dia (PE-80, PN-6) HDPE pipe as per IS 4984 through trenchless technology by drilling the bore of suitable dia directly in ground upto the depth of 3 meters from the ground level including necessary joining, coupling, splicing etc complete as required. | 1250.00 | Mtr | 10.00 | 1206.00 | 1507500.00 | 2350.00 | 2937500.00 | 1507500.00 | K B CONTRACT (P) LTD
28.00 | SH-IV : Earthing & Surge Protection System
29.00 | SITC of 3 Phase / Type1+2 (KEMA Certified) Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (LN) Single-pole combined lightning current and surge arrester, Type 1 SPDThe device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350μs) of 25kA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV,. The device shall haveinbuilt fuse for L-N. Follow current extinguishing capability [L-N]/[N-PE] : 100kArms / 100Arms. The device shall have built in fuse and operation of SPD shall be independent of Line current for L N SPD. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643-1s and these should be fitted on main PCB. DC capacitors shall not be mounted on PCB. DRPC shall used powder iron core instead of CRG (Make : Dehn/ Pheonix/ or as per preffered list of make). | 2.00 | Set | 10.00 | 189900.00 | 379800.00 | 50000.00 | 100000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
30.00 | Supply, Installation, Testing and Commissioning of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 254 microns of copper plating, UL listed with company name marked on rod. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min, Approvals- Tested acc. IEC / EN 62561-2, UL 467, 20 kg backfilled compound, - Material Carbon based backfill/earthing compound, Fulgurite formation test at direct lightning (10/350 μs), lightning long duration test at- 100C No fulgurites/Pass, Environmentally Friendly ROHS certified, Resistivity- < 0.12 ΩM, Complying Standard- IEC 62561-7 , Testing Approvals Certified from- NABL accredited Laboratories, StSt 316 grade clamp to terminate the load on earth electrode, Poly plastic pit cover of material- Polymer Body & Cover, Product Code- HEP. | 4.00 | Nos | 10.00 | 40500.00 | 162000.00 | 12000.00 | 48000.00 | 48000.00 | JCC ENGINEERS PRIVATE LIMITED
31.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 10.00 | 13500.00 | 27000.00 | 17000.00 | 34000.00 | 27000.00 | K B CONTRACT (P) LTD
32.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr | 10.00 | 1080.00 | 32400.00 | 1250.00 | 37500.00 | 32400.00 | K B CONTRACT (P) LTD
33.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 100.00 | Mtr | 10.00 | 1080.00 | 108000.00 | 1000.00 | 100000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
34.00 | SH-V : Fire Extinguisher & Suppression System
35.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 30 gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. (Make : STAT-X, Pyrogen, Epotosor as approved by EIC). | 35.00 | Nos | 10.00 | 27000.00 | 945000.00 | 12000.00 | 420000.00 | 420000.00 | JCC ENGINEERS PRIVATE LIMITED
36.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 60 gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. (Make : STAT-X, Pyrogen, Epotos or as approved by EIC). | 10.00 | Nos | 10.00 | 30600.00 | 306000.00 | 20000.00 | 200000.00 | 200000.00 | JCC ENGINEERS PRIVATE LIMITED
37.00 | SITC of Self Operated Aerosol based fire Extinguisher for the protection of up to 0.2 cubic mtrs of space in DBs & Electrical Panels using 8 gms. Of Aerosol Standard NFPA 2010. design density of the aerosol should be less than for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 10 years . (Makes: STAT-X, Pyrogen, Epotos or as approved by EIC) | 30.00 | Nos | 10.00 | 15300.00 | 459000.00 | 6250.00 | 187500.00 | 187500.00 | JCC ENGINEERS PRIVATE LIMITED
38.00 | SH-VI : Miscellaneous items
39.00 | Supply, Installation, Testing and Commissioning of smart energy management Cloud with gateway base complete, Data Base, Reporting tool, License Key and capable of integrating 50 number of devices including developing of the graphical screen, reporting formats etc. The Cloud with gateway base shall be compatible with windows based operating system and shall have the following minimum features complete as required: 1. Continuous Monitoring. 2. View instantaneous parameters like voltage, current, power factor, temperature, humidity and all type of harmonics, parameters, e.g. power, kWh, KVAHr current, voltage (L-N, L-L, & N-E) frequency, temperature etc. 3. Historical Trend patterns for any logged parameters such as electrical energy usage, power demand and any other logged parameter. Leverage these values In Excel to create detailed reports data storage 1 yrs. 4. Energies by day, energies by hour – analyses measured kilowatthours for cost allocation or comparison purpose. 5. Generation and transmission of alerts / notifications through emails and SMS. Approved by CE/NABL (Make : Dehn/ Selec/ Nexpo/ Vasu Power/ Siemens/ Schneider or as approved by EIC) | 1.00 | Nos | 10.00 | 396000.00 | 396000.00 | 250000.00 | 250000.00 | 250000.00 | JCC ENGINEERS PRIVATE LIMITED
40.00 | Dismentleing of existing all type LT panels and Power cables (as directed by EIC). | 1.00 | Job | 10.00 | 1800.00 | 1800.00 | 25000.00 | 25000.00 | 1800.00 | K B CONTRACT (P) LTD
41.00 | SITC of 63/ 100 Amp 4 pole MCCB having thermal magnetic release in the exisiting panel or enclouser, including making an arrangement for mounting of MCCB etc. as required at site. | 6.00 | Each | 10.00 | 36000.00 | 216000.00 | 20000.00 | 120000.00 | 120000.00 | JCC ENGINEERS PRIVATE LIMITED
42.00 | SITC of Sheet Steel Enclosure large size (reputated make) suitable for mounting of 63/ 100 Amp 4 pole MCCB (without MCCB), the installation of enclouser shall be recessed or as directed by EIC. etc. as required at site. | 6.00 | Each | 10.00 | 5400.00 | 32400.00 | 5000.00 | 30000.00 | 30000.00 | JCC ENGINEERS PRIVATE LIMITED
43.00 | SITC of 200 Amp 4 pole Bus bar Chamber recessed type, the Busbar made of ETP Grade Copper, etc. as required at site. | 6.00 | Each | 10.00 | 6300.00 | 37800.00 | 10000.00 | 60000.00 | 37800.00 | K B CONTRACT (P) LTD
44.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 1.50 | Cum | 10.00 | 7200.00 | 10800.00 | 7000.00 | 10500.00 | 10500.00 | JCC ENGINEERS PRIVATE LIMITED
45.00 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels. | 5.00 | Sq m | 10.00 | 450.00 | 2250.00 | 350.00 | 1750.00 | 1750.00 | JCC ENGINEERS PRIVATE LIMITED
46.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in charge.
46.01 | (a) All Kind of Soil | 8.00 | Cum | 10.00 | 360.00 | 2880.00 | 300.00 | 2400.00 | 2400.00 | JCC ENGINEERS PRIVATE LIMITED
47.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :
47.01 | (a) 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | 2.00 | Cum | 10.00 | 4500.00 | 9000.00 | 4000.00 | 8000.00 | 8000.00 | JCC ENGINEERS PRIVATE LIMITED
48.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:
48.01 | (a) Cement mortar 1:6 (1 cement : 6 coarse sand) | 3.00 | Cum | 10.00 | 5400.00 | 16200.00 | 5000.00 | 15000.00 | 15000.00 | JCC ENGINEERS PRIVATE LIMITED
49.00 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required.
49.01 | (a) In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works | 1000.00 | Kg | 10.00 | 270.00 | 270000.00 | 100.00 | 100000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
50.00 | CEMENT PLASTER (IN COARSE SAND) 15 mm cement plaster on rough side of single or half brick wall of mix:
50.01 | (a) 1:6 (1 cement: 6 coarse sand) | 50.00 | Sq m | 10.00 | 5400.00 | 270000.00 | 300.00 | 15000.00 | 15000.00 | JCC ENGINEERS PRIVATE LIMITED
51.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :
51.01 | (a) Two or more coats on new work | 50.00 | Sq m | 10.00 | 360.00 | 18000.00 | 200.00 | 10000.00 | 10000.00 | JCC ENGINEERS PRIVATE LIMITED
52.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.
52.01 | (a) Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 3.00 | Cum | 10.00 | 4500.00 | 13500.00 | 4000.00 | 12000.00 | 12000.00 | JCC ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 17466462.00 |  | 18455555.00
Lowest Amount Quoted BY: K B CONTRACT (P) LTD(17466462.00)

## BOQ Summary
BOQ Summary Details Tender Title: Finalization of site for CCR Room, Sub Station as well as renovation construction of VIP Room, Pilot/Crew Room for VVIP/VIP Movement, NSG Control Room and Anti-Hijack Control Room at Safdarjung Airport (SH- Electrical works) Tender ID: 2024_AAI_188653_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | K B CONTRACT (P) LTD | 17466462.00 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED | 18455555.00 | L2