## BoQ1
Government eProcurement System Created By: Ravindra Kumar Created Date/Time: 12-Apr-2024 03:45 PM Tender Title: Widening and Strengthening of Existing apron and taxi at Bareilly Airport SH Provision of Taxiway Edge Lighting and Signages Tender ID: 2024_AAI_188756_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Widening and Strengthening of Apron and Taxi Track at Bareilly Airport. Sub Head : Provision of Taxiway Edge Lighting & Signages.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -688999 |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)--689036
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of elevated type Omni- directional, medium intensity LED Taxiway Edge Light fitting suitable for Taxiway, Apron Edge Lights, Turning Pad Lights for operation at 2.8 to 6.6 Amps, series circuit supply, complete with Omni-directional Blue lens, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with 06 No's, M - 10 stainless steel bolts and other accessories including White LED lamp not more then 10 watt ,with an integrated encapsulated electronic module as required , suitable for installtion on existing CI transformer housing box, etc. complete as required. Conforming the manufactures who meet FAA/ICAO/DGCA-CAR requirement. Omni- directional Blue | 90.00 | Each |  | 4000.00 | 360000.00 | 4500.00 | 405000.00 | 360000.00 | Manish Electricals
2.00 | Supply of FAA/ICAO/DGCA-CAR certified LED type Inset Omni-directional fitting for aviation visual aid at taxiway line suitable for curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Omni- directional Blue | 10.00 | Each |  | 68000.00 | 680000.00 | 72000.00 | 720000.00 | 680000.00 | Manish Electricals
3.00 | Supply of FAA/ICAO/DGCA-CAR certified LED type Inset Uni-directional Stop Bar fitting for aviation visual aid at Rapid taxiway line suitable for curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Uni-directional Stop Bar Fitting Red. | 11.00 | Each |  | 74000.00 | 814000.00 | 70000.00 | 770000.00 | 770000.00 | JCC ENGINEERS PRIVATE LIMITED
4.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thyristor type suitable for operation on 230/415 volts, 50Hz input AC supply with 6.6A output having 5 steps variation of current output and able to communicate with local & remote operational controlled system (RC-Desk/ALCMS), with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, individual lamp control and monitoring system module, hours run counter, LCD display, complete as required for the following rating and confirm to specifications enclosed., should have provision of MAFI compitability. 2.5 kw | 1.00 | Each |  | 180000.00 | 180000.00 | 195000.00 | 195000.00 | 180000.00 | Manish Electricals
5.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thristor type suitable for operation on 230/415 volts, 50Hz input AC supply with 6.6A output having 5 steps variation of current output and able to communicate with local & remote operational controlled system (RC-Desk/ALCMS), with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, individual lamp control and monitoring system module, hours run counter, LCD display, complete as required for the following rating and confirm to specifications enclosed.should have provision of MAFI compitability. 4 kw | 2.00 | Each |  | 190000.00 | 380000.00 | 195000.00 | 390000.00 | 380000.00 | Manish Electricals
6.00 | Supply of 5 kV Type C without metallic screen, Cross-linked polyethylene 6 Sqmm unshielded round stranded bare copper class 2 with Polyethylene (PE) outer sheath cable as required as per the technical specification. UN-SHIELDED PRIMARY CABLE 1CX 6SQ MM | 7000.00 | Metre |  | 90.00 | 630000.00 | 79.00 | 553000.00 | 553000.00 | JCC ENGINEERS PRIVATE LIMITED
7.00 | Supply of 2X4 Sq.mm secondary lead made out of multi stranded copper conductor, EPR insulated PCP sheathed, anti termite & anti rodent treated 600V grade cable as specified in particular specification and as required. | 200.00 | Metre |  | 210.00 | 42000.00 | 200.00 | 40000.00 | 40000.00 | JCC ENGINEERS PRIVATE LIMITED
8.00 | Supply of 6 Sqmm Receptacle of type I, class B connector & suitable field attachment with 5 KV grade XLPE insulated PE sheathed single core screened copper conductor cable as required. | 220.00 | Nos |  | 425.00 | 93500.00 | 450.00 | 99000.00 | 93500.00 | Manish Electricals
9.00 | Supply of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base, conforming to IS:12290 (latest edition) with up to amendments complete as per specifications attached. 15 watts, 6.6A/6.6A | 110.00 | Each |  | 3000.00 | 330000.00 | 3150.00 | 346500.00 | 330000.00 | Manish Electricals
10.00 | Supply of following size of 1.1KV grade multicore stranded aluminium conductor XLPE insulated & PVC sheathed armoured cable (FRLS Type) as per IS: 7098 (Part-1) 1988 complete as required & as per enclosed specification. (4C x 10 Sqmm) | 200.00 | Metre |  | 270.00 | 54000.00 | 250.00 | 50000.00 | 50000.00 | JCC ENGINEERS PRIVATE LIMITED
11.00 | Supply of 3.5 core 95 sq.mm size heavy duty XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098, Part-I 1988 with up to date amendments and confirm to particular specifications enclosed in the tender. | 100.00 | Metre |  | 535.00 | 53500.00 | 550.00 | 55000.00 | 53500.00 | Manish Electricals
12.00 | Supply of CI Base plate of size 10 mm thick and outside dia 330 mm, surface suitable to receive a light fitting-base plate on the top and having a clear opening of 220 mm hole centre and 6 nos of holes tapped to receive M-10 stainless steel bolts as per drawing as required. | 10.00 | Each |  | 900.00 | 9000.00 | 1150.00 | 11500.00 | 9000.00 | Manish Electricals
13.00 | Supply of following dia ISI mark HDPE pipe of PN6 & PE80 grade with accessories etc. and as per relevant IS amended upto date complete as per site requirement. 50 mm dia {OD} | 2200.00 | Mtr. |  | 76.00 | 167200.00 | 65.00 | 143000.00 | 143000.00 | JCC ENGINEERS PRIVATE LIMITED
14.00 | Supply, installation, testing and commissioning of LED Guidance Sign Board of various sizes as per ICAO Annex.14 Vol.I (legends as approved by Engineer-in-Charge) made out of anodized 2mm thick Aluminum frame with suitable angle support with 1.5MM thick (minimum) Al. back cover, 4 MM thick polycarbonate sheet with glare free face, the letter & symbol should be screen printed on inside of sign face made of self adhesive film of 3M applied on the inside face with required coloring, mandatory/information guidence suitable arrangement shall be made for water tightness & locking arrangement, signboard shall be uniformly internally illuminated with LED lights with DC converter to achieve illumination level operated on input source 2.5A to 6.6A constant current without flickering including isolating transformer, supporting frangible legs & frame etc. complete as required i/c signages installation in 1:2:4 grade cement concrete of 400 x 400 x500mm (for legs) and a total base of 150mm thick which extends all around the board with the distance of 1000mm (front, back and both the sides). The concrete base and leg foundation should be on the same level and 20-25mm above the ground level complete as required. | 13.00 | Sq. Mtr. |  | 33000.00 | 429000.00 | 32500.00 | 422500.00 | 422500.00 | JCC ENGINEERS PRIVATE LIMITED
15.00 | Installation, testing and commissioning of following Inset fittings with core drilling, aligning & setting including providing sealing material & installation of isolating transformers, crimping / joining of plug & receptacles and moulding the leads, connections etc. as required. | 20.00 | Job |  | 7000.00 | 140000.00 | 8000.00 | 160000.00 | 140000.00 | Manish Electricals
16.00 | Installation, testing and commissioning of elevated taxiway fittings aligning, on the existing transformer housing box i/c. installation of transformer, lens and other accessories, alignment, levelling etc. as required, sealing material, installation of isolating transformer etc. as required. | 90.00 | Job |  | 300.00 | 27000.00 | 350.00 | 31500.00 | 27000.00 | Manish Electricals
17.00 | Installation, testing & commissioning of 2.5 / 4 KW microprocessor controlled CCRs including providing earth connection with GI strip of size 25mm x 5mm, all necessary arrangement, end termination with plug and recepticle etc. for commissioning of CCR etc. as required. | 3.00 | Job |  | 10000.00 | 30000.00 | 9500.00 | 28500.00 | 28500.00 | JCC ENGINEERS PRIVATE LIMITED
18.00 | Making field connections of 5 KV grade 6 Sq.mm PVC / XLPE insulated PVC sheathed copper conductor single core cable with 5 KV grade plug/ receptacle suitable for field attachment with HT tape complete as required. | 220.00 | Nos. |  | 180.00 | 39600.00 | 220.00 | 48400.00 | 39600.00 | Manish Electricals
19.00 | Installation, Testing and Commissioning of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits including HT tape etc complete as required. 15/45/100 watts, 6.6A/6.6A | 110.00 | Nos. |  | 250.00 | 27500.00 | 345.00 | 37950.00 | 27500.00 | Manish Electricals
20.00 | Laying of one no. PVC insulated & PVC sheathed AFL cable of 5 KV grade size upto 25 sqmm in the existing RCC/ METAL/HDPE/Open Trench pipe as required. | 4000.00 | Metre |  | 15.00 | 60000.00 | 40.00 | 160000.00 | 60000.00 | Manish Electricals
21.00 | Installation of Transformer housing boxes by excavation of earth upto depth of 525 mm with a base concrete of 1:3:6 of size 630x630x100 mm thick, all round concrete of 1:2:4, 150mm thick,the top sloped with 1:2:4 cement concrete including providing and fixing 250 mm long 15mm dia "B" class GI pipe with check nut for drainage of water complete as required as per the technical specification. (wherever the transformers boxes are to be installed in a line, the same has to be aligned in such a way that the centre fall in a straight line) etc. complete as required. | 20.00 | Each |  | 2800.00 | 56000.00 | 3000.00 | 60000.00 | 56000.00 | Manish Electricals
22.00 | Installation of CI Base plate (complete with all accessories) of size 10 mm thick and outside dia 330 mm complete with all accessories as required . | 10.00 | Each |  | 300.00 | 3000.00 | 260.00 | 2600.00 | 2600.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Laying of 50 mm dia HDPE pipe to connect the consecutive existing Trasformer Housing Boxes at a sutaible depth i/c providing the socket , lock/ check nut/ other suitable accessories at both sides of Transformer housing wall to fix pipe. The laying shall be in hard surface/soft surface with standard industries practice with all safety and precautions including getting out the excavated materials, returning the soil as requied in layers not exceeding 20cm in depth including consolidating each deposit layer by ramming & watering etc. making good the same & disposal of unusable material etc. as required as per direction of Engineer-in-charge. | 1000.00 | Mtr. |  | 170.00 | 170000.00 | 195.00 | 195000.00 | 170000.00 | Manish Electricals
24.00 | Kerf cutting with machine on taxiway of Bitumin surface of suitable depth and width upto 2/4/6/8 nos of 1x4sqmm secondary cable etc. complete as required (without refilling by suitable sealing material). | 75.00 | Mtr. |  | 700.00 | 52500.00 | 600.00 | 45000.00 | 45000.00 | JCC ENGINEERS PRIVATE LIMITED
25.00 | Laying 2/4/6/8 nos of 4sqmm secondary leads in the existing taxiway surface trench, filling up polysulphide compound and baker rod foam etc. complete as required (Including Material cost). | 75.00 | Mtr. |  | 50.00 | 3750.00 | 65.00 | 4875.00 | 3750.00 | Manish Electricals
26.00 | Supply of 1.5 TR AC 5 Star Rating Inverter type Split Air-Conditioner with stabliser free operation on 230 V (Voltage range 140 V to 270 V )AC supply complete with refrigerant ,plug top ,interconnection between indoor & outdoor unit with suitable size copper flexible wire & refrigerant pipeing up to 3 Mtrs & Suitable length drain pipe etc. with copper condenser & evaporator coils as per approved make list complete as required. | 2.00 | Job |  | 40000.00 | 80000.00 | 42500.00 | 85000.00 | 80000.00 | Manish Electricals
27.00 | Supply of 10 W LED 6500 K Wall mounted batten extruded aluminium heat sink provided for efficient heat dissipation & integrated electronic driver complete with all necessary accessories & lamp as required. (Havells, Code no. LheXACP7in1W010 or equivalent) | 6.00 | Each |  | 900.00 | 5400.00 | 770.00 | 4620.00 | 4620.00 | JCC ENGINEERS PRIVATE LIMITED
28.00 | Installation, testing & commissioning of 1.5 TR AC 5 Star Rating Split Air-Conditioner suitable for operation on 230 V AC supply complete with refrigerant piping, piping insulation, cabling work up to 3.0 Mtrs & fixing of outdoor unit in wall with suitable size MS stand etc. complete as required.. | 2.00 | Job |  | 3000.00 | 6000.00 | 2250.00 | 4500.00 | 4500.00 | JCC ENGINEERS PRIVATE LIMITED
29.00 | Supply & fixing of extra refrigerant copper tubing of suitable size as per recommendation of OEM for both suction and discharge along with nitrile rubber insulation for tube covering suitable for 1.5 TR / 2.0 TR Air conditioner laying/clamping on surface, chiselling & making good of wall etc connection complete as per requirement of site & as instructed by EIC. | 6.00 | Mtrs |  | 700.00 | 4200.00 | 640.00 | 3840.00 | 3840.00 | JCC ENGINEERS PRIVATE LIMITED
30.00 | Supply & fixing of Extra draing piping of suitable size as per recommendation of OEM required beyond 3 Mtrs. of piping suitable for 1.5 TR / 2.0 TR Air conditioner laying/clamping on surface, chiselling & making good of wall etc connection complete as per requirement of site & as instructed by EIC. | 6.00 | Mtr. |  | 125.00 | 750.00 | 105.00 | 630.00 | 630.00 | JCC ENGINEERS PRIVATE LIMITED
31.00 | Supply and laying 80 mm dia medium class GI pipe direct in ground including execavation existing pavement size of 75cm (depth), and refilling etc as required. | 18.00 | Mtr. |  | 1200.00 | 21600.00 | 950.00 | 17100.00 | 17100.00 | JCC ENGINEERS PRIVATE LIMITED
32.00 | Earthing with GI earth pipe 4.5 m long and 40mm dia, accessories and providing masonary enclosure with cover plate on the top having locking arrangement and watering pipe, complete with charcoal and salt etc. as required. | 10.00 | Nos |  | 7500.00 | 75000.00 | 8200.00 | 82000.00 | 75000.00 | Manish Electricals
33.00 | Providing & laying of 6 SWG dia GI wire in the existing pipe/duct/ HDPE etc. i/c connection/termination with GI thimble etc. complete as required. | 4500.00 | Metre |  | 24.00 | 108000.00 | 18.00 | 81000.00 | 81000.00 | JCC ENGINEERS PRIVATE LIMITED
34.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement: 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2.00 | Each |  | 10000.00 | 20000.00 | 11500.00 | 23000.00 | 20000.00 | Manish Electricals
35.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe etc. as required. (Upto 35 sq. mm) | 100.00 | Metre |  | 25.00 | 2500.00 | 10.00 | 1000.00 | 1000.00 | JCC ENGINEERS PRIVATE LIMITED
36.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required Above 35 sq. mm and upto 95 sq. mm | 30.00 | Metre |  | 350.00 | 10500.00 | 420.00 | 12600.00 | 10500.00 | Manish Electricals
37.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe etc. as required. Above 35 sq. mm and upto 95 sq. mm | 70.00 | Metre |  | 30.00 | 2100.00 | 24.00 | 1680.00 | 1680.00 | JCC ENGINEERS PRIVATE LIMITED
38.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4 X 10 sq. mm (25mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 500.00 | 2000.00 | 440.00 | 1760.00 | 1760.00 | JCC ENGINEERS PRIVATE LIMITED
39.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 X 95 sq. mm (25mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 700.00 | 1400.00 | 760.00 | 1520.00 | 1400.00 | Manish Electricals
40.00 | Supplying and fixing 25 amps rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissionng etc. as required. | 1.00 | Each |  | 4700.00 | 4700.00 | 4850.00 | 4850.00 | 4700.00 | Manish Electricals
41.00 | Supplying and fixing 5 amps to 32 amps rating, 240 /415 volts, "C" curve, miniature circuit breaker suitable for inductive load of single poles in the existing MCB DB complete with connections, testing and comissioning etc. as required. | 4.00 | Each |  | 220.00 | 880.00 | 200.00 | 800.00 | 800.00 | JCC ENGINEERS PRIVATE LIMITED
42.00 | Supplying and fixing 6 way (2 + 4 way), double door, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator). | 1.00 | Each |  | 6000.00 | 6000.00 | 6550.00 | 6550.00 | 6000.00 | Manish Electricals
43.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. (Group -C). | 2.00 | Point |  | 1200.00 | 2400.00 | 1350.00 | 2700.00 | 2400.00 | Manish Electricals
44.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. (Group C) | 2.00 | Point |  | 1200.00 | 2400.00 | 1150.00 | 2300.00 | 2300.00 | JCC ENGINEERS PRIVATE LIMITED
45.00 | Supplying and fixing metal box of 180mm x 100mm x 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 6 pin 5/6 & 15/16 amps socket outlet and 15/16 amps piano type swtich connection, painting etc. as required. | 1.00 | Each |  | 400.00 | 400.00 | 441.00 | 441.00 | 400.00 | Manish Electricals
46.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
46.01 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 18.00 | Mtr. |  | 250.00 | 4500.00 | 200.00 | 3600.00 | 3600.00 | JCC ENGINEERS PRIVATE LIMITED
46.02 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | 30.00 | Mtr. |  | 350.00 | 10500.00 | 300.00 | 9000.00 | 9000.00 | JCC ENGINEERS PRIVATE LIMITED
47.00 | Supply,Installation,Testing & Commissioning of microprocesser controlled True online double conversion,parallel redundant mode3 phase 415V output UPS consisting of Following: i)UPS module with integrated 100% rectifier + inverter ,Battery circuit breaker for each ups module in CRCA housing with all required fixing acccessories & hardware. Galvanic isolation transformer K-rated, at the inverter output of Each UPS module. IN-bypass,interconnecting copper cabling (DCcabling) between UPS, Active filter, Battery breaker & Batteries of required length and size. ii)Sealed maintenanace free batteries for 2X7.5 KVA UPS with 30 min backup time on each UPS module with interconnectors,rackand accessories. Rack shall have shrods for safety from live battery terminals RAMLBS kit for 2N configuration. Rating of the UPS as follows:2X7.5 KVA parallel redundant UPS operating in parrallel redundant configuartion (CostofUPS,Batteries,Terminalconnections&wires,Rackforbatteries & mounting arrangement etc. all inclusive) | 1.00 | Set. |  | 700000.00 | 700000.00 | 670000.00 | 670000.00 | 670000.00 | JCC ENGINEERS PRIVATE LIMITED
48.00 | MV Panel Design, manufacture , supply , installation, testing and commissioning of following cubical type indoor panel, made of 2 mm thick CRCA sheet, base channel, doors & partitions complete with,moulded case circuit breakers, meters, indicating lamps, current transformer etc. complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection,bus bar shrouds at joints, wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel shall be dust & vermin proof construction with rubber gasket and powder coated . The panel shall be completely modular and compartmentalised with Form 3 B Seperation. The panel shall be free standing floor mounted type / wall mounted type as per site requirement. i. Incomer one (1) Nos. 63A, 25 kA, Four Pole, MCCB with variable thermal magnetic release for short circuit, over current and earth fault . Incomer shall be provided with the following.. One (1) No. Multi Function Meter with one set (3 Nos.) of CTs of ratio 63/5A Class 1.0, 15VA. One set ( 3 nos.) phase indication lamps with control MCB. One set ( 3 nos.) ON/OFF/TRIP indication lamp ii. Busbar : 100A , 25 kA TP + N Al. Busbar insulated with heat shrinkable sleeves and shall be colour coded. The neutral busbar shall be 100% rated. Separate earth busbar of 25 x 3 mm of GI shall be provided on the rear bottom of the panel. iii. Outgoings : Three (3) Nos. 32A, 25 kA, TP + N MCCB with continuous variable thermal magnetic release for short circuit, over current protection. Two (2) Nos. 16 A, 25 kA, TP + N MCCB with variable thermal magnetic release for short circuit, over current protection . Two (2) Nos. 16 A, 25 kA 2 pole MCB | 1.00 | Set |  | 100000.00 | 100000.00 | 95000.00 | 95000.00 | 95000.00 | JCC ENGINEERS PRIVATE LIMITED
49.00 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar | .55 | cum |  | 750.00 | 412.50 | 600.00 | 330.00 | 330.00 | JCC ENGINEERS PRIVATE LIMITED
50.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | .13 | cum |  | 750.00 | 97.50 | 650.00 | 84.50 | 84.50 | JCC ENGINEERS PRIVATE LIMITED
51.00 | Repairing of existing aluminium door and windows I/c opening the section and refixing the section as per the existing as per direction of Engineer-in-charge. | 2.00 | each |  | 950.00 | 1900.00 | 880.00 | 1760.00 | 1760.00 | JCC ENGINEERS PRIVATE LIMITED
52.00 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved. | .68 | cum |  | 500.00 | 340.00 | 450.00 | 306.00 | 306.00 | JCC ENGINEERS PRIVATE LIMITED
53.00 | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. All kinds of soil | 19.74 | sqm |  | 100.00 | 1974.00 | 65.00 | 1283.10 | 1283.10 | JCC ENGINEERS PRIVATE LIMITED
54.00 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | 6.26 | cum |  | 2800.00 | 17528.00 | 2500.00 | 15650.00 | 15650.00 | JCC ENGINEERS PRIVATE LIMITED
55.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:5:10 (1 cement : 5 coarse sand (zone-III) derived from natural sources : 10 graded stone aggregate 40 mm nominal size derived from natural sources) | 1.56 | cum |  | 2600.00 | 4056.00 | 2450.00 | 3822.00 | 3822.00 | JCC ENGINEERS PRIVATE LIMITED
56.00 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 12.5mm nominal size derived from natural sources) | 3.48 | sqm |  | 680.00 | 2366.40 | 860.00 | 2992.80 | 2366.40 | Manish Electricals
57.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand) | 8.98 | cum |  | 7000.00 | 62860.00 | 7200.00 | 64656.00 | 62860.00 | Manish Electricals
58.00 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level. Cement mortar 1:4 (1 cement :4 coarse sand) | 6.21 | sqm |  | 3200.00 | 19872.00 | 3500.00 | 21735.00 | 19872.00 | Manish Electricals
59.00 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : 125 mm | 2.00 | each |  | 270.00 | 540.00 | 220.00 | 440.00 | 440.00 | JCC ENGINEERS PRIVATE LIMITED
60.00 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade with necessary screws etc. complete : 50x10 mm | 2.00 | each |  | 420.00 | 840.00 | 465.00 | 930.00 | 840.00 | Manish Electricals
61.00 | Providing and fixing aluminium sliding door bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete : 250x16 mm | 2.00 | each |  | 580.00 | 1160.00 | 440.00 | 880.00 | 880.00 | JCC ENGINEERS PRIVATE LIMITED
62.00 | Providing and fixing ISI marked aluminium butt hinges anodised (anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with necessary screws etc. complete: 100x63x4 mm | 6.00 | each |  | 420.00 | 2520.00 | 350.00 | 2100.00 | 2100.00 | JCC ENGINEERS PRIVATE LIMITED
63.00 | Providing and fixing Brass 100mm mortice latch and lock with 6 levers without pair of handles (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | 2.00 | each |  | 380.00 | 760.00 | 350.00 | 700.00 | 700.00 | JCC ENGINEERS PRIVATE LIMITED
64.00 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868)transparent or dyed to required colour and shade with necessary screws etc. complete. Twin rubber stopper | 2.00 | each |  | 110.00 | 220.00 | 100.00 | 200.00 | 200.00 | JCC ENGINEERS PRIVATE LIMITED
65.00 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2.00 | each |  | 1500.00 | 3000.00 | 1150.00 | 2300.00 | 2300.00 | JCC ENGINEERS PRIVATE LIMITED
66.00 | Providing and laying Vitrified tiles in floor in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only . Laying of tiles will be done with the notch trowel, plier,wedge, clips of required thickness, leveling system and rubber mallet for placing the tiles gently and easily. Double charge vitrified tile polished finish of size. Size of Tile 600 x 600 mm | 13.13 | sqm |  | 490.00 | 6433.70 | 550.00 | 7221.50 | 6433.70 | Manish Electricals
67.00 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on interlocking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanized butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all Tsections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. 8 mm thick fully perforated calcium silicate board made with Calcareous & Siliceous materials reinforced with cellulose fiber manufactured through autoclaving process to give stable crystalline structure with minimum compressive strength 225 kg/ sq. cm, bending strength 100 kg/sq. cm , of size 595x595 mm, having perforation of dia. 10 mm with minimum perforated area 18 % with non woven tissue on the back side, having an NRC ( Noise Reduction Coefficient) of 0.85, with 50 mm thick rockwool of 48 kg /cum backing. | 11.84 | sqm |  | 510.00 | 6038.40 | 550.00 | 6512.00 | 6038.40 | Manish Electricals
68.00 | 12 mm cement plaster of mix : 1:6 (1 cement: 4 coarse sand) | 49.08 | sqm |  | 105.00 | 5153.40 | 95.00 | 4662.60 | 4662.60 | JCC ENGINEERS PRIVATE LIMITED
69.00 | 15 mm cement plaster on the rough side of single or half brick wall of mix : 1:6 (1 cement: 6 fine sand) | 44.30 | sqm |  | 110.00 | 4873.00 | 95.00 | 4208.50 | 4208.50 | JCC ENGINEERS PRIVATE LIMITED
70.00 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gram/litre, of approved manufacturer and of required shade and colour all complete to achieve even shade and colour: New work (two or more coats) over and including water thinnable priming coat with cement primer having VOC content less than 50 gram/litre. | 42.48 | cum |  | 45.00 | 1911.60 | 50.00 | 2124.00 | 1911.60 | Manish Electricals
71.00 | Finishing walls with Acrylic Smooth exterior paint of required shade: New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 0.90litre/10 sqm) | 38.09 | sqm |  | 65.00 | 2475.85 | 70.00 | 2666.30 | 2475.85 | Manish Electricals
72.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 200.00 | kg |  | 160.00 | 32000.00 | 200.00 | 40000.00 | 32000.00 | Manish Electricals
73.00 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade: Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture. | 20.00 | sqm |  | 70.00 | 1400.00 | 55.00 | 1100.00 | 1100.00 | JCC ENGINEERS PRIVATE LIMITED
74.00 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion. Powder coated aluminium (minimum thickness of powder coating 50 micron) | 28.35 | kg |  | 590.00 | 16726.50 | 620.00 | 17577.00 | 16726.50 | Manish Electricals
75.00 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately) Powder coated aluminium (minimum thickness of powder coating 50 micron) | 28.35 | kg |  | 510.00 | 14458.50 | 620.00 | 17577.00 | 14458.50 | Manish Electricals
76.00 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides. | 1.89 | sqm |  | 1780.00 | 3364.20 | 1840.00 | 3477.60 | 3364.20 | Manish Electricals
77.00 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5 mm thickness (weight not less than 12.50 kg/sqm) | .50 | sqm |  | 1780.00 | 890.00 | 1790.00 | 895.00 | 890.00 | Manish Electricals
78.00 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05 mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | 13.48 | sqm |  | 640.00 | 8627.20 | 550.00 | 7414.00 | 7414.00 | JCC ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 6227578.75 |  | 6325420.90
Lowest Amount Quoted BY: Manish Electricals(6227578.75)

## BOQ Summary
BOQ Summary Details Tender Title: Widening and Strengthening of Existing apron and taxi at Bareilly Airport SH Provision of Taxiway Edge Lighting and Signages Tender ID: 2024_AAI_188756_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 6227578.75 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED | 6325420.90 | L2