## BoQ1
Government eProcurement System Created By: Gajraj Singh Bhati Created Date/Time: 03-Jun-2024 01:37 PM Tender Title: Provision of expansion of SHA in Air Side at Civil Enclave Jodhpur. SH Airconditioning by VRF VRV type system in existing Security hold area Tender ID: 2024_AAI_189086_1
Tender Inviting Authority: Asst. General Manager Engg.- E, Airports Authority of India, Civil Airport, Jodhpur
Name of Work:- “Provision of expansion of SHA in Air Side at Civil Enclave Jodhpur. SH : Airconditioning by VRF/ VRV type system in existing Security hold area."
e-Tender ID.: 2024_AAI_189086_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NIRMAN ELECTRIC STORE (GSTN-08AOIPS5332P1Z8) BID ID -690851 |  | VOLKS ENERGIE PVT LTD (GSTN-07AADCV9396C1ZZ) BID ID -691340 |  | RA ENGINEERS(GSTN-NA)--688771 |  | ANUPAM AGENCIES(GSTN-NA)--690493
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Outdoor Unit: (Total 100 HP Minimum) Supply, installation, testing and commissioning of Variable Refrigerant Volume / Variable Refrigerant Flow modular type air-conditioning Outdoor Units including lifting, loading/unloading, and transportation charges, equiped with full / 100% multiple inverter driven highly efficient twin rotary / scroll based compressors, precoated aluminium fin type heat exchanger, low noise, condenser fans, GI coated condenser stands, microprocessor panel with sequential starting of condensing units, coils, expansion valves, filters, single phase preventer, complete with controller and with accessories & sub assemblies fittings etc. for proper functioning of atleast 80 Tr units, including full charging of R-410A refrigerant gas or green gas at site complete as per specifications. The Unit shall be constructed from heavy gauge mild steel panels and coated, suitable for air conditioning operation on three phase, 415 Volts, 50 Hz, RUN status & Remote start/stop command including multi-conecting KIT and MS Stand with vibration isolators, necessary accessories and top up of refrigerant gas at site.
1.01 | 26 to 30 HP dual compressor Module | 3.00 | Each | 0.00 | 551000.00 | 1653000.00 | 525000.00 | 1575000.00 | 432500.00 | 1297500.00 | 579000.00 | 1737000.00 | 1297500.00 | RA ENGINEERS
1.02 | 16 to 20 HP dual compressor Module | 1.00 | Each | 0.00 | 378000.00 | 378000.00 | 415000.00 | 415000.00 | 291374.00 | 291374.00 | 450000.00 | 450000.00 | 291374.00 | RA ENGINEERS
2.00 | Indoor Units: (Total 80 Ton Minimum) Supply, Installation, Testing & Commissioning of VRV/VRF based Ceiling suspended Cassette type Indoor unit including lifting, loading/unloading, and transportation charges, with 4 way / round flow, includes washable pre filter, fan section with low noise section, multi speed motor, coil section with DX-coil, outer cabinet, inbuilt drain pump and drain pan, insulation, pipe connections etc. with ability to communicate with Central Monitoring System and corded/wireless remote controller etc. as per specifications complete as required. including Core cutting , fitting, supports, any other civil work required.
2.01 | 8.0 Tr Ductable type indoor units | 2.00 | Each | 0.00 | 108000.00 | 216000.00 | 95000.00 | 190000.00 | 71300.00 | 142600.00 | 59500.00 | 119000.00 | 119000.00 | ANUPAM AGENCIES
2.02 | 4.0 Tr Tower type indoor units | 12.00 | Each | 0.00 | 98000.00 | 1176000.00 | 79500.00 | 954000.00 | 36600.00 | 439200.00 | 48000.00 | 576000.00 | 439200.00 | RA ENGINEERS
2.03 | 4.0 Tr Cassette type indoor units | 3.00 | Each | 0.00 | 42500.00 | 127500.00 | 55000.00 | 165000.00 | 40654.00 | 121962.00 | 49500.00 | 148500.00 | 121962.00 | RA ENGINEERS
2.04 | 2.0 Tr Wall mounted type indoor units | 2.00 | Each | 0.00 | 30500.00 | 61000.00 | 45000.00 | 90000.00 | 22070.00 | 44140.00 | 21500.00 | 43000.00 | 43000.00 | ANUPAM AGENCIES
3.00 | Supply, Installation, Testing & Commissioning of Central Controller capable of centrally controlling all the outdoor and indoor units including temprature, On/Off, control wiring and connections etc. as per OEM recommandation complete as required. | 1.00 | Each | 0.00 | 41000.00 | 41000.00 | 25000.00 | 25000.00 | 47398.00 | 47398.00 | 35000.00 | 35000.00 | 25000.00 | VOLKS ENERGIE PVT LTD
4.00 | Refrigerant Copper Piping: Supply, installation, testing of inter connecting of hard drawn heavy duty copper refrigerant pipe of following sizes suitable for R-410A refrigerant including suitable no. of Y, T Joints/ Headers/Refnets for SUB & connections of refrigerant pipes to units alongwith 19mm thick closed cell elastometric nitrile rubber tubular insulation(13/19 mm) between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS / GI / STUDS / CLAMPS / HANGERS etc. complete as required. The thickness of copper pipe shall be as per OEM Standards. |  |  | 0.00
4.10 | (a) 34.9 mm O.D. (insulation : 19 mm) | 100.00 | Each | 0.00 | 1800.00 | 180000.00 | 1500.00 | 150000.00 | 1210.00 | 121000.00 | 2100.00 | 210000.00 | 121000.00 | RA ENGINEERS
4.20 | (b) 28.6 mm O.D. (insulation : 19 mm) | 100.00 | Each | 0.00 | 1550.00 | 155000.00 | 1200.00 | 120000.00 | 1040.00 | 104000.00 | 1750.00 | 175000.00 | 104000.00 | RA ENGINEERS
4.30 | (c) 22.2 mm O.D. (insulation : 19 mm) | 50.00 | Each | 0.00 | 1200.00 | 60000.00 | 900.00 | 45000.00 | 950.00 | 47500.00 | 1350.00 | 67500.00 | 45000.00 | VOLKS ENERGIE PVT LTD
4.40 | (d) 19.1 mm O.D. (insulation : 19 mm) | 50.00 | Each | 0.00 | 890.00 | 44500.00 | 790.00 | 39500.00 | 790.00 | 39500.00 | 1200.00 | 60000.00 | 39500.00 | RA ENGINEERS, VOLKS ENERGIE PVT LTD
4.50 | (e) 15.9 mm O.D. (insulation : 19 mm) | 50.00 | Each | 0.00 | 850.00 | 42500.00 | 500.00 | 25000.00 | 620.00 | 31000.00 | 950.00 | 47500.00 | 25000.00 | VOLKS ENERGIE PVT LTD
5.00 | Drain Piping: Supply, installation, testing and commissioning of Rigid UPVC standard make piping for drain line complete with fittings, joints, elbows etc. supports as per specification and duly insulated with 6mm thick closed cell nitrile rubber insulation.
5.10 | (a) 32 mm dia | 150.00 | Meter | 0.00 | 260.00 | 39000.00 | 100.00 | 15000.00 | 280.00 | 42000.00 | 150.00 | 22500.00 | 15000.00 | VOLKS ENERGIE PVT LTD
5.20 | (b) 25 mm dia | 100.00 | Meter | 0.00 | 180.00 | 18000.00 | 100.00 | 10000.00 | 190.00 | 19000.00 | 100.00 | 10000.00 | 10000.00 | ANUPAM AGENCIES, VOLKS ENERGIE PVT LTD
6.00 | Control & Transmission Wiring: Supply and drawing of 2 x 0.75 Sq.mm PVC insulated, PVC sheathed and shielded copper conductor control cum transmission Cable between indoor and out door unit & outdoor units to central remotes controllers as required in the existing surface/recessed steel/ PVC conduit etc. complete as required. | 450.00 | Meter | 0.00 | 250.00 | 112500.00 | 50.00 | 22500.00 | 120.00 | 54000.00 | 175.00 | 78750.00 | 22500.00 | VOLKS ENERGIE PVT LTD
7.00 | Supply, Installation, Testing of Long Life Mesh Flitters- Ducted | 2.00 | Each | 0.00 | 6500.00 | 13000.00 | 4500.00 | 9000.00 | 2100.00 | 4200.00 | 2000.00 | 4000.00 | 4000.00 | ANUPAM AGENCIES
8.00 | Supply, Installation, & Testing of Double Canvas Flexible Connection constructed of fire resitant material. | 2.00 | Set | 0.00 | 2200.00 | 4400.00 | 5500.00 | 11000.00 | 3200.00 | 6400.00 | 2000.00 | 4000.00 | 4000.00 | ANUPAM AGENCIES
9.00 | Dismantling of existing 2TR/3TR/4TR wall mounted/floor mounted/ Cassette type split Acs/ including indoor and outdoor units, stand, stablizer, refrigerant pipe etc. complete as required as per site conditions and shifting the material from site to AAI store. | 11.00 | Each | 0.00 | 800.00 | 8800.00 | 4500.00 | 49500.00 | 2500.00 | 27500.00 | 1200.00 | 13200.00 | 8800.00 | NIRMAN ELECTRIC STORE
10.00 | Amending the existing POP/Wooden/Mattle ceiling for Ductable AC & refinishing the same material as existing. | 50.00 | SQFT | 0.00 | 200.00 | 10000.00 | 800.00 | 40000.00 | 160.00 | 8000.00 | 300.00 | 15000.00 | 8000.00 | RA ENGINEERS
11.00 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/ round ducting/ plenum complete as per IS 655-2006 with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of 0.63 mm sheet thickness complete as required. | 20.00 | Sq.Mtr | 0.00 | 850.00 | 17000.00 | 1500.00 | 30000.00 | 1100.00 | 22000.00 | 1500.00 | 30000.00 | 17000.00 | NIRMAN ELECTRIC STORE
12.00 | Supply,installation,testing and commissioning of Supply air jet Nozzle in extruded Aluminium construction and powder coated finish as per specifications and drawings of 275 mm dia. | 8.00 | Each | 0.00 | 4200.00 | 33600.00 | 4500.00 | 36000.00 | 2100.00 | 16800.00 | 4000.00 | 32000.00 | 16800.00 | RA ENGINEERS
13.00 | Supply of 1.1 KV grade XLPE armoured aluminium conductor cable of 3.5 x 185 sqmm sizes & as per IS:7098-part-I specifications i/c loading/unloading & transportation of cables etc. complete as required: | 180.00 | Mtrs. | 0.00 | 410.00 | 73800.00 | 700.00 | 126000.00 | 760.00 | 136800.00 | 820.00 | 147600.00 | 73800.00 | NIRMAN ELECTRIC STORE
14.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 95 Sqmm and upto 185 sqmm (clamped with 25/40 X 3mm thick MS flat clamp). | 150.00 | Mtrs. | 0.00 | 60.00 | 9000.00 | 100.00 | 15000.00 | 190.00 | 28500.00 | 355.00 | 53250.00 | 9000.00 | NIRMAN ELECTRIC STORE
15.00 | Suppling and making end termination with brass compression gland and copper/aluminium lugs according to the cable for 3.5mm X 185 sq. mm (57mm) aluminimum cable. size for PVC/ XLPE insulated and PVC sheathed armoured copper/ aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Set | 0.00 | 92.00 | 184.00 | 4500.00 | 9000.00 | 4500.00 | 9000.00 | 3000.00 | 6000.00 | 184.00 | NIRMAN ELECTRIC STORE
16.00 | Design, manufacturing, supply, installation, testing and commissioning of cubical type totally enclosed free standing, dust free, damp and vermin proof and water proof double door outdoor (IP 66) LT feeder panel fabricated out of 2 mm thick CRCA sheet duly powder coated and including supply and fixing of the following items and interconnections,wiring with suitable sizes wires/ cables and including mounting legs, all civil works like PCC, brick work pedestal, plastering etc. and as per specification as required. Incommer a) 01 No. 200 Amps, FP MCCB (Ics=100%Icu, 25 KA) Bus Bar Aluminium 200A Outgoings a) 03 Nos. 63 Amps, FP MCCB (Ics=100%Icu, 16 KA) b) 01 No. 36 Amps, FP MCCB (Ics=100%Icu, 16 KA) c) 01 set RYB LED Indication lamp with protection MCB. | 1.00 | Each | 0.00 | 12050.00 | 12050.00 | 155000.00 | 155000.00 | 175000.00 | 175000.00 | 145000.00 | 145000.00 | 12050.00 | NIRMAN ELECTRIC STORE
17.00 | Supplying and fixing suitable size GI box/polycarbonate with modular plate and cover in FRLS on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 19.00 | Each | 0.00 | 280.00 | 5320.00 | 500.00 | 9500.00 | 800.00 | 15200.00 | 715.00 | 13585.00 | 5320.00 | NIRMAN ELECTRIC STORE
18.00 | Wiring for circuit/ submain wiring alongwith earth wire with the 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required. | 150.00 | Mtrs. | 0.00 | 70.00 | 10500.00 | 120.00 | 18000.00 | 245.00 | 36750.00 | 210.00 | 31500.00 | 10500.00 | NIRMAN ELECTRIC STORE
19.00 | Wiring for circuit/ submain wiring alongwith earth wire with the 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required. | 200.00 | Mtrs. | 0.00 | 140.00 | 28000.00 | 120.00 | 24000.00 | 288.00 | 57600.00 | 325.00 | 65000.00 | 24000.00 | VOLKS ENERGIE PVT LTD
20.00 | Supplying and fixing 12 way , Double door, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 2.00 | Each | 0.00 | 8550.00 | 17100.00 | 25000.00 | 50000.00 | 4501.00 | 9002.00 | 14000.00 | 28000.00 | 9002.00 | RA ENGINEERS
21.00 | Providing and fixing 63 A capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required. | 2.00 | Each | 0.00 | 7775.00 | 15550.00 | 4500.00 | 9000.00 | 3000.00 | 6000.00 | 7900.00 | 15800.00 | 6000.00 | RA ENGINEERS
22.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of Single pole in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 20.00 | Each | 0.00 | 140.00 | 2800.00 | 800.00 | 16000.00 | 2300.00 | 46000.00 | 170.00 | 3400.00 | 2800.00 | NIRMAN ELECTRIC STORE
| Total in Figures |  |  |  |  | 4565104.00 |  | 4448000.00 |  | 3446926.00 |  | 4387085.00
Lowest Amount Quoted BY: RA ENGINEERS(3446926.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of expansion of SHA in Air Side at Civil Enclave Jodhpur. SH Airconditioning by VRF VRV type system in existing Security hold area Tender ID: 2024_AAI_189086_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RA ENGINEERS | 3446926.00 | L1
| 2 | ANUPAM AGENCIES | 4387085.00 | L2
| 3 | VOLKS ENERGIE PVT LTD | 4448000.00 | L3
| 4 | NIRMAN ELECTRIC STORE | 4565104.00 | L4