## BoQ1
Government eProcurement System Created By: Rudra Prasad Acharya Created Date/Time: 06-May-2024 06:17 PM Tender Title: SITC of 250KVA UPS with outgoing LT panel and Commercial LT panel at T-1 terminal BPI Airport, Bhubaneswar. Tender ID: 2024_AAI_191172_1
Tender Inviting Authority: Asst. General Manager (Engg.-Elect.)-II, Airports Authority of India, B.P.I.Airport, Bhubaneswar.
Name of Work: SITC of 250KVA UPS with outgoing LT panel and Commercial LT panel at T-1 terminal BPI Airport, Bhubaneswar.
Contract No: 2024_AAI_191172_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GIRI ENTERPRISES (GSTN-20ACEPG3920H1ZA) BID ID -692166 |  | Youngmen Traders (GSTN-19AEIPB6323B1ZZ) BID ID -693355 |  | RASS CONTRACTOR AND ENGINEERS (GSTN-09AFIPR1600N1Z7) BID ID -693454 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -693520 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -693522 |  | vardhman Airport solutions pvt. Ltd.(GSTN-NA)--693414
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design,Supply, Installation, Testing & Commissioning of 250KVA Nominal capacity UPS unit, 3-phase-4 wire, suitable for operating condition 415±15%, 3ph, 50Hz ± 10% ,IGBT rectifier and PWM Controlled IGBT inverter based online double conversion(>=96% efficiency at 50-100% Load) type DSP controlled UPS, True Sinewave (with Electrical Neutral on Output side), 100% unbalanced load and working on necessary static bypass system & maintenance bypass outside of UPS with suitable isolator confirming to the specification attached along with identical isolation transformer at output suitable for the system. UPS should be dust and vermin proof duly painted and with ventilation ducts, floor mounted, forced air cooling suitable for 15 minutes backup time for UPS on full load and capable of giving desired output of 3 phase 415 V 50 Hz with Modbus/SNMP,RS485 communication facility and surge protection system conforming to standards IEC 62040-1,2,3 , IS: 16242-1 and necessary upto date amendments etc. as required as per tender condition including preventative maintenance and checks during 02 years warranty as per site requirements. | 1.00 | Job |  | 3000000.00 | 3000000.00 | 2250000.00 | 2250000.00 | 1450000.00 | 1450000.00 | 1950000.00 | 1950000.00 | 2065000.00 | 2065000.00 | 2156050.00 | 2156050.00 | 1450000.00 | RASS CONTRACTOR AND ENGINEERS
2.00 | Design & SITC (Supply, Installation, Testing & Commissioning) of VRLA battery bank mounted in suitable rack (as per recommendation of battery manufatcurer) consisting of 12 V VRLA battery capable of providing backup for at least 15 mins at full rated load of above mentioned UPS (as per item no.1) along with necessary intercell connectors, interconnection of UPS and Battery bank using suitable rated fire resistance Nyvin copper cables (as recommended by battery manufacturer) including preventative maintenance and checks during 02 year warranty. | 1.00 | Set |  | 900000.00 | 900000.00 | 1500000.00 | 1500000.00 | 850000.00 | 850000.00 | 1750000.00 | 1750000.00 | 1975000.00 | 1975000.00 | 1245694.00 | 1245694.00 | 850000.00 | RASS CONTRACTOR AND ENGINEERS
3.00 | Supply, Installation, Testing and Commissioning of TTA type indoor cubicle LT panel as per IEC 61439, IP42, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars with 100% size neutral bus as that of phase bus, supported with SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 35 kA for 1 sec, bottom base channel of MS section not less than 75 mm x 40 mm, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/ flexible copper connections from main earth bus bar to switchgears with required size of Cooper conductors/ bus bars and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable,cable alleys, cable gland plates in two halves, including control providing following switchgears/ accessories as per specifications.
3.01 | Incomer 1 Nos. 400A, 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification and incomer shall be provided with following accessories. 1 Set of phase indicating LED lamps with 2 amp back up MCB. 1 No. 96 x 96 sqmm Digital MFM meter and 3 nos. Cast resin CTs of ratio 400/5A , Class 0.5 accuracy and 10 VA burden, suitable to measure voltage,Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI & Individual Odd Harmonics for voltage and current including THD upto 31st Order with RS 485 port. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB Busbars 4P aluminium bus bars of 600A capacity with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. The electrical panel shall be fully ventilated to maintain internal body temp. < 40 deg 'C' when room amb. temp. is equal of less than 35 deg 'C'. Required ventilation fans shall be provided and tested. Outgoings 2 Nos.125A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA) ,1 Sets - ON,OFF,Trip LED lamps ,Digital Ammeter etc. 10 Nos. 63A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA),1 Sets - ON,OFF,Trip LED lamps ,Digital Ammeter Ammeter. For busbar section-1 Set Surge protection device Type 2 ( Class C), 4 Module, MOV type suitable for 8/ 20µs surge,Voltage Protection level Up < 1.5kV, Operating Temperature -40 deg 'c' - +80 deg 'C', Connected Between 3Nos. phase to neutral and 1Nos. neutral to earth with discharge Current Imax.≥ 40KA Per module & In ≥ 20kA per Module. SPD shall be with built in fuse and plugable type. For connecting SPD minimum 10sqmm copper wire must be used & length of connecting leads shall not be more than 500mm per mode connection including all necessary accessories. The SPD shall be complient and tested from KEMA KEUR / VDE / NABL for UPS input tested as per IEC 61643-11 / UL | 1.00 | Job |  | 370000.00 | 370000.00 | 475000.00 | 475000.00 | 850000.00 | 850000.00 | 625000.00 | 625000.00 | 2050000.00 | 2050000.00 | 558420.00 | 558420.00 | 370000.00 | GIRI ENTERPRISES
4.00 | Supply and installation of 400A, 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification for installation in existing LT panel vacant space with supply of busbar,connection material accessories etc. | 3.00 | Nos. |  | 20000.00 | 60000.00 | 65000.00 | 195000.00 | 65000.00 | 195000.00 | 39500.00 | 118500.00 | 135000.00 | 405000.00 | 44649.00 | 133947.00 | 60000.00 | GIRI ENTERPRISES
5.00 | Design, fabrication,Supply, Installation, testing & commissioning of TTA type bothside extendable,floor mounted type, fully compartmentalised, front operated, back openable, LT cubicle panel suitable for incoming and out going cable entry from bottom designed verified as per IEC 61439-1 & 2 and international recognized test house/CPRI/ERDA tested . Bus Bars: 1250A, 3phase with 100% Neutral Aluminium busbar- 1 set. Incomers 1 Nos Incomer - 800 Amp 415V, 35KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of atleast 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvolatge, undervoltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. Neutral protection shall be settable at 50% and 100%. ACB shall be capable of communicating data on Ethernet protocoland on-line parameterization capable. One number Digital MFM meter with CTs,Cl-0.5 accuracy suitable to measure V,I,W, VAR, VA, KWh, KVARh, VAh, Pf 1 Sets - ON,OFF,Trip, Spring Charged, ready to close indication LED lamps with back-up MCB 1 Sets - R,Y,B Phase indication LED lamp with back up MCB Outgoings: 2 Nos.200 A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA) ,1 Sets - ON,OFF,Trip LED lamps ,KWH Meter. 2 Nos.160A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA) ,1 Sets - ON,OFF,Trip LED lamps ,KWH meter etc. 4 Nos.125 A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA) ,1 Sets - ON,OFF,Trip LED lamps ,KWH meter etc. 6 Nos.63 A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu =25 KA) ,1 Sets - ON,OFF,Trip LED lamps ,KWH meter etc. | 1.00 | Job |  | 590000.00 | 590000.00 | 950000.00 | 950000.00 | 1300000.00 | 1300000.00 | 950000.00 | 950000.00 | 2600000.00 | 2600000.00 | 785568.00 | 785568.00 | 590000.00 | GIRI ENTERPRISES
6.00 | Earthing with copper earth plate 600 mm x 600 mm x 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal / coke and salt as required. | 2.00 | Set |  | 15000.00 | 30000.00 | 12000.00 | 24000.00 | 16500.00 | 33000.00 | 16000.00 | 32000.00 | 18000.00 | 36000.00 | 19677.00 | 39354.00 | 24000.00 | Youngmen Traders
7.00 | Earthing with GI earth plate 600 mm x 600 mm x 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal / coke and salt as required. | 6.00 | Set |  | 11000.00 | 66000.00 | 7000.00 | 42000.00 | 8500.00 | 51000.00 | 11000.00 | 66000.00 | 7000.00 | 42000.00 | 11136.00 | 66816.00 | 42000.00 | Youngmen Traders, Manish Electricals
8.00 | Providing and fixing 50 mm x 6 mm copper strip in 80 mm dia G.I pipe from earth electrode including connnection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter |  | 2565.00 | 76950.00 | 2600.00 | 78000.00 | 2800.00 | 84000.00 | 3550.00 | 106500.00 | 1050.00 | 31500.00 | 3856.00 | 115680.00 | 31500.00 | Manish Electricals
9.00 | Providing and fixing 50 mm x 6 mm GI strip in 80 mm dia G.I pipe from earth electrode including connnection with GI nut, bolt, spring, washer excavation and re-filling etc. as required. | 180.00 | Meter |  | 2584.00 | 465120.00 | 1200.00 | 216000.00 | 850.00 | 153000.00 | 1190.00 | 214200.00 | 600.00 | 108000.00 | 1348.00 | 242640.00 | 108000.00 | Manish Electricals
10.00 | Providing and fixing 50 mm x 6 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Meter |  | 2400.00 | 48000.00 | 1800.00 | 36000.00 | 1650.00 | 33000.00 | 3100.00 | 62000.00 | 1050.00 | 21000.00 | 2809.00 | 56180.00 | 21000.00 | Manish Electricals
11.00 | Supplying and installing following size of Hot dip Galvanised perforated type cable trays of following sections along with connectors, necessary wall support made of RS Angle including bolts & nuts etc. and painting as required.
11.01 | a) 450 mm wide X 62.5 mm X 1.6 mm thick | 250.00 | Meter |  | 1500.00 | 375000.00 | 1100.00 | 275000.00 | 1250.00 | 312500.00 | 1150.00 | 287500.00 | 1500.00 | 375000.00 | 1030.00 | 257500.00 | 257500.00 | vardhman Airport solutions pvt. Ltd.
11.02 | b) 150 mm wide X 50 mm X 2mm thick | 50.00 | Meter |  | 600.00 | 30000.00 | 600.00 | 30000.00 | 950.00 | 47500.00 | 670.00 | 33500.00 | 700.00 | 35000.00 | 478.00 | 23900.00 | 23900.00 | vardhman Airport solutions pvt. Ltd.
12.00 | Supply of following size power cables of 1.1 KV grade, XLPE Insulated PVC Sheathed aluminium conductor cable, armoured, and PVC sheathed conforming to IS 7098 Part-I with up to date ammendments.
12.01 | (a)3.5Cx 50sq mm | 500.00 | Meter |  | 225.00 | 112500.00 | 228.00 | 114000.00 | 240.00 | 120000.00 | 230.00 | 115000.00 | 510.00 | 255000.00 | 218.00 | 109000.00 | 109000.00 | vardhman Airport solutions pvt. Ltd.
12.02 | (b)3.5Cx70 Sq mm | 500.00 | Meter |  | 300.00 | 150000.00 | 310.00 | 155000.00 | 330.00 | 165000.00 | 315.00 | 157500.00 | 330.00 | 165000.00 | 294.00 | 147000.00 | 147000.00 | vardhman Airport solutions pvt. Ltd.
12.03 | (c)3.5Cx120 Sq mm | 1000.00 | Meter |  | 470.00 | 470000.00 | 475.00 | 475000.00 | 500.00 | 500000.00 | 510.00 | 510000.00 | 497.00 | 497000.00 | 451.00 | 451000.00 | 451000.00 | vardhman Airport solutions pvt. Ltd.
12.04 | (d )3.5Cx150 sq mm | 500.00 | Meter |  | 525.00 | 262500.00 | 558.00 | 279000.00 | 600.00 | 300000.00 | 490.00 | 245000.00 | 625.00 | 312500.00 | 530.00 | 265000.00 | 245000.00 | Awasthi Electric Works
12.05 | (e)3.5C X240Sq. mm | 1000.00 | Meter |  | 900.00 | 900000.00 | 905.00 | 905000.00 | 1000.00 | 1000000.00 | 875.00 | 875000.00 | 970.00 | 970000.00 | 861.00 | 861000.00 | 861000.00 | vardhman Airport solutions pvt. Ltd.
12.06 | (f)3.5C X 400Sq. mm | 900.00 | Meter |  | 1400.00 | 1260000.00 | 1415.00 | 1273500.00 | 1550.00 | 1395000.00 | 1375.00 | 1237500.00 | 1495.00 | 1345500.00 | 1346.00 | 1211400.00 | 1211400.00 | vardhman Airport solutions pvt. Ltd.
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipe as required.
13.01 | (a)Above 35 sq. mm and upto 95 sq. mm Aluminium | 250.00 | Meter |  | 100.00 | 25000.00 | 35.00 | 8750.00 | 45.00 | 11250.00 | 40.00 | 10000.00 | 50.00 | 12500.00 | 21.00 | 5250.00 | 5250.00 | vardhman Airport solutions pvt. Ltd.
13.02 | (b)Above 95 sq. mm and upto 185 sq. mm Aluminium | 200.00 | Meter |  | 100.00 | 20000.00 | 40.00 | 8000.00 | 65.00 | 13000.00 | 70.00 | 14000.00 | 60.00 | 12000.00 | 27.00 | 5400.00 | 5400.00 | vardhman Airport solutions pvt. Ltd.
13.03 | (c)Above 185 sq. mm and upto 400 sq. mm Aluminium | 200.00 | Meter |  | 100.00 | 20000.00 | 45.00 | 9000.00 | 95.00 | 19000.00 | 90.00 | 18000.00 | 60.00 | 12000.00 | 43.00 | 8600.00 | 8600.00 | vardhman Airport solutions pvt. Ltd.
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
14.01 | (a)Above 35 sq. mm and upto 95 sq. mm Aluminium | 200.00 | Meter |  | 50.00 | 10000.00 | 25.00 | 5000.00 | 45.00 | 9000.00 | 35.00 | 7000.00 | 50.00 | 10000.00 | 11.00 | 2200.00 | 2200.00 | vardhman Airport solutions pvt. Ltd.
14.02 | (b)Above 95 sq. mm and upto 185 sq. mm Aluminium | 300.00 | Meter |  | 50.00 | 15000.00 | 30.00 | 9000.00 | 65.00 | 19500.00 | 60.00 | 18000.00 | 60.00 | 18000.00 | 16.00 | 4800.00 | 4800.00 | vardhman Airport solutions pvt. Ltd.
14.03 | (c)Above 185 sq. mm and upto 400 sq. mm Aluminium | 1050.00 | Meter |  | 50.00 | 52500.00 | 35.00 | 36750.00 | 95.00 | 99750.00 | 80.00 | 84000.00 | 70.00 | 73500.00 | 16.00 | 16800.00 | 16800.00 | vardhman Airport solutions pvt. Ltd.
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
15.01 | (a) Above 35 sq. mm and upto 95 sq. mm (clamped with 25 X 3 mm MS flat clamp) Aluminium | 350.00 | Meter |  | 100.00 | 35000.00 | 55.00 | 19250.00 | 45.00 | 15750.00 | 125.00 | 43750.00 | 90.00 | 31500.00 | 32.00 | 11200.00 | 11200.00 | vardhman Airport solutions pvt. Ltd.
15.02 | (b)Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40 X 3 mm MS flat clamp) Aluminium | 200.00 | Meter |  | 150.00 | 30000.00 | 65.00 | 13000.00 | 65.00 | 13000.00 | 160.00 | 32000.00 | 125.00 | 25000.00 | 43.00 | 8600.00 | 8600.00 | vardhman Airport solutions pvt. Ltd.
15.03 | (c) Above 185 sq. mm and upto 400 sq. mm (clamped with 40 X 3 mm MS flat clamp) Aluminium | 280.00 | Meter |  | 200.00 | 56000.00 | 125.00 | 35000.00 | 95.00 | 26600.00 | 170.00 | 47600.00 | 210.00 | 58800.00 | 54.00 | 15120.00 | 15120.00 | vardhman Airport solutions pvt. Ltd.
16.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
16.01 | (a) Above 35 sq. mm and upto 95 sq. mm (clamped with 25 X 3 mm MS flat clamp) Aluminium | 580.00 | Meter |  | 100.00 | 58000.00 | 65.00 | 37700.00 | 45.00 | 26100.00 | 125.00 | 72500.00 | 90.00 | 52200.00 | 54.00 | 31320.00 | 26100.00 | RASS CONTRACTOR AND ENGINEERS
16.02 | (b)Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40 X 3 mm MS flat clamp) Aluminium | 600.00 | Meter |  | 150.00 | 90000.00 | 85.00 | 51000.00 | 65.00 | 39000.00 | 160.00 | 96000.00 | 125.00 | 75000.00 | 75.00 | 45000.00 | 39000.00 | RASS CONTRACTOR AND ENGINEERS
16.03 | (c) Above 185 sq. mm and upto 400 sq. mm (clamped with 40 X 3 mm MS flat clamp) Aluminium | 300.00 | Meter |  | 200.00 | 60000.00 | 125.00 | 37500.00 | 95.00 | 28500.00 | 170.00 | 51000.00 | 210.00 | 63000.00 | 86.00 | 25800.00 | 25800.00 | vardhman Airport solutions pvt. Ltd.
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
17.01 | (a)3.5Cx 50sq mm | 8.00 | Each |  | 200.00 | 1600.00 | 325.00 | 2600.00 | 550.00 | 4400.00 | 390.00 | 3120.00 | 600.00 | 4800.00 | 914.00 | 7312.00 | 1600.00 | GIRI ENTERPRISES
17.02 | (b)3.5Cx70 Sq mm | 8.00 | Each |  | 250.00 | 2000.00 | 375.00 | 3000.00 | 650.00 | 5200.00 | 450.00 | 3600.00 | 700.00 | 5600.00 | 1299.00 | 10392.00 | 2000.00 | GIRI ENTERPRISES
17.03 | (c)3.5Cx120 Sq mm | 8.00 | Each |  | 350.00 | 2800.00 | 450.00 | 3600.00 | 750.00 | 6000.00 | 560.00 | 4480.00 | 900.00 | 7200.00 | 1969.00 | 15752.00 | 2800.00 | GIRI ENTERPRISES
17.04 | (d)3.5Cx150 sq mm | 6.00 | Each |  | 400.00 | 2400.00 | 475.00 | 2850.00 | 950.00 | 5700.00 | 850.00 | 5100.00 | 900.00 | 5400.00 | 2215.00 | 13290.00 | 2400.00 | GIRI ENTERPRISES
17.05 | (e)3.5C X240Sq. mm | 6.00 | Each |  | 1200.00 | 7200.00 | 700.00 | 4200.00 | 1250.00 | 7500.00 | 1250.00 | 7500.00 | 1100.00 | 6600.00 | 3708.00 | 22248.00 | 4200.00 | Youngmen Traders
17.06 | (f)3.5C X 400Sq. mm | 4.00 | Each |  | 1500.00 | 6000.00 | 1100.00 | 4400.00 | 1450.00 | 5800.00 | 1900.00 | 7600.00 | 1400.00 | 5600.00 | 4807.00 | 19228.00 | 4400.00 | Youngmen Traders
| Total in Figures |  |  |  |  | 9659570.00 |  | 9563100.00 |  | 9194050.00 |  | 9860450.00 |  | 13767200.00 |  | 8994461.00
Lowest Amount Quoted BY: vardhman Airport solutions pvt. Ltd.(8994461.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 250KVA UPS with outgoing LT panel and Commercial LT panel at T-1 terminal BPI Airport, Bhubaneswar. Tender ID: 2024_AAI_191172_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | vardhman Airport solutions pvt. Ltd. | 8994461.00 | L1
| 2 | RASS CONTRACTOR AND ENGINEERS | 9194050.00 | L2
| 3 | Youngmen Traders | 9563100.00 | L3
| 4 | GIRI ENTERPRISES | 9659570.00 | L4
| 5 | Awasthi Electric Works | 9860450.00 | L5
| 6 | Manish Electricals | 13767200.00 | L6