## BoQ1
Government eProcurement System Created By: JANARDHAN SWAMY SADULA Created Date/Time: 24-Apr-2024 05:42 PM Tender Title: Augmentation of AirConditioning System at ATS Complex and NAVAIDS by Replacing AHUs Phase II and Split ACs at Southern Region Chennai Airport Tender ID: 2024_AAI_192006_1
Tender Inviting Authority: Sr. Manager (Engg-Elect),ED-II, AAI, RHQ, Southern Region,Chennai Airport, Chennai-600 016.
Name of Work: Augmentation of Air conditioning system at ATS Complex and NAVAIDS by replacing AHUs (Phase-II) and Split Acs a Chennai Airport, Southern Region, Chennai.
E-Tender Id: 2024_AAI_192006_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLTAS LIMITED (GSTN-33AAACV2809DIZT) BID ID -694345 |  | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED (GSTN-33AABCG0898A1Z0) BID ID -694889 |  | Bluestar Limited(GSTN-NA)--691391
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: AHU RELATED WORKS:
1.01 | Supply, Installation, Testing and Commissioning of factory built floor mounted chilled water double skin type Air Handling Units (AHUs) made out of 25mm thick panels consisting pre coated G.I casing of thickness 0.8mm outside layer and 0.8mm inside layer with polyurethene foam (PUF) insulation having 38 kg/cu.M density, factory injected between them by injection moulding machine, complete with blower section with Backward curve blower, blower suitable for static pressure as detailed below, UVGI lamps between cooling coil and drift eliminators with necessary door limit switch ON/OFF control, PVC drift eliminators, Four row deep cooling coil with 0.15mm thick hydrophilic coated aluminium fins, copper tubes having min 0.5mm wall thickness & 12.5mm dia, filter sections with 50mm thick metal viscous /washable synthetic type MERV8 air pre-filters having 90% efficiency down to 10 Microns, drain connections, 18G thick stainless steel 304 grade drain pan with PUF / Nitrile rubber insulation, LED lights in each section of AHU with door switch control, belt drive package with TEFC drive motor of efficiency class IE4 suitable for 3 phase, 415 ± 10% volts, 50Hz, AC Supply, suitably designed for variable frequency drive applications, PCC cubicals to position the base frame of AHUs, necessary vibration isolation arrangement etc., including Installation, Testing and Commissioning of AHUs as detailed below: a) Necessary modification in the existing GI ducting to made suit the mouth connection with the new AHU including supply & fixing of necessary thermal & acoustic insulation as required. b) Necessary modification in the existing MS Chilled water pipeline including supply, fabrication of NEW MS 'C' class pipes of required size and length between cooling coil of AHU Inlet / AHU Outlet and butterfly valves of the AHU, supply & fixing of 2 Nos. drain valves (25mm ball valve) in chilled water pipes, supports, insulation with PUF sections, vapour barrier, GI wire mesh, sand cement plastering, approved coloring, etc as required. c) Necessary modification in the existing drain water piping for trouble free draining of condensate water including fabricating, supplying, fixing a removable 'U' trap having both side flanges with bolt nut arrangement (easy removal for cleaning), thermal insulation, sand cement plastering, coloring at the drain outlet of AHU. d) Termination of existing power cable, earth wires, control cables, Fire panel cable, Remote control cables for remote ON & OFF of AHU from remote location, etc. (with new starter panel) complete as per specifications and of following capacities:
1.02 | a) 10 TR Capacity, 5,600 CFM, 9,515 CMH b) K.Calorie per hour-30,000 c) Static pressure -75mmWC d) Quantity of Blower - 1 No. e) Location: Ground floor, 1st floor & 2nd floor | 3.00 | Job |  | 274198.00 | 822594.00 | 210000.00 | 630000.00 | 247372.00 | 742116.00 | 630000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
1.03 | a) 15 TR Capacity, 8,240 CFM, 14,000 CMH b) K.Calorie per hour-45,000 c) Static pressure -75mmWC d) Quantity of Blower - 1 No. e) Location: 1st floor, 2nd floor & 3rd floor | 4.00 | Job |  | 352033.00 | 1408132.00 | 270000.00 | 1080000.00 | 321079.00 | 1284316.00 | 1080000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
1.04 | a) 20 TR Capacity, 10,900 CFM, 18,500 CMH b) K.Calorie per hour-60,000 c) Static pressure -75mmWC d) Quantity of Blower - 1 No. e) Location: Ground floor & 1st floor | 4.00 | Job |  | 448597.00 | 1794388.00 | 340000.00 | 1360000.00 | 379213.00 | 1516852.00 | 1360000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
1.05 | a) 30 TR Capacity, 16,800 CFM, 28,544 CMH b) K.Calorie per hour-90,000 c) Static pressure -55mmWC d) Quantity of Blower - 1 No. e) Location: Ground floor | 1.00 | Job |  | 674692.00 | 674692.00 | 510000.00 | 510000.00 | 529828.00 | 529828.00 | 510000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
2.00 | Supply, Installation, Testing and Commissioning of Variable Frequency Drive Starter panels with Star-Delta bypass facility in the AHU room, made out of 2mm thick CRCA sheet duly powder coated as per specifications. The panel shall have hinged door with ON-OFF interlocks. The panel shall be complete with incoming MCCB, suitable connections, LED indication lamps, Auto Manual selector switch, remote start / stop contactors, relays, Auxiliary contactors, Digital Ammeter with selector switch, Digital Voltmeter with selector switch, necessary provision for Fire Damper controls & BMS controls, providing connectors for power and control cables, earthing connectors, printed wiring diagram of starter panel, etc. as required complete as per specifications for following capacity AHUs.
2.01 | 10 TR Capacity AHU at Ground floor, 1st floor & 2nd floor | 3.00 | Job |  | 53447.00 | 160341.00 | 80000.00 | 240000.00 | 51586.00 | 154758.00 | 154758.00 | Bluestar Limited
2.02 | 15 TR Capacity AHU at 1st floor, 2nd floor & 3rd floor | 4.00 | Job |  | 56789.00 | 227156.00 | 100000.00 | 400000.00 | 58735.00 | 234940.00 | 227156.00 | VOLTAS LIMITED
2.03 | 20 TR Capacity AHU at Ground floor & 1st floor. | 4.00 | Job |  | 73436.00 | 293744.00 | 130000.00 | 520000.00 | 75460.00 | 301840.00 | 293744.00 | VOLTAS LIMITED
2.04 | 30 TR Capacity AHU at Ground floor. | 1.00 | Job |  | 75796.90 | 75796.90 | 150000.00 | 150000.00 | 77466.00 | 77466.00 | 75796.90 | VOLTAS LIMITED
3.00 | Supply & fixing of MERV-13 air filter, washable type suitable to fix in flanges having size of 550mm x 550mm within existing supply air plenum of AHU rooms with necessary fixing arrangements like clamps, bolt, nut, washer etc complete as required. | 50.00 | Nos. |  | 2137.00 | 106850.00 | 4100.00 | 205000.00 | 4999.00 | 249950.00 | 106850.00 | VOLTAS LIMITED
4.00 | Supply and Fixing of following size butterfly valves wafer type with matching flanges, bolt, nuts, insulation, etc after cutting in the existing chilled water header pipes of AHU rooms including removal of existing insulation, providing one set of individual Tools, Men & Matrials for every two numbers butterfly valves at a time (i.e Five set of tools, men & materials for Ten butterfly valves at a time to minimise the down time of Air conditioning), etc complete as required.
4.01 | 100 mm dia | 4.00 | Job |  | 8707.70 | 34830.80 | 3600.00 | 14400.00 | 10348.00 | 41392.00 | 14400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
4.02 | 80 mm dia | 6.00 | Job |  | 6811.20 | 40867.20 | 2700.00 | 16200.00 | 9227.00 | 55362.00 | 16200.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
5.00 | Supply and Fixing of following size butterfly valve wafer type with matching flanges, bolt, nuts, insulation, etc after cutting in the existing supply & return chilled water pipes of AHUs including welding and removal of existing insulation etc complete as required.
5.01 | 80 mm dia | 2.00 | Job |  | 6811.20 | 13622.40 | 2700.00 | 5400.00 | 5217.00 | 10434.00 | 5400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
5.02 | 65 mm dia | 14.00 | Job |  | 6156.80 | 86195.20 | 2500.00 | 35000.00 | 4344.00 | 60816.00 | 35000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
5.03 | 50 mm dia | 6.00 | Job |  | 5450.30 | 32701.80 | 2300.00 | 13800.00 | 3763.00 | 22578.00 | 13800.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
6.00 | Supply and Fixing of following size balancing valve with matching flanges, bolt, nuts, insulation, etc after cutting in the existing supply & return chilled water pipes of AHUs including welding and removal of existing insulation etc complete as required.
6.01 | 80 mm dia | 9.00 | Job |  | 15563.50 | 140071.50 | 11600.00 | 104400.00 | 13296.00 | 119664.00 | 104400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
6.02 | 65 mm dia | 8.00 | Job |  | 13638.10 | 109104.80 | 10200.00 | 81600.00 | 10994.00 | 87952.00 | 81600.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
6.03 | 50 mm dia | 3.00 | Job |  | 12356.70 | 37070.10 | 9400.00 | 28200.00 | 9546.00 | 28638.00 | 28200.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
7.00 | Supply and Fixing of following size MS " Y" Strainer with matching flanges, bolt, nuts, insulation, etc after cutting in the existing supply & return chilled water pipes of AHUs including welding and removal of existing insulation etc complete as required.
7.01 | 80 mm dia | 1.00 | Job |  | 8826.70 | 8826.70 | 4300.00 | 4300.00 | 6450.00 | 6450.00 | 4300.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
7.02 | 65 mm dia | 8.00 | Job |  | 7504.40 | 60035.20 | 3500.00 | 28000.00 | 5572.00 | 44576.00 | 28000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
7.03 | 50 mm dia | 3.00 | Job |  | 6390.20 | 19170.60 | 2800.00 | 8400.00 | 4729.00 | 14187.00 | 8400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
8.00 | Supply, Installation, Testing and Commissioning of following size 3-way Modulating valve with actuator, matching flanges, bolts, nuts, insulation, Thermostat with temperature adjustment, necessary wiring for normal working, etc complete as required.
8.01 | 80 mm dia | 1.00 | Job |  | 32739.10 | 32739.10 | 41000.00 | 41000.00 | 54600.00 | 54600.00 | 32739.10 | VOLTAS LIMITED
8.02 | 65 mm dia | 8.00 | Job |  | 27384.90 | 219079.20 | 33000.00 | 264000.00 | 44703.00 | 357624.00 | 219079.20 | VOLTAS LIMITED
8.03 | 50 mm dia | 3.00 | Job |  | 20909.10 | 62727.30 | 27000.00 | 81000.00 | 33624.00 | 100872.00 | 62727.30 | VOLTAS LIMITED
9.00 | Supply and Fixing of 25 mm ball valve with MS pipe nipple for AHU Chilled water Header lines including welding etc complete as required. | 24.00 | Jobs |  | 2007.10 | 48170.40 | 1800.00 | 43200.00 | 1149.00 | 27576.00 | 27576.00 | Bluestar Limited
10.00 | Suply and Fixing of digital type Thermometer with adopter for AHU chilled water line including welding etc complete as required. | 24.00 | Job |  | 2402.00 | 57648.00 | 2100.00 | 50400.00 | 2740.00 | 65760.00 | 50400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
11.00 | Supply and Fixing of dial type Pressure gauges of 150mm dia for AHUs including forged ball valves and pipe stem, welding etc. complete as required. | 24.00 | Job |  | 2361.30 | 56671.20 | 2700.00 | 64800.00 | 1671.00 | 40104.00 | 40104.00 | Bluestar Limited
12.00 | Supply and Fixing of Canvass Connection between AHU & Duct made of fire retardant type cloth of required size with suitable fixing arrangement etc complete as required. | 12.00 | Job |  | 3541.90 | 42502.80 | 3400.00 | 40800.00 | 3875.00 | 46500.00 | 40800.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
13.00 | Supply & fixing of extruded aluminium powder coated fresh air grills without collar dampers with necessary fixing arrangements like clamps, screws, washer etc. | 4.00 | Sqm |  | 6658.80 | 26635.20 | 10500.00 | 42000.00 | 7127.00 | 28508.00 | 26635.20 | VOLTAS LIMITED
14.00 | Supply, Installation, Testing and Commissioning of Opposed blade G.I Construction box type factory fabricated duct Volume Control Damper made of 18 SWG thick GI Sheet complete with nuts, bolts, screw, linkage, flanges, duct lever and quadrants etc complete as required. | 6.00 | Sqm |  | 10484.10 | 62904.60 | 10500.00 | 63000.00 | 11320.00 | 67920.00 | 62904.60 | VOLTAS LIMITED
15.00 | Dismantling the existing Air Handling Units (AHUs) of following capacity from different floors of Air Traffic Service (ATS) Complex i/c motor, blower, cooling coil, electrical panel, complete UVGI system, Chilled water pipelines at Inlet & Outlet of AHUs upto 3-way mixing valve, etc with all associated accessories and handing over of all dismantled items to AAI stores, including transportation, loading & unloading etc. complete as required.
15.01 | 4.95 TR capacity | 2.00 | Job |  | 10035.40 | 20070.80 | 5000.00 | 10000.00 | 3341.00 | 6682.00 | 6682.00 | Bluestar Limited
15.02 | 6.75 TR capacity | 1.00 | Job |  | 10035.40 | 10035.40 | 5000.00 | 5000.00 | 3341.00 | 3341.00 | 3341.00 | Bluestar Limited
15.03 | 9.27 TR capacity | 1.00 | Job |  | 10035.40 | 10035.40 | 7000.00 | 7000.00 | 4009.00 | 4009.00 | 4009.00 | Bluestar Limited
15.04 | 13.81 TR capacity | 4.00 | Job |  | 12396.70 | 49586.80 | 7000.00 | 28000.00 | 4009.00 | 16036.00 | 16036.00 | Bluestar Limited
15.05 | 18 TR capacity | 4.00 | Job |  | 14758.00 | 59032.00 | 10000.00 | 40000.00 | 6682.00 | 26728.00 | 26728.00 | Bluestar Limited
15.06 | 25.80 TR capacity | 1.00 | Job |  | 15938.60 | 15938.60 | 10000.00 | 10000.00 | 8018.00 | 8018.00 | 8018.00 | Bluestar Limited
16.00 | SH:II FRESH AIR VENTILATION SYSTEM
17.00 | Supply, installation, balancing and commissioning of GSS sheet metal rectangular/round ducting (fabricated at site) as per IS 655-2006 complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
17.01 | 0.63 mm thick | 75.00 | Sqm |  | 944.50 | 70837.50 | 1000.00 | 75000.00 | 1456.00 | 109200.00 | 70837.50 | VOLTAS LIMITED
17.02 | 0.80 mm thick | 25.00 | Sqm |  | 1121.60 | 28040.00 | 1100.00 | 27500.00 | 1624.00 | 40600.00 | 27500.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
18.00 | Supply, Installation, Testing and Commissioning of following capacity ceiling suspended type axial flow fan complete with suitable capacity AC 3 Phase induction motor, DOL Starter Panel having protections for single phasing, phase reversal, overload, short circuit etc with auto restart facility during power failure, Electrical terminal box at outside of fan, dry pre-filter, volume control damper, suspension arrangement made of GI threaded rod / angle iron, vibration arresters, electrical termination, earth connections, etc as reqd.
18.01 | 3000 CFM, 25mmWC Static pressure | 4.00 | set |  | 52714.20 | 210856.80 | 110000.00 | 440000.00 | 60035.00 | 240140.00 | 210856.80 | VOLTAS LIMITED
18.02 | 1500 CFM, 25mmWC Static pressure | 2.00 | set |  | 48845.60 | 97691.20 | 66000.00 | 132000.00 | 53753.00 | 107506.00 | 97691.20 | VOLTAS LIMITED
19.00 | Supply, Installation, Testing and Commissioning of 24G thick GI cowl and bugmesh shall be fixed to the discharge side of the fans at variuos levels of building with necessary supporting arrangenents, fasteners, etc complete as reqd.
19.01 | GI Cowl | 10.00 | Sqm |  | 2951.60 | 29516.00 | 1100.00 | 11000.00 | 1203.00 | 12030.00 | 11000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
19.02 | GI Bug mesh | 3.00 | Sqm |  | 1771.00 | 5313.00 | 1100.00 | 3300.00 | 1203.00 | 3609.00 | 3300.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
20.00 | Supply, Installation, Testing and Commissioning of GI back draft damper with suitable links shall be fixed to the discharge side of the fans with necessary supporting arrangenents, fasteners, etc complete as reqd. | 3.00 | Sqm |  | 10271.50 | 30814.50 | 11000.00 | 33000.00 | 11320.00 | 33960.00 | 30814.50 | VOLTAS LIMITED
21.00 | Dismantling the existing fresh air ventilation system from following locations i/c tube axial fans, Ducts, supports, VCDs, End cowl, etc. complete with all associated accessories and handing over of all dismantled items to AAI stores, including transportation, loading & unloading etc complete as required. i. Ground floor air side AHU room - 1 set ii. First floor air side AHU room - 1 set iii. Second floor air side AHU room - 1 set iv. Third floor air side AHU room - 1 set v. Third floor city side AHU room - 1 set | 1.00 | Job |  | 16528.90 | 16528.90 | 50000.00 | 50000.00 | 23712.00 | 23712.00 | 16528.90 | VOLTAS LIMITED
22.00 | SH-III: SITC OF UNITARY AIR CONDITIONERS:
23.00 | Supply, Installation, Testing and Commissioning of 4 TR capacity Floor standing tower type Split AC unit, fitted with hermetically sealed compressor operating on 415 V +10% 50 Hz 3 phase AC supply with evaporator and condensing unit made of copper tubes with aluminium fins i/c cordless remote control, Angle iron floor stand for indoor unit, angle iron wall / floor stand for condensing unit, etc complete as required. | 11.00 | Nos |  | 101931.50 | 1121246.50 | 110000.00 | 1210000.00 | 94365.00 | 1038015.00 | 1038015.00 | Bluestar Limited
24.00 | Supply, Installation, Testing and Commissioning of 2 TR capacity wall mounted type Split AC unit, 5 star rated, invertor type, fitted with hermetically sealed compressor operating on 220 V +10% 50 Hz Single phase AC supply with evaporator and condensing unit made of copper tubes with aluminium fins i/c cordless remote control, copper piping for both suction and discharge of 3 metres standard length alongwith power & control cables and thermal insulation, angle iron wall / floor stand for condensing unit, etc complete as per specifications complete as required | 14.00 | Nos |  | 40889.10 | 572447.40 | 47000.00 | 658000.00 | 46956.00 | 657384.00 | 572447.40 | VOLTAS LIMITED
25.00 | Supply, Installation, Testing and Commissioning of 1.5 TR capacity wall mounted type Split AC unit, 5 star rated, invertor type, fitted with hermetically sealed compressor operating on 220 V +10% 50 Hz Single phase AC supply with evaporator and condensing unit made of copper tubes with aluminium fins i/c cordless remote control, copper piping for both suction and discharge of 3 metres standard length alongwith power & control cables and thermal insulation, angle iron wall / floor stand for condensing unit, etc complete as per specifications complete as required | 33.00 | Nos |  | 29933.70 | 987812.10 | 44000.00 | 1452000.00 | 38012.00 | 1254396.00 | 987812.10 | VOLTAS LIMITED
26.00 | Supply and Installation of Copper pipe for the following capacity Air conditioners including suction and delivery copper pipes with all accessories such as insulation, power & control cabling, etc. as per specifications complete as required
26.01 | For 4 TR floor standing tower type Air conditioner | 100.00 | Metre |  | 1121.60 | 112160.00 | 1600.00 | 160000.00 | 969.00 | 96900.00 | 96900.00 | Bluestar Limited
26.02 | For 2 TR Split Air conditioner (beyond 3 meters per Split AC unit) | 45.00 | Metre |  | 1044.90 | 47020.50 | 1000.00 | 45000.00 | 831.00 | 37395.00 | 37395.00 | Bluestar Limited
26.03 | For 1.5 TR Split Air conditioner (beyond 3 meters per Split AC unit) | 50.00 | Metre |  | 938.60 | 46930.00 | 1000.00 | 50000.00 | 761.00 | 38050.00 | 38050.00 | Bluestar Limited
27.00 | SITC of following capacity voltage stabilisers with copper wound coil having range of 170 to 270 voltage single phase, 50 Hz AC supply i/c necessary fixing arrangements, clamps, screws, metal clad top, connecting 3 core cable of 1 metre length, complete, etc as per specifications complete as required.
27.01 | 5 KVA stabilizer for 2 TR Spilt AC | 14.00 | Job |  | 2579.70 | 36115.80 | 4000.00 | 56000.00 | 1738.00 | 24332.00 | 24332.00 | Bluestar Limited
27.02 | 4 KVA stabilizer for 1.5 TR Spilt AC | 33.00 | Jobs |  | 1727.30 | 57000.90 | 3700.00 | 122100.00 | 1604.00 | 52932.00 | 52932.00 | Bluestar Limited
28.00 | Supplying & laying of condensate water drain pipe made of PVC having size of 40mm dia, 6kg/cm capacity, for additional requirement for AC units i/c necessary clamps, screws, supports, etc as per specifications complete as required | 175.00 | Metre |  | 141.70 | 24797.50 | 210.00 | 36750.00 | 388.00 | 67900.00 | 24797.50 | VOLTAS LIMITED
29.00 | Supply and fixing of following rated Cyclic timer for Split / Tower type air conditioners, suitable for cycle the air conditioners between duty and standby units at predetermined intervals that are suitable between 1 to 12 hours, with necessary buttons, display, inbuilt power and control contactors, control circuits, terminals, etc., as per specifications complete as required.
29.01 | Cyclic timer for split AC having 2 TR capacity, AC single phase power supply. Similar to Model no. A-MCT-02, make of Presevi Industries Pvt Ltd. | 17.00 | Job |  | 6434.50 | 109386.50 | 6500.00 | 110500.00 | 8039.00 | 136663.00 | 109386.50 | VOLTAS LIMITED
29.02 | Cyclic timer for split AC (Floor standing, Tower typer) having 4 TR capacity, AC, 3 Phase power supply. Similar to Model No. A -MCT-02-AM, make of Presevi Industries Pvt ltd. | 5.00 | Job |  | 6434.50 | 32172.50 | 8500.00 | 42500.00 | 8039.00 | 40195.00 | 32172.50 | VOLTAS LIMITED
30.00 | Dismantling and shifting of following capacity Indoor and outdoor units to AAI store /any location specified by AAI, including gas pumping down, pipes, cables, etc.,complete as required.
30.01 | 1.5 TR capacity split AC | 32.00 | Nos |  | 1180.60 | 37779.20 | 500.00 | 16000.00 | 1336.00 | 42752.00 | 16000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
30.02 | 2.0 TR capacity split AC | 14.00 | Nos |  | 1180.60 | 16528.40 | 600.00 | 8400.00 | 1336.00 | 18704.00 | 8400.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
30.03 | 3.0 TR capacity split AC | 11.00 | Nos |  | 2125.10 | 23376.10 | 700.00 | 7700.00 | 3341.00 | 36751.00 | 7700.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
31.00 | SH-IV: ELECTRICAL WORKS:
32.00 | Supply of following size XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (PART-l) with upto date amendments etc as required.
32.01 | 4C x 10 sq.mm | 200.00 | Metre |  | 107.70 | 21540.00 | 200.00 | 40000.00 | 158.00 | 31600.00 | 21540.00 | VOLTAS LIMITED
32.02 | 4C x 16 sq.mm | 350.00 | Metre |  | 130.10 | 45535.00 | 240.00 | 84000.00 | 191.00 | 66850.00 | 45535.00 | VOLTAS LIMITED
33.00 | Laying and fixing of one number XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade of size upto 35 sq.mm on wall surface including suitable size clamping as per CPWD specification etc as required. | 150.00 | Metre |  | 79.70 | 11955.00 | 120.00 | 18000.00 | 67.00 | 10050.00 | 10050.00 | Bluestar Limited
34.00 | Laying and fixing of one number XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade of size upto 35 Sqmm size on cable tray including suitable size clamping as per CPWD specification etc as required. | 400.00 | Metre |  | 74.40 | 29760.00 | 120.00 | 48000.00 | 67.00 | 26800.00 | 26800.00 | Bluestar Limited
35.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade etc as required.
35.01 | 4 X 10 Sq.mm (25 mm) | 12.00 | Job |  | 510.00 | 6120.00 | 180.00 | 2160.00 | 329.00 | 3948.00 | 2160.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
35.02 | 4 X 16 Sq.mm (28 mm) | 24.00 | Job |  | 573.80 | 13771.20 | 210.00 | 5040.00 | 393.00 | 9432.00 | 5040.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
35.03 | 4 X 25 Sq.mm (28 mm) | 6.00 | Job |  | 616.30 | 3697.80 | 320.00 | 1920.00 | 468.00 | 2808.00 | 1920.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
36.00 | Providing and fixing 6 SWG dia G.I wire on surface or in recess for loop earthing etc as reqired. | 1100.00 | Metre |  | 44.60 | 49060.00 | 150.00 | 165000.00 | 121.00 | 133100.00 | 49060.00 | VOLTAS LIMITED
37.00 | Supply, Installation, Testing and Commissioning of 16/20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB in sheet steel enclosure, with chained metal cover for the socket outlet and complete with connections, etc. as required. | 47.00 | Nos |  | 2759.70 | 129705.90 | 4500.00 | 211500.00 | 2072.00 | 97384.00 | 97384.00 | Bluestar Limited
38.00 | Supply, Installation, Testing and Commissioning of 25/32 A "C" curve, 4 pole, MCB in sheet steel enclosure, complete with connections, etc. as required. | 11.00 | Nos |  | 3211.30 | 35324.30 | 5500.00 | 60500.00 | 2339.00 | 25729.00 | 25729.00 | Bluestar Limited
39.00 | SH-V Buyback of AHUs, Split Acs & Ventilation System
40.00 | Buyback of following capacity dismanled Air Handling Units, Split AC units and ventilation system of following capacity from different floors of Air Traffic Service (ATS) Complex on "As Is Where Is" Basis. (a) AHU consist of Motor, blower, cooling coil, all sheet steel panels, Air filters, electrical starter panel, Chiller water pipilines at Intel & Outlet of AHUs upto and including IN & OUT valves, 3-way mixing valve, Balancing valve, Volume control damper, etc (b) Split AC consist of Indoor & outdoor units and associated copper tubes etc (c) Fresh Air Ventilation System consist of axial flow fans, starter, duct, VCD etc
40.01 | Air Handling units and associated installations
40.02 | 4.95 TR, 3000 CFM capacity - 2 Set
40.03 | 6.75 TR, 5000 CFM capacity - 1 Set
40.04 | 9.27 TR, 5600 CFM capacity - 1 Set
40.05 | 13.81 TR, 8300 CFM capacity - 4 Set
40.06 | 18 TR, 10800 CFM capacity - 4 Set
40.07 | 25.80 TR, 15500 CFM capacity - 1 Set
40.08 | Split/Tower type Air-conditioners
40.09 | 1.5 TR capacity split AC - 31 Set
40.10 | 2.0 TR capacity split AC - 15 Set
40.11 | 3.0 TR capacity split AC - 11 Set
40.12 | Ventilation system
40.13 | Ground floor air side AHU room - 1 Set
40.14 | First Floor air side AHU room - 1 Set
40.15 | Second floor air side AHU room - 1 set
40.16 | Third floor air side AHU room - 1 set
40.17 | Third floor city side AHU room - 1 Set
40.18 | All the above from 40.00 to 40.17 | 1.00 | LOT |  | 233051.00 | -233051.00 | 1000000.00 | -1000000.00 | 561294.00 | -561294.00 | -1000000.00 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 10747756.50 |  | 10607770.00 |  | 10397926.00
Lowest Amount Quoted BY: Bluestar Limited(10397926.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of AirConditioning System at ATS Complex and NAVAIDS by Replacing AHUs Phase II and Split ACs at Southern Region Chennai Airport Tender ID: 2024_AAI_192006_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Bluestar Limited | 10397926.00 | L1
| 2 | GEMINI COOLING SYSTEMS PROJECTS PRIVATE LIMITED | 10607770.00 | L2
| 3 | VOLTAS LIMITED | 10747756.50 | L3