## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 10-Jun-2024 05:29 PM Tender Title: SITC of 750 KVA DG Set at SGRDJI Airport Amritsar Tender ID: 2024_AAI_192997_1
Tender Inviting Authority: <Asstt. GM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <SITC of 750 KVA DG Set at SGRDJI Airport, Amritsar.>
Tender ID: <2024_AAI_192997_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -698436 |  | Mona Generator Services Pvt. Ltd. (GSTN-07AAFCM4263P1ZZ) BID ID -698546 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -698599 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -698632 |  | VIJAYPOWER GENERATORS LIMITED (GSTN-07AAACV0191N1Z4) BID ID -698639 |  | Shiva Enterprises(GSTN-NA)--698614 |  | Edge Telecom Pvt Ltd(GSTN-NA)--698475 |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)--698439
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Providing, Installing, Testing & Commissioning of 'silent type' diesel generating with Latest G3 governing, remote monitoring capability on laptop/ mobile and having prime power rating of 750 KVA/600 KW at 0.8 lagging p.f., 415 volts, 50 HZ at 1500 RPM, 3 phase power supply system & for 0.85 load factor design including necessary einforcement(RCC) foundation as per manufacurer recommendation and DG should be consisting of the following: a) Diesel Engine, 4 stroke, Radiator cooled, electric start, of suitable BHP at 1500 RPM, suitable for generating above electrical output from alternator at 40 dgree C, 50% RH & at 1000 meter altitude above MSL and confirming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for 1 hour after every 12 hours of continuos operation at variable load. The engine will be fitted complete with all the required accessories. b) Engine mounted instrument panel having digital display and having following features: l) Start - Stop switch, Il) Water temperature indication, Ill) Lubrication oil pressure indication, IV Battery charging indication, V) RPM indication, Vl) Over speed indication, VIl) Low fuel Oil level alarm indication, IX) Engine running hours indication c) Alternator: Synchronous alternator rated at 750 KVA, 415 Volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 degree C, 50% RH & at 1000 meter altitude above MSL. The alternator shall be having SPDP enclosure, brushless, continues duty self-excited and self-regulated through AVR confirming to IS : 4722/BS 2613 suitable for tropical conditions and with class-H insulation. d) Base frame : Both engine and alternator shall be mounted on suitable base frame made of MS channel and vibration isolation arrangement as per recommendations of manufacturer. e) Fuel Tank: Daily service inbuilt fuel tank of 990 liters capacity, fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. f) Exhaust System : Dry exhaust mainfold with hospital/residential type exhaust silencer meeting latest CPCB norms (CPCB IV+) and MOEF guidelines for noise level. g) Starting system: 12 V /24 V DC starting system comprising of starter motors voltage regulator and arrangement of initial excitation complete with suitable no. of batteries (25 plates, 180 Amp, hour capacity lead acid type) as required as per specification. h) Acoustic and weather proof enclosure with arrangement of fresh air intake for engine breathing and for cooling of engine and alternater and hot air extraction/ discharging system as per specification. NOTE:The New DG need to be integrated and synchornized in parallel with Existing 2 no 750 KVA Kirloskar make DGs (Model No. KG1 - 750WS) along with integration in Existing SYNC Panel complete as required. Cost of integration / synchronization is included in this item. | 1.00 | Job |  | 7400000.00 | 7400000.00 | 8000100.00 | 8000100.00 | 12178600.00 | 12178600.00 | 8465000.00 | 8465000.00 | 7736983.00 | 7736983.00 | 7450000.00 | 7450000.00 | 6400000.00 | 6400000.00 | 9500000.00 | 9500000.00 | 6400000.00 | Edge Telecom Pvt Ltd
2.00 | SITC of following Circuit Breakers, metering and instruments in the existing spare cabinet of sync panel along with all connections of control wiring , contactors and timers, changes/ addition of Busbar, channel, insulators, hardware, sleeves etc and integration with existing PLC based control system for operation of all existing functions complete in all respect 01 No. INCOMER: 1250A EDO ACB TP 50 k, Ics = 100% Icu, microprocessor based with inbuilt Rs. 485 Communication port etc - 02 sets (with NIC contrator of 300A TP ac3 rating). 01 No BUS COUPLER: 2500A EDO ACB, FP, 50 kA, Ics = 100% Icu, microprocessor based, with inbuilt Rs. 485 Communication port etc. METERING & INSTRUMENTS: Incomer having digital MFM - vaf, pf with phase and on, off, trip indication of ACB, on indication of NIC.Suitable range and required number of components/ accessories for proper operation of Auto Mains Failure cum Auto Synchronization with auto load sharing facilities including 01 No. synchronizing controller,, , 01 nos. earth fault relay, 01 nos. engine cranking relay, 01 nos. voltage monitoring relay, 01 nos. automatic battery charger, LED type indicating lamps, CTs, PTs, digital DC ammeters & voltmeters, alarm annouciator, hooters, auxilary contractors and relays, local push buttons, emergency push button, selector switches etc as per Incomer and Buscoupler requirement. All equpiments should be compatible and complete as per existing incomer and bus coupler complete as required. Note: The New Air Circuit Breakers in sync panel need to be integrated in Existing panel having L&T make ACBs (Model No. Omega series) and PLC complete as required. | 1.00 | Job |  | 950000.00 | 950000.00 | 1650000.00 | 1650000.00 | 925000.00 | 925000.00 | 1865000.00 | 1865000.00 | 1200000.00 | 1200000.00 | 970000.00 | 970000.00 | 1200000.00 | 1200000.00 | 600000.00 | 600000.00 | 600000.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply, installation, testing & commissioning of MS class-B exhaust pipe and all fixing accessories and hardwares. The exhaust pipes shall be insulated with 75 mm thick mineral wool (density 150 kg/m3) insulation wrapped in chicken mesh and clad with 26 gauge aluminium sheet including all hot dip galvanized/MS support structure, as required.
3.10 | 300/350 mm dia MS class B Pipe and 75 mm thick mineral wool insulation as per description given above. | 25.00 | Mtr |  | 10000.00 | 250000.00 | 52800.00 | 1320000.00 | 3500.00 | 87500.00 | 6300.00 | 157500.00 | 7500.00 | 187500.00 | 9690.00 | 242250.00 | 18500.00 | 462500.00 | 3250.00 | 81250.00 | 81250.00 | JCC ENGINEERS PRIVATE LIMITED
3.20 | 180 mm dia MS class-B pipe & 75mm thick mineral wool insulation as per description given above. | 10.00 | Mtr |  | 7000.00 | 70000.00 | 33000.00 | 330000.00 | 3200.00 | 32000.00 | 4500.00 | 45000.00 | 5000.00 | 50000.00 | 7140.00 | 71400.00 | 9500.00 | 95000.00 | 3550.00 | 35500.00 | 32000.00 | Manish Electricals
4.00 | Supply & fixing of self supporting MS structure suitable for following DG sets complete. This structure shall be designed for a wind velocity prevailing at site & soil bearing capacity provided by you. | 1000.00 | Kgs |  | 124.00 | 124000.00 | 300.00 | 300000.00 | 125.00 | 125000.00 | 145.00 | 145000.00 | 145.00 | 145000.00 | 170.00 | 170000.00 | 250.00 | 250000.00 | 130.00 | 130000.00 | 124000.00 | DOSHI ELECTRIC ENGG. CO.
5.00 | SS Bellows 300/350 mm. | 2.00 | EA |  | 18000.00 | 36000.00 | 120000.00 | 240000.00 | 21000.00 | 42000.00 | 20000.00 | 40000.00 | 12000.00 | 24000.00 | 20000.00 | 40000.00 | 22000.00 | 44000.00 | 7000.00 | 14000.00 | 14000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supplying, installing by suspension on ceiling/along the wall, testing and commissioning of following capacity Sandwich Type Rising Mains for use on 3 phase 4 wire 415 V, 50Hz A.C. supply with metal clad enclosure having IP-65/IP 66 with canopy rating after fixing the tap off boxes and all accessories, made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars having current density of 130 Al sq. em at nominal current rating, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every meter, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.l. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required. 1600 A (Isc=50 kA for 1 second) | 25.00 | Mtr |  | 29000.00 | 725000.00 | 44000.00 | 1100000.00 | 29500.00 | 737500.00 | 62000.00 | 1550000.00 | 36000.00 | 900000.00 | 51800.00 | 1295000.00 | 22000.00 | 550000.00 | 50000.00 | 1250000.00 | 550000.00 | Edge Telecom Pvt Ltd
7.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | EA |  | 7000.00 | 14000.00 | 11250.00 | 22500.00 | 8000.00 | 16000.00 | 9500.00 | 19000.00 | 9000.00 | 18000.00 | 11100.00 | 22200.00 | 8500.00 | 17000.00 | 6000.00 | 12000.00 | 12000.00 | JCC ENGINEERS PRIVATE LIMITED
8.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | EA |  | 15000.00 | 30000.00 | 19250.00 | 38500.00 | 18500.00 | 37000.00 | 16000.00 | 32000.00 | 27000.00 | 54000.00 | 22500.00 | 45000.00 | 18000.00 | 36000.00 | 15000.00 | 30000.00 | 30000.00 | DOSHI ELECTRIC ENGG. CO., JCC ENGINEERS PRIVATE LIMITED
9.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 15.00 | Mtr |  | 1200.00 | 18000.00 | 1800.00 | 27000.00 | 1200.00 | 18000.00 | 1300.00 | 19500.00 | 1350.00 | 20250.00 | 1550.00 | 23250.00 | 1500.00 | 22500.00 | 1000.00 | 15000.00 | 15000.00 | JCC ENGINEERS PRIVATE LIMITED
10.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Mtr |  | 200.00 | 4000.00 | 365.00 | 7300.00 | 300.00 | 6000.00 | 170.00 | 3400.00 | 150.00 | 3000.00 | 290.00 | 5800.00 | 450.00 | 9000.00 | 200.00 | 4000.00 | 3000.00 | VIJAYPOWER GENERATORS LIMITED
11.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtr |  | 1800.00 | 18000.00 | 1680.00 | 16800.00 | 1200.00 | 12000.00 | 1600.00 | 16000.00 | 1875.00 | 18750.00 | 1960.00 | 19600.00 | 4000.00 | 40000.00 | 1400.00 | 14000.00 | 12000.00 | Manish Electricals
12.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtr |  | 600.00 | 6000.00 | 375.00 | 3750.00 | 490.00 | 4900.00 | 650.00 | 6500.00 | 650.00 | 6500.00 | 710.00 | 7100.00 | 2500.00 | 25000.00 | 600.00 | 6000.00 | 3750.00 | Mona Generator Services Pvt. Ltd.
13.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or inrecess for connections etc. as required. | 15.00 | Mtr |  | 1000.00 | 15000.00 | 1600.00 | 24000.00 | 1250.00 | 18750.00 | 1250.00 | 18750.00 | 1300.00 | 19500.00 | 1510.00 | 22650.00 | 1200.00 | 18000.00 | 1000.00 | 15000.00 | 15000.00 | DOSHI ELECTRIC ENGG. CO., JCC ENGINEERS PRIVATE LIMITED
14.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 15.00 | Mtr |  | 150.00 | 2250.00 | 350.00 | 5250.00 | 300.00 | 4500.00 | 170.00 | 2550.00 | 150.00 | 2250.00 | 260.00 | 3900.00 | 450.00 | 6750.00 | 200.00 | 3000.00 | 2250.00 | DOSHI ELECTRIC ENGG. CO., VIJAYPOWER GENERATORS LIMITED
15.00 | Supply of 6C X 2.5 Sqmm solid copper conductor XLPE insulated armoured multicore cable, 1100 volt grade, PVC tape innersheathed complete as per IS 7098 (Part 1) 1988 standards. | 100.00 | Mtr |  | 300.00 | 30000.00 | 435.00 | 43500.00 | 485.00 | 48500.00 | 275.00 | 27500.00 | 350.00 | 35000.00 | 260.00 | 26000.00 | 220.00 | 22000.00 | 400.00 | 40000.00 | 22000.00 | Edge Telecom Pvt Ltd
16.00 | Supply of 2C X 1.5 Sqmm solid copper conductor XLPE insulated armoured multicore cable, 1100 volt grade, PVC tape innersheathed complete as per IS 7098 (Part 1) 1988 standards. | 100.00 | Mtr |  | 70.00 | 7000.00 | 100.00 | 10000.00 | 140.00 | 14000.00 | 90.00 | 9000.00 | 130.00 | 13000.00 | 98.00 | 9800.00 | 110.00 | 11000.00 | 200.00 | 20000.00 | 7000.00 | DOSHI ELECTRIC ENGG. CO.
32.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 9699250.00 |  | 13138700.00 |  | 14307250.00 |  | 12421700.00 |  | 10433733.00 |  | 10423950.00 |  | 9208750.00 |  | 11769750.00
Lowest Amount Quoted BY: Edge Telecom Pvt Ltd(9208750.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 750 KVA DG Set at SGRDJI Airport Amritsar Tender ID: 2024_AAI_192997_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Edge Telecom Pvt Ltd | 9208750.00 | L1
| 2 | DOSHI ELECTRIC ENGG. CO. | 9699250.00 | L2
| 3 | Shiva Enterprises | 10423950.00 | L3
| 4 | VIJAYPOWER GENERATORS LIMITED | 10433733.00 | L4
| 5 | JCC ENGINEERS PRIVATE LIMITED | 11769750.00 | L5
| 6 | Awasthi Electric Works | 12421700.00 | L6
| 7 | Mona Generator Services Pvt. Ltd. | 13138700.00 | L7
| 8 | Manish Electricals | 14307250.00 | L8