## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 09-May-2024 04:30 PM Tender Title: Electrical Work of Tensile Fabric portico at NITB entrance and enhancement of lighting at B M Airport Ranchi. SH Provision of Hibay LED fitting for Tensile Fabric Portico, Path way and replacement of existing Hibay LED fitting of NITB. Tender ID: 2024_AAI_193053_1
Tender Inviting Authority: SM (E-E), AAI, B.M.airport, Ranchi
Name of Work:Electrical Work of Tensile Fabric portico at NITB entrance & enhancement of lighting at B M Airport Ranchi. SH: Provision of Hibay LED fitting for Tensile Fabric Portico, Path way and replacement of existing Hibay LED fitting of NITB.
Contract No: 2024_AAI_193053
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Reliable Systems (GSTN-20ABOPA7942G1ZW) BID ID -696112 |  | GIRI ENTERPRISES (GSTN-20ACEPG3920H1ZA) BID ID -696449 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -697719 |  | RVD INFRA SOLUTION PVT.LTD. (GSTN-24AAGCR7767L1ZQ) BID ID -697901 |  | M/s CGPL ELECTROMECH PVT LTD (GSTN-07AAGCC8228F1ZO) BID ID -697915 |  | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -698173 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -698268 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -698349 |  | Variant Infratech Private Limited(GSTN-NA)--697038 |  | SIMPLEX ELECTRICALS(GSTN-NA)--697479 |  | SAURABH ENTERPRISES(GSTN-NA)--696893 |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)--697954
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of suspended Type LED Highbay symmetric Beam Luminaire with housing made of die-cast aluminium of system wattage 80 W. The luminaire shall comprise of LEDs of preffered makes complete with Constant current output driver and accessories with High Power driver installed on housing or externally and prewired upto the terminal block, PF≥0.95, THD<10% & Internal 5 KV & External 10 KV surge protection, rated life of L-70@ 50,000 hours having lumen output not less than 9600 Lumens with luminaire efficacy of not less than 120 Lumens / watt with CRI Min 70, operating range 140V – 270V, 50Hz AC supply, CCT: 5700K to 6500K and suitable for outdoor applications.The Luminarie shall be with toughened glass cover and dedicated optics to provide precise light distribution of symmetric beam angle with specially designed thermal management with heat sinks. The luminaire shall be ≥IP65 & IK08 protected.LM 79 report to be submitted for luminaire from NABL accredited lab and LM 80 for LED source issued by LED manufacture (Similar to SLE HB 80W OCULUS or as per AAI Preffered makes) | 162.00 | Each | 15000.00 | 9200.00 | 1490400.00 | 11600.00 | 1879200.00 | 5985.00 | 969570.00 | 8667.00 | 1404054.00 | 7000.00 | 1134000.00 | 8300.00 | 1344600.00 | 5025.00 | 814050.00 | 6500.00 | 1053000.00 | 4100.00 | 664200.00 | 8458.00 | 1370196.00 | 4800.00 | 777600.00 | 6000.00 | 972000.00 | 664200.00 | Variant Infratech Private Limited
2.00 | Supply of suspended Type LED Highbay symmetric Beam Luminaire with housing made of die-cast aluminium of system wattage 120 W. The luminaire shall comprise of LEDs of preffered makes complete with Constant current output driver and accessories with High Power driver installed on housing or externally and prewired upto the terminal block, PF≥0.95, THD<10% & Internal 5 KV & External 10 KV surge protection, rated life of L-70@ 50,000 hours having lumen output not less than 14400 Lumens with luminaire efficacy of not less than 120 Lumens / watt with CRI Min 70, operating range 140V – 270V, 50Hz AC supply, CCT: 5700K to 6500K and suitable for outdoor applications.The Luminarie shall be with toughened glass cover and dedicated optics to provide precise light distribution of symmetric beam angle with specially designed thermal management with heat sinks. The luminaire shall be ≥IP65 & IK08 protected.LM 79 report to be submitted for luminaire from NABL accredited lab and LM 80 for LED source issued by LED manufacture (Similar to SLE HB 120 W OCULUS or as per AAI Preffered makes) | 226.00 | Each | 27000.00 | 11000.00 | 2486000.00 | 20727.00 | 4684302.00 | 8645.00 | 1953770.00 | 10112.00 | 2285312.00 | 10500.00 | 2373000.00 | 12221.00 | 2761946.00 | 6280.00 | 1419280.00 | 7500.00 | 1695000.00 | 5500.00 | 1243000.00 | 15139.00 | 3421414.00 | 5900.00 | 1333400.00 | 7000.00 | 1582000.00 | 1243000.00 | Variant Infratech Private Limited
3.00 | Dismantling & shifting to AAI Electrical Stores the existing High-Bay Light Fittings including all accessories located at different areas of the airport complete as per instruction of Engineer-In Charge | 215.00 | Each | 500.00 | 400.00 | 86000.00 | 380.00 | 81700.00 | 5320.00 | 1143800.00 | 144.00 | 30960.00 | 50.00 | 10750.00 | 100.00 | 21500.00 | 510.00 | 109650.00 | 350.00 | 75250.00 | 575.00 | 123625.00 | 525.00 | 112875.00 | 50.00 | 10750.00 | 100.00 | 21500.00 | 10750.00 | SAURABH ENTERPRISES, M/s CGPL ELECTROMECH PVT LTD
4.00 | Wiring for Double Height area Light Fitting Luminarie with 3 Core X 4 sq.mm FRLS PVC insulated PVC sheathed Copper conductor unarmoured cable in surface /truss/Column complete with clamps, saddles,loop earthing etc as per actual site requirement | 1000.00 | Mtrs | 300.00 | 742.00 | 742000.00 | 228.00 | 228000.00 | 200.00 | 200000.00 | 217.00 | 217000.00 | 150.00 | 150000.00 | 150.00 | 150000.00 | 960.00 | 960000.00 | 325.00 | 325000.00 | 200.00 | 200000.00 | 315.00 | 315000.00 | 25.00 | 25000.00 | 212.00 | 212000.00 | 25000.00 | SAURABH ENTERPRISES
5.00 | Installation, Testing and Commissioning of LED High-Bay Light fittings on different Height of cieling/Structure/Canopy with all mounting accessories & Hanging arrangement upto 15 Mtrs etc as required complete including connection with 2.5 sq.mm FRLS PVC insulated copper conductor three core cable etc. as required. Job includes all necessary hardware required to fix the fitting on ceiling/Canopy/structure etc as per site requirement. | 369.00 | Each | 430.00 | 1000.00 | 369000.00 | 327.00 | 120663.00 | 4855.00 | 1791495.00 | 433.00 | 159777.00 | 200.00 | 73800.00 | 300.00 | 110700.00 | 1180.00 | 435420.00 | 350.00 | 129150.00 | 3450.00 | 1273050.00 | 445.00 | 164205.00 | 25.00 | 9225.00 | 200.00 | 73800.00 | 9225.00 | SAURABH ENTERPRISES
6.00 | Supplying and fixing following way, horizontal type three pole and neutral, Suitable for 125 Amp FP MCCB incomer, made of sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way (4 + 24), Double door | 2.00 | Jobs | 7900.00 | 4500.00 | 9000.00 | 6003.00 | 12006.00 | 41748.00 | 83496.00 | 2889.00 | 5778.00 | 5503.00 | 11006.00 | 7000.00 | 14000.00 | 180600.00 | 361200.00 | 12500.00 | 25000.00 | 5200.00 | 10400.00 | 7905.00 | 15810.00 | 7687.00 | 15374.00 | 4000.00 | 8000.00 | 5778.00 | RVD INFRA SOLUTION PVT.LTD.
7.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPNMCB distribution board suitable for 125 amp FP MCCB incomer, made of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required . 8 way (4 + 24), Double door | 2.00 | Job | 15000.00 | 6500.00 | 13000.00 | 11399.00 | 22798.00 | 41748.00 | 83496.00 | 2889.00 | 5778.00 | 8500.00 | 17000.00 | 10000.00 | 20000.00 | 18600.00 | 37200.00 | 13500.00 | 27000.00 | 5200.00 | 10400.00 | 15105.00 | 30210.00 | 8500.00 | 17000.00 | 7000.00 | 14000.00 | 5778.00 | RVD INFRA SOLUTION PVT.LTD.
8.00 | Providing and fixing following rating and breaking capacity andpole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. 125 A,36KA,FPMCCB | 2.00 | Jobs | 5150.00 | 6500.00 | 13000.00 | 3913.00 | 7826.00 | 25180.00 | 50360.00 | 5778.00 | 11556.00 | 4000.00 | 8000.00 | 4000.00 | 8000.00 | 10050.00 | 20100.00 | 15500.00 | 31000.00 | 6325.00 | 12650.00 | 5145.00 | 10290.00 | 6100.00 | 12200.00 | 9550.00 | 19100.00 | 7826.00 | GIRI ENTERPRISES
9.00 | Supply & Fixing of 5A to 32A rating, 240/415 V, 10 kA, "C" curve, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. complete as required.
9.01 | Single pole | 30.00 | Nos. | 280.00 | 875.00 | 26250.00 | 213.00 | 6390.00 | 1102.00 | 33060.00 | 159.00 | 4770.00 | 200.00 | 6000.00 | 200.00 | 6000.00 | 300.00 | 9000.00 | 175.00 | 5250.00 | 190.00 | 5700.00 | 285.00 | 8550.00 | 100.00 | 3000.00 | 100.00 | 3000.00 | 3000.00 | SAURABH ENTERPRISES, JCC ENGINEERS PRIVATE LIMITED
9.02 | Double pole | 5.00 | Nos. | 800.00 | 1025.00 | 5125.00 | 608.00 | 3040.00 | 2190.00 | 10950.00 | 650.00 | 3250.00 | 350.00 | 1750.00 | 600.00 | 3000.00 | 800.00 | 4000.00 | 600.00 | 3000.00 | 450.00 | 2250.00 | 815.00 | 4075.00 | 350.00 | 1750.00 | 300.00 | 1500.00 | 1500.00 | JCC ENGINEERS PRIVATE LIMITED
9.03 | Triple pole & neutral | 6.00 | Nos. | 1200.00 | 1200.00 | 7200.00 | 912.00 | 5472.00 | 8175.00 | 49050.00 | 939.00 | 5634.00 | 400.00 | 2400.00 | 1000.00 | 6000.00 | 1635.00 | 9810.00 | 1250.00 | 7500.00 | 800.00 | 4800.00 | 1260.00 | 7560.00 | 800.00 | 4800.00 | 900.00 | 5400.00 | 2400.00 | M/s CGPL ELECTROMECH PVT LTD
10.00 | Supply of following sizes of XLPE insulated PVC sheathed, copper conductor armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 with upto date amendments complete as required
10.01 | 4 Core, 25 Sqmm | 250.00 | Metre | 1600.00 | 1845.00 | 461250.00 | 1216.00 | 304000.00 | 2860.00 | 715000.00 | 1733.00 | 433250.00 | 1100.00 | 275000.00 | 1400.00 | 350000.00 | 1995.00 | 498750.00 | 1350.00 | 337500.00 | 1500.00 | 375000.00 | 1850.00 | 462500.00 | 150.00 | 37500.00 | 1200.00 | 300000.00 | 37500.00 | SAURABH ENTERPRISES
10.02 | 4 Core, 16 Sqmm | 250.00 | Metre | 1200.00 | 1460.00 | 365000.00 | 912.00 | 228000.00 | 2461.00 | 615250.00 | 1300.00 | 325000.00 | 750.00 | 187500.00 | 1100.00 | 275000.00 | 1280.00 | 320000.00 | 880.00 | 220000.00 | 1100.00 | 275000.00 | 1315.00 | 328750.00 | 150.00 | 37500.00 | 800.00 | 200000.00 | 37500.00 | SAURABH ENTERPRISES
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
11.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 250.00 | Metre | 60.00 | 200.00 | 50000.00 | 46.00 | 11500.00 | 665.00 | 166250.00 | 87.00 | 21750.00 | 10.00 | 2500.00 | 60.00 | 15000.00 | 135.00 | 33750.00 | 140.00 | 35000.00 | 120.00 | 30000.00 | 63.00 | 15750.00 | 50.00 | 12500.00 | 100.00 | 25000.00 | 2500.00 | M/s CGPL ELECTROMECH PVT LTD
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
12.01 | Upto 35 sq. mm | 250.00 | Metre | 45.00 | 200.00 | 50000.00 | 34.00 | 8500.00 | 665.00 | 166250.00 | 87.00 | 21750.00 | 10.00 | 2500.00 | 45.00 | 11250.00 | 130.00 | 32500.00 | 140.00 | 35000.00 | 120.00 | 30000.00 | 51.00 | 12750.00 | 50.00 | 12500.00 | 25.00 | 6250.00 | 2500.00 | M/s CGPL ELECTROMECH PVT LTD
13.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required
13.01 | 4 X 25 sq. mm (28mm) | 4.00 | Each | 850.00 | 14500.00 | 58000.00 | 646.00 | 2584.00 | 200.00 | 800.00 | 361.00 | 1444.00 | 714.00 | 2856.00 | 500.00 | 2000.00 | 1140.00 | 4560.00 | 450.00 | 1800.00 | 575.00 | 2300.00 | 875.00 | 3500.00 | 500.00 | 2000.00 | 300.00 | 1200.00 | 800.00 | Instapower Ltd
13.02 | 4 X 16 sq. mm (32mm) | 4.00 | Each | 750.00 | 14500.00 | 58000.00 | 570.00 | 2280.00 | 160.00 | 640.00 | 289.00 | 1156.00 | 500.00 | 2000.00 | 500.00 | 2000.00 | 1100.00 | 4400.00 | 475.00 | 1900.00 | 575.00 | 2300.00 | 790.00 | 3160.00 | 400.00 | 1600.00 | 200.00 | 800.00 | 640.00 | Instapower Ltd
14.00 | SITC of Low-Intensity,Type-A, Aviation Light LED luminarie (steady Red Colour obstruction light) as per the ICAO Specifications and the Technical Parameters as per Annexure - I to install above the PBB including dismantling of the existing conventional fitting and taking it to AAI Store (to a distance of lead 50 mtrs) etc., as required and directed by Engg-In-Charge. | 5.00 | Each | 4100.00 | 12000.00 | 60000.00 | 3116.00 | 15580.00 | 19800.00 | 99000.00 | 8667.00 | 43335.00 | 3000.00 | 15000.00 | 4000.00 | 20000.00 | 12705.00 | 63525.00 | 6500.00 | 32500.00 | 5175.00 | 25875.00 | 4120.00 | 20600.00 | 4500.00 | 22500.00 | 4001.00 | 20005.00 | 15000.00 | M/s CGPL ELECTROMECH PVT LTD
15.00 | Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge. Sign face: Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour(colour Pantone Black 6C) and vinyl for text Pantone yellow C or Pantone Cyan 311C as per graphics and of specified make duly approved by the Engineer-in-Charge. Sign Frame (Type -1 :Suspended type) Providing and fixing sign frame 50mm wide Powder coated, colour RAL 9006 special aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with 3M brand dual lock system in one side and 3M both way tape from the other side or other suitable means. The panel should be made easily openable for maintenance. Sign Structure (Type -2) All hardware used for fixing of sign shall be Stainless Steel. Projection supported internally by side mounting of SS frame. Lighting: All internal illumination shall be using Power LED strip edge Lights from Osram or as per AAI Preferred makes with electronic controllers, having even spread and overlaps to avoid banding and dark spots including all internal connections and wiring, termination and connection to the incoming electrical supply cable from nearest available point at the site. The actual structural design of the sign for its stability shall be responsibility of the contactor.Secret fixing methods should be used to fix parts together. Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut- inserts, screws, rivets, bolts, washers, nuts, etc. complete in all respect as per drawing/ specification as required.
15.01 | Single sided | 10.00 | Sqm | 22000.00 | 25000.00 | 250000.00 | 16716.00 | 167160.00 | 10640.00 | 106400.00 | 14445.00 | 144450.00 | 14500.00 | 145000.00 | 10000.00 | 100000.00 | 43150.00 | 431500.00 | 55000.00 | 550000.00 | 64000.00 | 640000.00 | 24015.00 | 240150.00 | 32000.00 | 320000.00 | 23000.00 | 230000.00 | 100000.00 | M/S AMAR ENTERPRISES
15.02 | Double sided | 10.00 | sqm | 30000.00 | 40000.00 | 400000.00 | 22797.00 | 227970.00 | 19950.00 | 199500.00 | 21668.00 | 216680.00 | 15000.00 | 150000.00 | 10000.00 | 100000.00 | 52750.00 | 527500.00 | 70000.00 | 700000.00 | 64000.00 | 640000.00 | 34198.00 | 341980.00 | 34380.00 | 343800.00 | 26000.00 | 260000.00 | 100000.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 6999225.00 |  | 8018971.00 |  | 8438137.00 |  | 5342684.00 |  | 4570062.00 |  | 5320996.00 |  | 6096195.00 |  | 5289850.00 |  | 5570550.00 |  | 6889325.00 |  | 2999999.00 |  | 3955555.00
Lowest Amount Quoted BY: SAURABH ENTERPRISES(2999999.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical Work of Tensile Fabric portico at NITB entrance and enhancement of lighting at B M Airport Ranchi. SH Provision of Hibay LED fitting for Tensile Fabric Portico, Path way and replacement of existing Hibay LED fitting of NITB. Tender ID: 2024_AAI_193053_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES | 2999999.00 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED | 3955555.00 | L2
| 3 | M/s CGPL ELECTROMECH PVT LTD | 4570062.00 | L3
| 4 | Awasthi Electric Works | 5289850.00 | L4
| 5 | M/S AMAR ENTERPRISES | 5320996.00 | L5
| 6 | RVD INFRA SOLUTION PVT.LTD. | 5342684.00 | L6
| 7 | Variant Infratech Private Limited | 5570550.00 | L7
| 8 | Yash Energy Pvt. Ltd | 6096195.00 | L8
| 9 | SIMPLEX ELECTRICALS | 6889325.00 | L9
| 10 | Reliable Systems | 6999225.00 | L10
| 11 | GIRI ENTERPRISES | 8018971.00 | L11
| 12 | Instapower Ltd | 8438137.00 | L12