## BoQ1
Government eProcurement System Created By: Pankaj Wanjari Created Date/Time: 20-May-2024 04:51 PM Tender Title: Additional works construction of retaining wall car park road work and other miscellaneous development works CISF bachelor accommodation including electrical works at CE Goa SH Service Connection Tender ID: 2024_AAI_193754_1
Tender Inviting Authority: Asst. General Manager (Engg-E)
Name of Work: Additional works construction of retaining wall, car park, road work and other miscellaneous development works CISF bachelor accommodation (including electrical works) at C.E. Goa. SH: Service Connection.
Contract No: Tender ID : 2024_AAI_193754_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -700706
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and Erection 11 mtr. long of RCC/ PCC pole of following length in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded granitic or basaltic stone aggregate 40 m nominal size foundation, including hard rock pit digging/ excavation etc as required as per GED specification. | 2.00 | Each |  | 30867.00 | 61734.00 | 61734.00 | SARASWAT ENGINEERING SERVICES
2.00 | Supplying and erection of stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle ( 20 mm X 60 cm ), 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded granitic or basaltic stone aggregate 40 m nominal size foundation, including hard rock pit digging/ excavation etc as required as per GED specification. | 1.00 | Set |  | 5358.00 | 5358.00 | 5358.00 | SARASWAT ENGINEERING SERVICES
3.00 | Supply and Erection of HDGI structural material for DP strucutre. | 125.00 | Kg |  | 177.00 | 22125.00 | 22125.00 | SARASWAT ENGINEERING SERVICES
4.00 | Supply and fixing of 11KV 200 Amps GOAB switch. | 1.00 | Set |  | 31449.00 | 31449.00 | 31449.00 | SARASWAT ENGINEERING SERVICES
5.00 | Supply and erection of H.G. Fuse unit 11 KV 200 Amps. | 1.00 | Set |  | 13279.00 | 13279.00 | 13279.00 | SARASWAT ENGINEERING SERVICES
6.00 | Supplying and erection of three piece nonlinear resistor type lightning arrestor suitable for 3 wire, 11 KV overhead lines with rated voltage 9 KV (rms) with a nominal discharge current rating of 5 KA and complete with galvanised clamping arrangement, G.I. bolts, nuts, washers etc. as required as per GED specification. | 1.00 | Set |  | 4426.00 | 4426.00 | 4426.00 | SARASWAT ENGINEERING SERVICES
7.00 | Supplying and erection of 11 KV pin insulator complete with large steel head G.I. pin, nuts, washers etc. as required as per GED specification. | 6.00 | Each |  | 1008.00 | 6048.00 | 6048.00 | SARASWAT ENGINEERING SERVICES
8.00 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg permetre) V shape cross arm for two 11 KV over head line conductors complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts and washers etc and painting with primer and finish paint as required as per GED specification. | 1.00 | Each |  | 2533.00 | 2533.00 | 2533.00 | SARASWAT ENGINEERING SERVICES
9.00 | Supply and stringing of ACSR Weasel conductor (7/2.59 mm dia.) for jumppering and earthing as per GED specification. | 100.00 | Meter |  | 61.00 | 6100.00 | 6100.00 | SARASWAT ENGINEERING SERVICES
10.00 | Supply and Erection of HDGI top fitting for 11 KV RCC Pole as per GED specification. | 1.00 | Each |  | 699.00 | 699.00 | 699.00 | SARASWAT ENGINEERING SERVICES
11.00 | Supply of following sizes 11 KV grade, XLPE insulated & PVC sheathed armoured aluminium conductor HT(E) cable generally confirming to IS 7098 Part II-1985 with up to date amendments as required. Makes: As per approved make list of Goa Electrical Division. (Polycab, Torrent, Universal cables (Unistar), KEI, KEC Intl Ltd.) a) 3C X 300 sq.mm. | 550.00 | Meter |  | 2278.00 | 1252900.00 | 1252900.00 | SARASWAT ENGINEERING SERVICES
12.00 | Laying of HDPE pipe (High Density Polyethylene) upto 160 mm dia. direct in ground up to a depth of 100 cm including excavation in hard rock and refilling the trench including repairing the road by providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded granitic or basaltic stone aggregate 40 m nominal size 200 mm depth (for road crossing) as per GED specifiaction. | 30.00 | Meter |  | 1398.00 | 41940.00 | 41940.00 | SARASWAT ENGINEERING SERVICES
13.00 | Supply & Erection of Medium duty, HDGI Class B pipe of nominal diameter 150 mm (alongwith HDGI bends wherever required) for bridge crossing/riser pipe for 300Sq.mm XLPE Cable etc., as per technical specifications including supporting arrangement for the pipe. | 12.00 | Meter |  | 3145.00 | 37740.00 | 37740.00 | SARASWAT ENGINEERING SERVICES
14.00 | Laying of two number 3C x 300 sq. mm. PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade along with warning tapes in ground including excavation by mechanical means( hydraulic excavator)/manual means including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposl of surplus excavated soil as directed within a lead of 50 m(a) in all types of laterite/Hard rock etc. with trench lengths depth and width 1.10 x 0.60 for laying of 2 run cable, sand cushioning, protective covering concrete slab of size 480mm x 250mm x 50mm, (+/- 2mm) M30 and refilling of available excavated earth (excluding rock/stones) in trench in layer not exceeding 0.2mts as per GED specification and drawing. | 250.00 | Meter |  | 2446.00 | 611500.00 | 611500.00 | SARASWAT ENGINEERING SERVICES
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required. a) Above 120 sq. mm and upto 400 sq. mm | 54.00 | Meter |  | 291.00 | 15714.00 | 15714.00 | SARASWAT ENGINEERING SERVICES
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing masonary open duct as required. a) upto 120 sq. mm. | 20.00 | Meter |  | 262.00 | 5240.00 | 5240.00 | SARASWAT ENGINEERING SERVICES
17.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size XLPE aluminium conductor cable of 11 kV grade as required. Makes: As per approved make list of Goa Electricity Department. Raychem, Behr Bircher Cellpack BVC India Pvt Ltd.
17.01 | a) 3C X 300 sq.mm. | 2.00 | Set |  | 17472.00 | 34944.00 | 34944.00 | SARASWAT ENGINEERING SERVICES
17.02 | b) 3C X 95 sq.mm. | 4.00 | Set |  | 13396.00 | 53584.00 | 53584.00 | SARASWAT ENGINEERING SERVICES
18.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size XLPE aluminium conductor cable of 11 kV grade as required. Makes: As per approved make list of Goa Electrical Division. Raychem, Behr Bircher Cellpack BVC India Pvt Ltd. a) 3C X 300 sq.mm. | 2.00 | Set |  | 19801.00 | 39602.00 | 39602.00 | SARASWAT ENGINEERING SERVICES
19.00 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 5.00 | Each |  | 2213.00 | 11065.00 | 11065.00 | SARASWAT ENGINEERING SERVICES
20.00 | Supply, installation, testing and commissioning of outdoor type (IP 54) 11 KV grade 3 way RMU (ring main unit), consisting of 2 LBS and 1 VCB with rated current 630 Amps and rated short time current of 21 KA for 3 sec, SF6 gas housed in hermetically robotically sealed high tensile stainless steel enclosure not less than 3 mm. (IP 67). The RMU metal parts shall be greater than 3mm thickness high tensile steel which must be shot blasted, spray galvanized with minimum thickness of 30 micron and subsequently powder coated. The unit shall have bottom cable entry with suitable rating C.T.s alongwith Over-current & Earth-fault protection relay, voltage indicator, Tripping mechanism, emergency push-trip button with Fault passage indicator and SCADA compliant, supply and laying of 1.5 sq. mm armoured copper conrtol cable for providing AC supply including all necessary standard fitting required at site and as per technical specifications complete as required including civil foundation with cement concrete 1:2:4, 12 mm cement plaster 1:4 as per GED specification. Note: All the above materials shall be as per approved makes of Goa Electrical Department. Lucy Electric, Schneider, ABB, Siemens, CG power and industrial solutions, L&T Ltd. | 1.00 | Job |  | 631904.00 | 631904.00 | 631904.00 | SARASWAT ENGINEERING SERVICES
21.00 | HT METERING PANEL Design, Supply, Installation, Testing and Commissioning of outdoor type double door 11 KV HT metering cubicle panel, made out of 10 SWG thick CRCA sheet steel, totally enclosed, IP-55 protection free standing with mounting pole supports, dust and vermin proof, compartmentalized, powder coated painting as per approved drawing and specifications prescribed by MRT, Electricity Deptt Govt. of Goa, 3 nos. copper busbars, GI earth bar, space heaters with associated internal wiring/secondary wiring for PTs and CTs, earth bar and as per technical specifications comprising following components and jobs including Civil foundation: a) Indoor type resin cast 11 KV rating CT’s- 3 nos. Having accuracy class of .5s CT ratio of 25/5 Amps and burden of 15 VA STC 13.1 KA for 1 sec. b)Indoor type resin cast 11 KV rating PT's - 3 nos. Having accuracy class of .5 CT ratio of 11KV/√3/110V/√3 and rated burden of 50 VA VF 1.2 continuous and 1.9 for 8 hours c)Electronic Trivector meter, 110 volts -/+ 5 Amps 3 Phase 4 wire, DLMS protocol with TOD, CAT C. d) Job includes Supply and providing of insulkote insulation enhancement coating to 11 KV breaker (CT/PT and copper busbar along with cable kit) using Z1311 Insulkote class B, Z906, Provar antitrack 8086 safety solvent, 8480 carbon cleaner, electrosol tape, mccoy silirub silicon sealant and mccoy Gen 750 foam sealant. e) Supply of analogics Modems. Note: All the above materials shall be as per approved makes and as per approved drawing and specification of Electricity Department Govt. of Goa & tested by MRT. | 1.00 | Job |  | 314496.00 | 314496.00 | 314496.00 | SARASWAT ENGINEERING SERVICES
22.00 | Earthing with G.I. earth pipe 2500 mm long, 40mm dia class B fabricated and perforated filled with homogenous mixture of 20Kgs of Charcoal, 20Kgs of salt and with brick masonary enclosure with cover plate 300 mm x 300 mm having locking arrangement and watering pipe including hard rock pit digging and refilling etc. as required as per GED specification. | 15.00 | Set |  | 6756.00 | 101340.00 | 101340.00 | SARASWAT ENGINEERING SERVICES
23.00 | Providing & fixing HDGI flat of size 25 mm x 6 mm including supply and fixing of required quantity of HDGI nut bolts for earthing of all euipment. | 75.00 | Meter |  | 466.00 | 34950.00 | 34950.00 | SARASWAT ENGINEERING SERVICES
24.00 | Providing and fixing H.T. Danger Notice Plate of 250 mm X 200 mm, made of MS sheet , at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 2.00 | Each |  | 308.00 | 616.00 | 616.00 | SARASWAT ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 3341286.00
Lowest Amount Quoted BY: SARASWAT ENGINEERING SERVICES(3341286.00)

## BOQ Summary
BOQ Summary Details Tender Title: Additional works construction of retaining wall car park road work and other miscellaneous development works CISF bachelor accommodation including electrical works at CE Goa SH Service Connection Tender ID: 2024_AAI_193754_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SARASWAT ENGINEERING SERVICES | 3341286.00 | L1