## BoQ1
Government eProcurement System Created By: Sujit Kumar Modak Created Date/Time: 03-Jul-2024 05:46 PM Tender Title: Operation and Maintenance of Fire fighting system and misc works Tender ID: 2024_AAI_195599_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: R & M and other Electrical Works at NSCBI Airport, Kolkata. SH: Operation & Maintenance of Fire Fighting system including related miscellaneous works.
Contract No: 2024_AAI_195599_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s CGPL ELECTROMECH PVT LTD (GSTN-07AAGCC8228F1ZO) BID ID -705905 |  | Voltas Limited (GSTN-19AAACV2809D1ZJ) BID ID -706295 |  | Blue Star Ltd (GSTN-19AAACB4487D1ZP) BID ID -706988 |  | J.K.DEFENCE FIRE ENGG. SERVICES(GSTN-NA)--707283
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I Operation & Maintenance
2.00 | Round the clock (24x7) Operation for the Fire fighting system installed in Terminal Building along with its associated system accessories including day to day Maintenance of Fire fighting system by carrying out regular inspection, testing, Preventive Maintenance, documentation etc. for the Fire Fighting System installed at Terminal-2 as well as Fire Figting Pump Section near NSCBI Airport Police Stationin accordance to the GCC, Special Conditions of Contract and Particular & Technical Specification of Contract and by deploying following minimum manpower at NSCBI Airport, Kolkata. Manpower: i. Overall Supervisor (Highly Skilled): 01 No. ii. Shift in-Charge (Highly Skilled): 03 Nos. iii. Electrician/Plumber/Fitter (Skilled): 07 nos. iv. Helper (Unskilled): 11 Nos. Note: Follow Special Conditions of Contract (SCC) for shift wise bifurcation along with category of manpower.
3.00 | a) First Year | 12.00 | Month |  | 624000.00 | 7488000.00 | 511979.16 | 6143749.92 | 709362.00 | 8512344.00 | 1200000.00 | 14400000.00 | 6143749.92 | Voltas Limited
4.00 | b) Second Year | 12.00 | Month |  | 623200.00 | 7478400.00 | 511979.16 | 6143749.92 | 737735.00 | 8852820.00 | 1225000.00 | 14700000.00 | 6143749.92 | Voltas Limited
5.00 | SH: II Overhauling & Servicing of pumps, blowers, Fire DG etc.
6.00 | Servicing and complete overhauling of 3 phase 415 Volts, 50 Hz, 15 HP /11 KW Kirloskar make Fire Jockey pump motor set having Class F insulation and protection of IP 55, RPM of 2890, including replacement of mechanical & oil seal, o-ring, moisture sensor, defective bearing, coupling, impellars, and other necessary spare parts, heat varnishing the motor etc. as required after dismantling the existing pump set, reinstallation after overhauling, testing and commissioning etc. complete as required.
7.00 | a) First Year | 1.00 | Job |  | 7500.00 | 7500.00 | 4000.00 | 4000.00 | 17250.00 | 17250.00 | 15000.00 | 15000.00 | 4000.00 | Voltas Limited
8.00 | b) Second Year | 1.00 | Job |  | 8500.00 | 8500.00 | 2000.00 | 2000.00 | 11500.00 | 11500.00 | 15000.00 | 15000.00 | 2000.00 | Voltas Limited
9.00 | Servicing and complete overhauling of 3 phase 415 Volts, 50 Hz, 100 HP /75 KW Kirloskar make Fire Hydrant pump motor set having Class F insulation and protection of IP 22, RPM of 1468, having total head of 70 mtr. and discharge capacity of 47.5 ltr/sec including replacement of mechanical & oil seal, o-ring, moisture sensor, replacement of bearing, coupling, impellars and other necessary parts if required, heat varnishing the motor etc. as required after dismantling the existing pump set, reinstallation after overhauling, testing and commissioning etc. complete as required. Pump Model: Kirloskar Make, Type DSM 5BE
10.00 | a) First Year | 1.00 | Job |  | 35500.00 | 35500.00 | 5000.00 | 5000.00 | 69000.00 | 69000.00 | 75000.00 | 75000.00 | 5000.00 | Voltas Limited
11.00 | b) Second Year | 1.00 | Job |  | 38000.00 | 38000.00 | 5250.00 | 5250.00 | 69000.00 | 69000.00 | 75000.00 | 75000.00 | 5250.00 | Voltas Limited
12.00 | Servicing and complete overhauling of 3 phase 415 Volts, 50 Hz, 90 HP /67.5 KW Kirloskar make Fire Hydrant pump motor set having Class F insulation and protection of IP 22, RPM of 1465, having total head of 70 mtr. and discharge capacity of 47.5 ltr/sec including replacement of mechanical & oil seal, o-ring, moisture sensor, replacement of defective bearing, coupling, impellars, and other necessary spare parts, heat varnishing the motor etc. as required after dismantling the existing pump set, reinstallation after overhauling, testing and commissioning etc. complete as required. Pump Model: Kirloskar Make, Type DSM 5BE
13.00 | a) First Year | 1.00 | Job |  | 32000.00 | 32000.00 | 5000.00 | 5000.00 | 46000.00 | 46000.00 | 60000.00 | 60000.00 | 5000.00 | Voltas Limited
14.00 | b) Second Year | 1.00 | Job |  | 35000.00 | 35000.00 | 5250.00 | 5250.00 | 46000.00 | 46000.00 | 60000.00 | 60000.00 | 5250.00 | Voltas Limited
15.00 | Servicing and complete overhauling of 3 phase 415 Volts, 50 Hz, 10 HP /7.5 KW Kirloskar make Fire Jockey pump motor set having Class F insulation and protection of IP 55, RPM of 1450, having total head of 70 mtrs. and discharge capacity of 15 m3/hr including replacement of mechanical & oil seal, o-ring, moisture sensor, replacement of defective bearing, coupling, impellars, and other necessary spare parts, heat varnishing the motor etc. as required after dismantling the existing pump set, reinstallation after overhauling, testing and commissioning etc. complete as required. Pump Model: Kirloskar Make, Type RKB 50/15L9
16.00 | a) First Year | 2.00 | Job |  | 6500.00 | 13000.00 | 3000.00 | 6000.00 | 8050.00 | 16100.00 | 10000.00 | 20000.00 | 6000.00 | Voltas Limited
17.00 | b) Second Year | 2.00 | Job |  | 7000.00 | 14000.00 | 3150.00 | 6300.00 | 8050.00 | 16100.00 | 10000.00 | 20000.00 | 6300.00 | Voltas Limited
18.00 | Servicing and complete overhauling of 3 phase 415 Volts, 50 Hz, 75 HP /55 KW Kirloskar make Fire Hydrant / Sprinkler pump motor set having Class F insulation and protection of IP 55, RPM of 1450, having total head of 70 mtrs. and discharge capacity of 171 m3/hr including replacement of mechanical & oil seal, o-ring, moisture sensor, replacement of defective bearing, coupling, impellars, and other necessary spare parts, heat varnishing the motor etc. as required after dismantling the existing pump set, reinstallation after overhauling, testing and commissioning etc. complete as required. Pump Model: Kirloskar Make, Type DSM 125/40.
19.00 | a) First Year | 2.00 | Job |  | 30000.00 | 60000.00 | 4000.00 | 8000.00 | 34500.00 | 69000.00 | 35000.00 | 70000.00 | 8000.00 | Voltas Limited
20.00 | b) Second Year | 2.00 | Job |  | 32000.00 | 64000.00 | 4200.00 | 8400.00 | 34500.00 | 69000.00 | 35000.00 | 70000.00 | 8400.00 | Voltas Limited
21.00 | Carrying out B Check servicing of 67.7 KW / 92 HP Kirloskar make fire engine, Type 6R1080 including replacement of entire lub oil, fuel filter element pre, fuel filter element micro, spin on filter for lubricating oil, air filter etc. as required as per OEM recommendations as well as carrying out the work through OEM along with submission of service reports etc. as required.
22.00 | a) First Year | 4.00 | Job |  | 30000.00 | 120000.00 | 32000.00 | 128000.00 | 34500.00 | 138000.00 | 35000.00 | 140000.00 | 120000.00 | M/s CGPL ELECTROMECH PVT LTD
23.00 | b) Second Year | 4.00 | Job |  | 32000.00 | 128000.00 | 33600.00 | 134400.00 | 34500.00 | 138000.00 | 35000.00 | 140000.00 | 128000.00 | M/s CGPL ELECTROMECH PVT LTD
24.00 | Carrying out B Check servicing of 75 KW / 100 HP Cummins make fire engine, including replacement of entire lub oil, fuel filter element pre, fuel filter element micro, spin on filter for lubricating oil, air filter etc. as required as per OEM recommendations as well as carrying out the work through OEM along with submission of service reports etc. as required.
25.00 | a) First Year | 2.00 | Job |  | 32000.00 | 64000.00 | 20000.00 | 40000.00 | 34500.00 | 69000.00 | 30000.00 | 60000.00 | 40000.00 | Voltas Limited
26.00 | b) Second Year | 2.00 | Job |  | 35000.00 | 70000.00 | 21000.00 | 42000.00 | 34500.00 | 69000.00 | 30000.00 | 60000.00 | 42000.00 | Voltas Limited
27.00 | Carrying out B Check servicing of 75 KW / 100 HP Cummins make fire engine, including replacement of entire lub oil, fuel filter element pre, fuel filter element micro, spin on filter for lubricating oil, air filter etc. as required as per OEM recommendations as well as carrying out the work through OEM along with submission of service reports etc. as required.
28.00 | SH: III Providing / Servicing of various valves & MS Pipes
29.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required.
30.00 | 200 mm. dia (wall thickness = 6.3 mm)
31.00 | a) First Year | 20.00 | Mtrs. |  | 2550.00 | 51000.00 | 2090.00 | 41800.00 | 4025.00 | 80500.00 | 3450.00 | 69000.00 | 41800.00 | Voltas Limited
32.00 | b) Second Year | 20.00 | Mtrs. |  | 2550.00 | 51000.00 | 2194.50 | 43890.00 | 4025.00 | 80500.00 | 3450.00 | 69000.00 | 43890.00 | Voltas Limited
33.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required.
34.00 | 25 mm dia
35.00 | a) First Year | 20.00 | Mtrs. |  | 250.00 | 5000.00 | 170.00 | 3400.00 | 432.00 | 8640.00 | 500.00 | 10000.00 | 3400.00 | Voltas Limited
36.00 | b) Second Year | 20.00 | Mtrs. |  | 250.00 | 5000.00 | 187.00 | 3740.00 | 449.00 | 8980.00 | 500.00 | 10000.00 | 3740.00 | Voltas Limited
37.00 | 32 mm dia
38.00 | a)First Year | 20.00 | Mtrs. |  | 275.00 | 5500.00 | 223.00 | 4460.00 | 506.00 | 10120.00 | 700.00 | 14000.00 | 4460.00 | Voltas Limited
39.00 | b)Second Year | 20.00 | Mtrs. |  | 290.00 | 5800.00 | 245.30 | 4906.00 | 418.00 | 8360.00 | 700.00 | 14000.00 | 4906.00 | Voltas Limited
40.00 | 40 mm dia
41.00 | a)First Year | 10.00 | Mtrs. |  | 325.00 | 3250.00 | 259.00 | 2590.00 | 558.00 | 5580.00 | 900.00 | 9000.00 | 2590.00 | Voltas Limited
42.00 | b)Second Year | 10.00 | Mtrs. |  | 350.00 | 3500.00 | 285.00 | 2850.00 | 570.00 | 5700.00 | 900.00 | 9000.00 | 2850.00 | Voltas Limited
43.00 | 50 mm dia
44.00 | a)First Year | 10.00 | Mtrs. |  | 450.00 | 4500.00 | 361.00 | 3610.00 | 834.00 | 8340.00 | 1100.00 | 11000.00 | 3610.00 | Voltas Limited
45.00 | b)Second Year | 10.00 | Mtrs. |  | 465.00 | 4650.00 | 397.00 | 3970.00 | 863.00 | 8630.00 | 1100.00 | 11000.00 | 3970.00 | Voltas Limited
46.00 | 100 mm dia
47.00 | a)First Year | 20.00 | Mtrs. |  | 1350.00 | 27000.00 | 852.00 | 17040.00 | 1380.00 | 27600.00 | 1750.00 | 35000.00 | 17040.00 | Voltas Limited
48.00 | b)Second Year | 20.00 | Mtrs. |  | 1375.00 | 27500.00 | 937.20 | 18744.00 | 1380.00 | 27600.00 | 1750.00 | 35000.00 | 18744.00 | Voltas Limited
49.00 | 150 mm dia
50.00 | a)First Year | 20.00 | Mtrs. |  | 1650.00 | 33000.00 | 1252.00 | 25040.00 | 1380.00 | 27600.00 | 2800.00 | 56000.00 | 25040.00 | Voltas Limited
51.00 | b)Second Year | 20.00 | Mtrs. |  | 1750.00 | 35000.00 | 1377.20 | 27544.00 | 1380.00 | 27600.00 | 2800.00 | 56000.00 | 27544.00 | Voltas Limited
52.00 | 200 mm dia (wall thickness 6.3 mm)
53.00 | a)First Year | 20.00 | Mtrs. |  | 2700.00 | 54000.00 | 2090.00 | 41800.00 | 2530.00 | 50600.00 | 3300.00 | 66000.00 | 41800.00 | Voltas Limited
54.00 | b)Second Year | 20.00 | Mtrs. |  | 2800.00 | 56000.00 | 2299.00 | 45980.00 | 2530.00 | 50600.00 | 3300.00 | 66000.00 | 45980.00 | Voltas Limited
55.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required.
56.00 | 40 mm dia
57.00 | a) First Year | 1.00 | Set |  | 1500.00 | 1500.00 | 1674.00 | 1674.00 | 3215.00 | 3215.00 | 2500.00 | 2500.00 | 1500.00 | M/s CGPL ELECTROMECH PVT LTD
58.00 | b) Second Year | 1.00 | Set |  | 1600.00 | 1600.00 | 1841.40 | 1841.40 | 3215.00 | 3215.00 | 2800.00 | 2800.00 | 1600.00 | M/s CGPL ELECTROMECH PVT LTD
59.00 | 80 mm dia
60.00 | a) First Year | 1.00 | Set |  | 2000.00 | 2000.00 | 2530.00 | 2530.00 | 4715.00 | 4715.00 | 3500.00 | 3500.00 | 2000.00 | M/s CGPL ELECTROMECH PVT LTD
61.00 | b) Second Year | 1.00 | Set |  | 2100.00 | 2100.00 | 2783.00 | 2783.00 | 4715.00 | 4715.00 | 3800.00 | 3800.00 | 2100.00 | M/s CGPL ELECTROMECH PVT LTD
62.00 | 100 mm dia
63.00 | a) First Year | 1.00 | Set |  | 2300.00 | 2300.00 | 3348.00 | 3348.00 | 6000.00 | 6000.00 | 4200.00 | 4200.00 | 2300.00 | M/s CGPL ELECTROMECH PVT LTD
64.00 | b) Second Year | 1.00 | Set |  | 2400.00 | 2400.00 | 3682.80 | 3682.80 | 6000.00 | 6000.00 | 4500.00 | 4500.00 | 2400.00 | M/s CGPL ELECTROMECH PVT LTD
65.00 | 150 mm dia
66.00 | a) First Year | 1.00 | Set |  | 3800.00 | 3800.00 | 4650.00 | 4650.00 | 9085.00 | 9085.00 | 7500.00 | 7500.00 | 3800.00 | M/s CGPL ELECTROMECH PVT LTD
67.00 | b) Second Year | 1.00 | Set |  | 4000.00 | 4000.00 | 5115.00 | 5115.00 | 9085.00 | 9085.00 | 8000.00 | 8000.00 | 4000.00 | M/s CGPL ELECTROMECH PVT LTD
68.00 | 250 mm dia
69.00 | a) First Year | 1.00 | Set |  | 4200.00 | 4200.00 | 15618.00 | 15618.00 | 19090.00 | 19090.00 | 28500.00 | 28500.00 | 4200.00 | M/s CGPL ELECTROMECH PVT LTD
70.00 | b) Second Year | 1.00 | Set |  | 4500.00 | 4500.00 | 17180.00 | 17180.00 | 19090.00 | 19090.00 | 30000.00 | 30000.00 | 4500.00 | M/s CGPL ELECTROMECH PVT LTD
71.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required.
72.00 | 80 mm dia
73.00 | a) First Year | 1.00 | Set |  | 2500.00 | 2500.00 | 6944.00 | 6944.00 | 1900.00 | 1900.00 | 6500.00 | 6500.00 | 1900.00 | Blue Star Ltd
74.00 | b) Second Year | 1.00 | Set |  | 2600.00 | 2600.00 | 7638.40 | 7638.40 | 1900.00 | 1900.00 | 7000.00 | 7000.00 | 1900.00 | Blue Star Ltd
75.00 | 100 mm dia
76.00 | a) First Year | 1.00 | Set |  | 2800.00 | 2800.00 | 10360.00 | 10360.00 | 2530.00 | 2530.00 | 7500.00 | 7500.00 | 2530.00 | Blue Star Ltd
77.00 | b) Second Year | 1.00 | Set |  | 3000.00 | 3000.00 | 11396.00 | 11396.00 | 2530.00 | 2530.00 | 7800.00 | 7800.00 | 2530.00 | Blue Star Ltd
78.00 | 200 mm dia
79.00 | a) First Year | 1.00 | Set |  | 9500.00 | 9500.00 | 35979.00 | 35979.00 | 5120.00 | 5120.00 | 23000.00 | 23000.00 | 5120.00 | Blue Star Ltd
80.00 | b) Second Year | 1.00 | Set |  | 10500.00 | 10500.00 | 39576.00 | 39576.00 | 5120.00 | 5120.00 | 25000.00 | 25000.00 | 5120.00 | Blue Star Ltd
81.00 | 300 mm dia
82.00 | a) First Year | 1.00 | Set |  | 15500.00 | 15500.00 | 64889.00 | 64889.00 | 7600.00 | 7600.00 | 40000.00 | 40000.00 | 7600.00 | Blue Star Ltd
83.00 | b) Second Year | 1.00 | Set |  | 16500.00 | 16500.00 | 71377.90 | 71377.90 | 7600.00 | 7600.00 | 42000.00 | 42000.00 | 7600.00 | Blue Star Ltd
84.00 | Complete servicing and overhauling of all Cast Iron Gear Operating Gate valves of following sizes complete as required.
85.00 | 200 mm
86.00 | a) First Year | 1.00 | Set |  | 2500.00 | 2500.00 | 2100.00 | 2100.00 | 1610.00 | 1610.00 | 5000.00 | 5000.00 | 1610.00 | Blue Star Ltd
87.00 | b) Second Year | 1.00 | Set |  | 3000.00 | 3000.00 | 2205.00 | 2205.00 | 1610.00 | 1610.00 | 5000.00 | 5000.00 | 1610.00 | Blue Star Ltd
88.00 | Complete servicing and overhauling of all Cast Iron Gate valves of following sizes complete as required.
89.00 | 50 mm
90.00 | a) First Year | 1.00 | Job |  | 1500.00 | 1500.00 | 300.00 | 300.00 | 1035.00 | 1035.00 | 1500.00 | 1500.00 | 300.00 | Voltas Limited
91.00 | b) Second Year | 1.00 | Job |  | 1700.00 | 1700.00 | 315.00 | 315.00 | 1045.00 | 1045.00 | 1500.00 | 1500.00 | 315.00 | Voltas Limited
92.00 | 80 mm
93.00 | a) First Year | 1.00 | Job |  | 1600.00 | 1600.00 | 400.00 | 400.00 | 1610.00 | 1610.00 | 2000.00 | 2000.00 | 400.00 | Voltas Limited
94.00 | b) Second Year | 1.00 | Job |  | 1700.00 | 1700.00 | 420.00 | 420.00 | 1610.00 | 1610.00 | 2000.00 | 2000.00 | 420.00 | Voltas Limited
95.00 | 150 mm
96.00 | a) First Year | 1.00 | Job |  | 1800.00 | 1800.00 | 450.00 | 450.00 | 1610.00 | 1610.00 | 4000.00 | 4000.00 | 450.00 | Voltas Limited
97.00 | b) Second Year | 1.00 | Job |  | 2000.00 | 2000.00 | 472.50 | 472.50 | 1610.00 | 1610.00 | 4000.00 | 4000.00 | 472.50 | Voltas Limited
98.00 | 200 mm
99.00 | a) First Year | 1.00 | Job |  | 2000.00 | 2000.00 | 450.00 | 450.00 | 4025.00 | 4025.00 | 5000.00 | 5000.00 | 450.00 | Voltas Limited
100.00 | b) Second Year | 1.00 | Job |  | 2100.00 | 2100.00 | 472.50 | 472.50 | 4025.00 | 4025.00 | 5000.00 | 5000.00 | 472.50 | Voltas Limited
101.00 | 250 mm
102.00 | a) First Year | 1.00 | Job |  | 2200.00 | 2200.00 | 450.00 | 450.00 | 5520.00 | 5520.00 | 6000.00 | 6000.00 | 450.00 | Voltas Limited
103.00 | b) Second Year | 1.00 | Job |  | 2300.00 | 2300.00 | 472.50 | 472.50 | 5520.00 | 5520.00 | 6000.00 | 6000.00 | 472.50 | Voltas Limited
104.00 | Complete servicing and overhauling of all Cast Iron Non Return valves of following sizes including replacement of o-ring /gasket if damaged complete as required.
105.00 | 40 mm
106.00 | a) First Year | 10.00 | Job |  | 250.00 | 2500.00 | 300.00 | 3000.00 | 575.00 | 5750.00 | 2000.00 | 20000.00 | 2500.00 | M/s CGPL ELECTROMECH PVT LTD
107.00 | b) Second Year | 10.00 | Job |  | 300.00 | 3000.00 | 315.00 | 3150.00 | 575.00 | 5750.00 | 2200.00 | 22000.00 | 3000.00 | M/s CGPL ELECTROMECH PVT LTD
108.00 | 50 mm
109.00 | a) First Year | 10.00 | Job |  | 450.00 | 4500.00 | 300.00 | 3000.00 | 633.00 | 6330.00 | 2500.00 | 25000.00 | 3000.00 | Voltas Limited
110.00 | b) Second Year | 10.00 | Job |  | 500.00 | 5000.00 | 315.00 | 3150.00 | 633.00 | 6330.00 | 2600.00 | 26000.00 | 3150.00 | Voltas Limited
111.00 | 65 mm
112.00 | a) First Year | 10.00 | Job |  | 500.00 | 5000.00 | 300.00 | 3000.00 | 805.00 | 8050.00 | 2800.00 | 28000.00 | 3000.00 | Voltas Limited
113.00 | b) Second Year | 10.00 | Job |  | 550.00 | 5500.00 | 315.00 | 3150.00 | 805.00 | 8050.00 | 3000.00 | 30000.00 | 3150.00 | Voltas Limited
114.00 | 80 mm
115.00 | a) First Year | 1.00 | Job |  | 600.00 | 600.00 | 400.00 | 400.00 | 1610.00 | 1610.00 | 3200.00 | 3200.00 | 400.00 | Voltas Limited
116.00 | b) Second Year | 1.00 | Job |  | 650.00 | 650.00 | 420.00 | 420.00 | 1610.00 | 1610.00 | 3500.00 | 3500.00 | 420.00 | Voltas Limited
117.00 | 100 mm | 1.00 | Job |  | 750.00 | 750.00 | 400.00 | 400.00 | 1610.00 | 1610.00 | 4000.00 | 4000.00 | 400.00 | Voltas Limited
118.00 | 150 mm | 1.00 | Job |  | 850.00 | 850.00 | 450.00 | 450.00 | 1610.00 | 1610.00 | 4200.00 | 4200.00 | 450.00 | Voltas Limited
119.00 | 200 mm
120.00 | a) First Year | 4.00 | Job |  | 1000.00 | 4000.00 | 450.00 | 1800.00 | 1610.00 | 6440.00 | 6500.00 | 26000.00 | 1800.00 | Voltas Limited
121.00 | b) Second Year | 4.00 | Job |  | 1200.00 | 4800.00 | 472.50 | 1890.00 | 1610.00 | 6440.00 | 7000.00 | 28000.00 | 1890.00 | Voltas Limited
122.00 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required.
123.00 | Stainless Steel (Grade 304)
124.00 | a) First Year | 30.00 | Set |  | 2500.00 | 75000.00 | 4100.00 | 123000.00 | 748.00 | 22440.00 | 3500.00 | 105000.00 | 22440.00 | Blue Star Ltd
125.00 | b) Second Year | 30.00 | Set |  | 2700.00 | 81000.00 | 4305.00 | 129150.00 | 748.00 | 22440.00 | 4000.00 | 120000.00 | 22440.00 | Blue Star Ltd
126.00 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories.
127.00 | Pendent Sprinkler
128.00 | a) First Year | 25.00 | Nos. |  | 250.00 | 6250.00 | 360.00 | 9000.00 | 6040.00 | 151000.00 | 650.00 | 16250.00 | 6250.00 | M/s CGPL ELECTROMECH PVT LTD
129.00 | b) Second Year | 25.00 | Nos. |  | 300.00 | 7500.00 | 378.00 | 9450.00 | 6040.00 | 151000.00 | 750.00 | 18750.00 | 7500.00 | M/s CGPL ELECTROMECH PVT LTD
130.00 | Upright Sprinkler
131.00 | a) First Year | 25.00 | Nos. |  | 300.00 | 7500.00 | 1410.00 | 35250.00 | 345.00 | 8625.00 | 600.00 | 15000.00 | 7500.00 | M/s CGPL ELECTROMECH PVT LTD
132.00 | b) Second Year | 25.00 | Nos. |  | 350.00 | 8750.00 | 1480.50 | 37012.50 | 345.00 | 8625.00 | 700.00 | 17500.00 | 8625.00 | Blue Star Ltd
133.00 | Supplying & fixing 63 mm dia short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required.
134.00 | Stainless Steel (Grade 304)
135.00 | a) First Year | 50.00 | Nos. |  | 1400.00 | 70000.00 | 3350.00 | 167500.00 | 1495.00 | 74750.00 | 2000.00 | 100000.00 | 70000.00 | M/s CGPL ELECTROMECH PVT LTD
136.00 | b) Second Year | 50.00 | Nos. |  | 1500.00 | 75000.00 | 3517.50 | 175875.00 | 1495.00 | 74750.00 | 2100.00 | 105000.00 | 74750.00 | Blue Star Ltd
137.00 | Providing, installation, testing & commissioning of adjustable rosette plate for 15mm dia in white finish UL Listed or FM approved complete as required.
138.00 | a) First Year | 250.00 | Nos. |  | 45.00 | 11250.00 | 250.00 | 62500.00 | 120.00 | 30000.00 | 250.00 | 62500.00 | 11250.00 | M/s CGPL ELECTROMECH PVT LTD
139.00 | b) Second Year | 250.00 | Nos. |  | 55.00 | 13750.00 | 262.50 | 65625.00 | 120.00 | 30000.00 | 300.00 | 75000.00 | 13750.00 | M/s CGPL ELECTROMECH PVT LTD
140.00 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 20 mm nominal internal dia water hose rubber type. 20 mm nominal internal dia Stainless Steel globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop Stainless Steel valve & M.S. Pipe and socket.
141.00 | 30 m
142.00 | a) First Year | 2.00 | Set |  | 5500.00 | 11000.00 | 10000.00 | 20000.00 | 9775.00 | 19550.00 | 10500.00 | 21000.00 | 11000.00 | M/s CGPL ELECTROMECH PVT LTD
143.00 | b) Second Year | 2.00 | Set |  | 6000.00 | 12000.00 | 10500.00 | 21000.00 | 9775.00 | 19550.00 | 12000.00 | 24000.00 | 12000.00 | M/s CGPL ELECTROMECH PVT LTD
144.00 | Providing, installation, testing & commissioning of M.S. Fire Hose box mild steel double door 900mm x 600mm x 250mm made from 20 SWG MS sheet suitable to accomodate 2 nos. 63mm dia & 15 mtrs. long hose pipe with nozzle and has two doors with locking arrangement. | 10.00 | Nos. |  | 2500.00 | 25000.00 | 6000.00 | 60000.00 | 2300.00 | 23000.00 | 6500.00 | 65000.00 | 23000.00 | Blue Star Ltd
145.00 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
146.00 | 1500 mm
147.00 | a) First Year | 25.00 | Nos. |  | 650.00 | 16250.00 | 2800.00 | 70000.00 | 1472.00 | 36800.00 | 2250.00 | 56250.00 | 16250.00 | M/s CGPL ELECTROMECH PVT LTD
148.00 | b) Second Year | 25.00 | Nos. |  | 700.00 | 17500.00 | 2940.00 | 73500.00 | 1472.00 | 36800.00 | 2500.00 | 62500.00 | 17500.00 | M/s CGPL ELECTROMECH PVT LTD
149.00 | Supplying and fixing internal hydrant valve with instantaneous Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Stainless Steel cap and chain as required.
150.00 | Single headed Stainless steel
151.00 | a) First Year | 2.00 | Set |  | 3500.00 | 7000.00 | 7000.00 | 14000.00 | 8625.00 | 17250.00 | 6500.00 | 13000.00 | 7000.00 | M/s CGPL ELECTROMECH PVT LTD
152.00 | b) Second Year | 2.00 | Set |  | 4000.00 | 8000.00 | 7350.00 | 14700.00 | 8625.00 | 17250.00 | 7000.00 | 14000.00 | 8000.00 | M/s CGPL ELECTROMECH PVT LTD
153.00 | Double headed Stainless steel
154.00 | a) First Year | 2.00 | Set |  | 5000.00 | 10000.00 | 18626.00 | 37252.00 | 8625.00 | 17250.00 | 17500.00 | 35000.00 | 10000.00 | M/s CGPL ELECTROMECH PVT LTD
155.00 | b) Second Year | 2.00 | Set |  | 5200.00 | 10400.00 | 19557.30 | 39114.60 | 8625.00 | 17250.00 | 18000.00 | 36000.00 | 10400.00 | M/s CGPL ELECTROMECH PVT LTD
156.00 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Stainless Steel cap and chain as required.
157.00 | Single headed Stainless steel
158.00 | a) First Year | 2.00 | Set |  | 3800.00 | 7600.00 | 11900.00 | 23800.00 | 8050.00 | 16100.00 | 6500.00 | 13000.00 | 7600.00 | M/s CGPL ELECTROMECH PVT LTD
159.00 | b) Second Year | 2.00 | Set |  | 4500.00 | 9000.00 | 12495.00 | 24990.00 | 8050.00 | 16100.00 | 7000.00 | 14000.00 | 9000.00 | M/s CGPL ELECTROMECH PVT LTD
160.00 | Double headed Stainless steel
161.00 | a) First Year | 2.00 | Set |  | 5000.00 | 10000.00 | 31600.00 | 63200.00 | 9775.00 | 19550.00 | 17500.00 | 35000.00 | 10000.00 | M/s CGPL ELECTROMECH PVT LTD
162.00 | b) Second Year | 2.00 | Set |  | 5200.00 | 10400.00 | 33180.00 | 66360.00 | 9775.00 | 19550.00 | 18000.00 | 36000.00 | 10400.00 | M/s CGPL ELECTROMECH PVT LTD
163.00 | Supply and fixing of 63mm dia fire hydrant rubber type female coupling ring washer of 3mm thickness.
164.00 | a) First Year | 50.00 | Nos. |  | 350.00 | 17500.00 | 35.00 | 1750.00 | 518.00 | 25900.00 | 300.00 | 15000.00 | 1750.00 | Voltas Limited
165.00 | b) Second Year | 50.00 | Nos. |  | 350.00 | 17500.00 | 36.75 | 1837.50 | 518.00 | 25900.00 | 350.00 | 17500.00 | 1837.50 | Voltas Limited
166.00 | Supply and fixing of 63mm dia fire hydrant gasket rubber type of 3mm thickness.
167.00 | a) First Year | 50.00 | Nos. |  | 250.00 | 12500.00 | 10.00 | 500.00 | 518.00 | 25900.00 | 300.00 | 15000.00 | 500.00 | Voltas Limited
168.00 | b) Second Year | 50.00 | Nos. |  | 300.00 | 15000.00 | 10.50 | 525.00 | 518.00 | 25900.00 | 350.00 | 17500.00 | 525.00 | Voltas Limited
169.00 | Supply and fixing of PVC type for following type NRV gasket.
170.00 | 80 mm
171.00 | a) First Year | 4.00 | Nos. |  | 350.00 | 1400.00 | 200.00 | 800.00 | 690.00 | 2760.00 | 500.00 | 2000.00 | 800.00 | Voltas Limited
172.00 | b) Second Year | 4.00 | Nos. |  | 400.00 | 1600.00 | 210.00 | 840.00 | 690.00 | 2760.00 | 550.00 | 2200.00 | 840.00 | Voltas Limited
173.00 | 200 mm
174.00 | a) First Year | 8.00 | Nos. |  | 450.00 | 3600.00 | 300.00 | 2400.00 | 828.00 | 6624.00 | 1500.00 | 12000.00 | 2400.00 | Voltas Limited
175.00 | b) Second Year | 8.00 | Nos. |  | 450.00 | 3600.00 | 315.00 | 2520.00 | 828.00 | 6624.00 | 1800.00 | 14400.00 | 2520.00 | Voltas Limited
176.00 | Complete dewatering and cleaning of Fire Sprinkler / Borewell tank (having depth of 8 mtrs. approx.) through high pressure mechanized cleaning of water tank to get rid of calcination, algae, sludge, sediment and other contaminants by bleaching solution, sodium hypochlorite and other standard chemical treatment to arrest microbiological contaminants etc. as required and as per instruction of Engineer-in-Charge of following volumes (approx.) including providing relevant safety kit and breathing appratus (oxygen mask, cylinder etc.) to cleaning personnel:
177.00 | 2.73 lakh litres volume of water
178.00 | a) First Year | 2.00 | Job |  | 10500.00 | 21000.00 | 16000.00 | 32000.00 | 20700.00 | 41400.00 | 75000.00 | 150000.00 | 21000.00 | M/s CGPL ELECTROMECH PVT LTD
179.00 | b) Second Year | 2.00 | Job |  | 12500.00 | 25000.00 | 16800.00 | 33600.00 | 20700.00 | 41400.00 | 80000.00 | 160000.00 | 25000.00 | M/s CGPL ELECTROMECH PVT LTD
180.00 | 3.62 lakh litres volume of water
181.00 | a) First Year | 2.00 | Job |  | 15000.00 | 30000.00 | 19000.00 | 38000.00 | 20700.00 | 41400.00 | 100000.00 | 200000.00 | 30000.00 | M/s CGPL ELECTROMECH PVT LTD
182.00 | b) Second Year | 2.00 | Job |  | 17000.00 | 34000.00 | 19950.00 | 39900.00 | 20700.00 | 41400.00 | 125000.00 | 250000.00 | 34000.00 | M/s CGPL ELECTROMECH PVT LTD
183.00 | Blocking of inlet / outlet pipes of 200 / 250 mm dia in completely filled up water tanks having a depth of 8 mtrs. (approx) with the help of scuba divers for the purpose of replacement of gate valves and unblocking the pipes after replacement of gate valves complete etc. as required and as per instruction of Engineer-in-Charge. (Valve will be supplied by AAI) including providing relevant safety kit and breathing appratus (oxygen mask, cylinder etc.) to scuba divers. | 4.00 | Job |  | 1500.00 | 6000.00 | 8000.00 | 32000.00 | 34500.00 | 138000.00 | 35000.00 | 140000.00 | 6000.00 | M/s CGPL ELECTROMECH PVT LTD
184.00 | SH: IV Civil Works
185.00 | Excavation for foundation in soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 50.00 | Cum |  | 200.00 | 10000.00 | 500.00 | 25000.00 | 4025.00 | 201250.00 | 8500.00 | 425000.00 | 10000.00 | M/s CGPL ELECTROMECH PVT LTD
186.00 | Filling available excavated earth (excluding rock) in trenches, sides of foundations etc. in layers (not exceeding 20 cm in depth), consolidating each deposited layer by ramming and watering, lead up to 50 mtrs. | 50.00 | Cum |  | 110.00 | 5500.00 | 100.00 | 5000.00 | 4025.00 | 201250.00 | 5000.00 | 250000.00 | 5000.00 | Voltas Limited
187.00 | Demolishing cement concrete manually / by mechanical means including disposal of materials within 50 metres lead as per direction of Engineer-in-Charge. | 2.00 | Cum |  | 2000.00 | 4000.00 | 1500.00 | 3000.00 | 20700.00 | 41400.00 | 20000.00 | 40000.00 | 3000.00 | Voltas Limited
188.00 | Demolishing R.C.C. work manually / by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | 2.00 | Cum |  | 2500.00 | 5000.00 | 2000.00 | 4000.00 | 2300.00 | 4600.00 | 25000.00 | 50000.00 | 4000.00 | Voltas Limited
189.00 | Demolishing brick work manually/ by mechanical means in cement mortar including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. | 3.00 | Cum |  | 850.00 | 2550.00 | 900.00 | 2700.00 | 13800.00 | 41400.00 | 15000.00 | 45000.00 | 2550.00 | M/s CGPL ELECTROMECH PVT LTD
190.00 | Providing and laying in position cement concrete of 1:2:4 (1 Cement : 2 Coarse sand : 4 graded stone aggregate 20 mm nominal size) etc as required. | 2.00 | Cum |  | 5000.00 | 10000.00 | 7500.00 | 15000.00 | 25300.00 | 50600.00 | 9500.00 | 19000.00 | 10000.00 | M/s CGPL ELECTROMECH PVT LTD
191.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) etc as required. | 2.00 | Cum |  | 4500.00 | 9000.00 | 6500.00 | 13000.00 | 25300.00 | 50600.00 | 10000.00 | 20000.00 | 9000.00 | M/s CGPL ELECTROMECH PVT LTD
192.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 3.00 | Cum |  | 4500.00 | 13500.00 | 8400.00 | 25200.00 | 920.00 | 2760.00 | 12000.00 | 36000.00 | 2760.00 | Blue Star Ltd
193.00 | Providing 15 mm thick cement plaster with a floating coat of neat cement of mix 1:4 (1 cement : 4 fine sand) at all levels. | 50.00 | Sqmt. |  | 225.00 | 11250.00 | 300.00 | 15000.00 | 345.00 | 17250.00 | 15000.00 | 750000.00 | 11250.00 | M/s CGPL ELECTROMECH PVT LTD
194.00 | SH: V Miscellaneous works
195.00 | Supply of Sodium Hypochlorite (NaOCl 8% free chlorine) as required. | 15000.00 | Ltrs. |  | 17.00 | 255000.00 | 35.00 | 525000.00 | 34.00 | 510000.00 | 125.00 | 1875000.00 | 255000.00 | M/s CGPL ELECTROMECH PVT LTD
196.00 | Supply of 5 Ltrs. Jar TASKI R2 (Cleaning chemical agent) or approved equivalent. | 8.00 | Nos. |  | 1650.00 | 13200.00 | 1300.00 | 10400.00 | 1380.00 | 11040.00 | 1500.00 | 12000.00 | 10400.00 | Voltas Limited
197.00 | Supply of 5 Ltrs. Jar TASKI R3 (Cleaning chemical agent) or approved equivalent. | 12.00 | Nos. |  | 1400.00 | 16800.00 | 1740.00 | 20880.00 | 1380.00 | 16560.00 | 1800.00 | 21600.00 | 16560.00 | Blue Star Ltd
198.00 | Supply of 5 Ltrs. SUMA Inox D7.1 (Cleaning chemical agent) or approved equivalent. | 16.00 | Nos. |  | 2850.00 | 45600.00 | 2290.00 | 36640.00 | 1725.00 | 27600.00 | 2000.00 | 32000.00 | 27600.00 | Blue Star Ltd
199.00 | Supply, installation, testing & commissioning of 12V, 150 AH SMF / VRLA Battery along with terminal clamps as per AAI Approved make. | 6.00 | Nos. |  | 14500.00 | 87000.00 | 20000.00 | 120000.00 | 17250.00 | 103500.00 | 18000.00 | 108000.00 | 87000.00 | M/s CGPL ELECTROMECH PVT LTD
200.00 | Fabrication works in M.S. C channel / angle / flat / plates including cutting to required length, welding including sparay / manual painting the same with two coats of ISI marked synthetic enamel paint of approved colour over one coat of red oxide metal primer as per direction of Engineer-in-Charge. | 500.00 | Kg |  | 95.00 | 47500.00 | 180.00 | 90000.00 | 150.00 | 75000.00 | 95.00 | 47500.00 | 47500.00 | M/s CGPL ELECTROMECH PVT LTD, J.K.DEFENCE FIRE ENGG. SERVICES
201.00 | SH: VI Painting Works
202.00 | Cleaning the surface of chequered plates and painting with two coats of synthetic enamel black paint etc. of approved brand and manufacturer as required. | 100.00 | Sqmt. |  | 250.00 | 25000.00 | 50.00 | 5000.00 | 173.00 | 17300.00 | 150.00 | 15000.00 | 5000.00 | Voltas Limited
203.00 | Scrubbing, cleaning the existing surface of cubicle panels / MS pipes and spray painting the same with two coats of synthetic enamel paint of approved brand and manufacturer of required colour over one coat of red oxide metal primer etc. to give an even shade as required. | 400.00 | Sqmt. |  | 350.00 | 140000.00 | 75.00 | 30000.00 | 173.00 | 69200.00 | 200.00 | 80000.00 | 30000.00 | Voltas Limited
204.00 | Letter writings with synthetic enamel paint of approved brand and manufacturer on the M.S. sheet / S.S. sheet / Painted Wall in English language complete as required as per the instruction and to the satisfaction of the Engineer in Charge of the following sizes.
205.00 | 4 CM | 800.00 | Nos. |  | 45.00 | 36000.00 | 5.00 | 4000.00 | 46.00 | 36800.00 | 30.00 | 24000.00 | 4000.00 | Voltas Limited
206.00 | 10 CM | 400.00 | Nos. |  | 55.00 | 22000.00 | 6.00 | 2400.00 | 46.00 | 18400.00 | 50.00 | 20000.00 | 2400.00 | Voltas Limited
207.00 | 15 CM | 200.00 | Nos. |  | 60.00 | 12000.00 | 8.00 | 1600.00 | 46.00 | 9200.00 | 75.00 | 15000.00 | 1600.00 | Voltas Limited
| Total in Figures |  |  |  |  | 17650200.00 |  | 15800135.44 |  | 21635292.00 |  | 36981450.00
Lowest Amount Quoted BY: Voltas Limited(15800135.44)

## BOQ Summary
BOQ Summary Details Tender Title: Operation and Maintenance of Fire fighting system and misc works Tender ID: 2024_AAI_195599_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Voltas Limited | 15800135.44 | L1
| 2 | M/s CGPL ELECTROMECH PVT LTD | 17650200.00 | L2
| 3 | Blue Star Ltd | 21635292.00 | L3
| 4 | J.K.DEFENCE FIRE ENGG. SERVICES | 36981450.00 | L4