## BoQ1
Government eProcurement System Created By: Suman Biswas Created Date/Time: 07-Aug-2024 11:00 AM Tender Title: Fire suppression system for HT/LT panel at NITB VSI Airport, Port Blair Tender ID: 2024_AAI_195811_1
Tender Inviting Authority: The Assistant General Manager (Engg-Elect), AAI, VSI Airport, Port Blair.
Name of Work: Fire suppression system for HT/LT panel at NITB VSI Airport, Port Blair.
Tender ID: 2024_AAI_195811_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -705352 |  | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -705717 |  | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -706440 |  | SVS Buildwel Pvt Ltd (GSTN-07AALCS7473H1ZU) BID ID -706867 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -707266 |  | SUPREMEX EQUIPMENTS (GSTN-27AACFS4291B1ZD) BID ID -707309 |  | Surendra Infrastructure Pvt. Ltd. (GSTN-35AAJCS7963C1Z4) BID ID -708131 |  | FOAMTECH ANTIFIRE PRIVATE LIMITED(GSTN-NA)--707487
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 1 Kg Automatic Direct Low Pressure Fire Suppression Extinguisher and Valve. Applicable on class A, B, C and electrically started fires. Extinguishing Agent: 1 Kg Clean Agent FK-5-1-12 (UL Listed or FM approved) with zero Ozone Depletion Potential. Fire Suppression Extinguisher Can: EPA & SNAP/PESO approved can, stored Pressure Type, deep drawn and argon welded , MS sheet metal of thickness withstanding 100% hydraulic pressure tested to 35 bars, Operating pressure 15 bar. Can as per IS:15683. Cylinder Mounting Bracket. Valve : The valve DLP is nickel plated brass , equipped with a pressure gauge to monitor the system pressure , with a ball valve interfacing the tubing and the cylinder , working pressure 10-15 bar, tested upto 35 bars.Valve shall be CE certified | 20.00 | Set | 54848.00 | 22680.00 | 453600.00 | 28000.00 | 560000.00 | 27950.00 | 559000.00 | 22275.00 | 445500.00 | 33000.00 | 660000.00 | 28500.00 | 570000.00 | 40500.00 | 810000.00 | 17900.00 | 358000.00 | 358000.00 | FOAMTECH ANTIFIRE PRIVATE LIMITED
2.00 | SITC of 2 Kg Automatic Direct Low Pressure Fire Suppression Extinguisher and Valve. Applicable on class A, B, C and electrically started fires. Extinguishing Agent: 2 Kg Clean Agent FK-5-1-12 (UL Listed or FM approved) with zero Ozone Depletion Potential. Fire Suppression Extinguisher Can: EPA & SNAP/PESO approved can, stored Pressure Type, deep drawn and argon welded , MS sheet metal of thickness withstanding 100% hydraulic pressure tested to 35 bars, Operating pressure 15 bar. Can as per IS:15683. Cylinder Mounting Bracket. Valve : The valve DLP is nickel plated brass , equipped with a pressure gauge to monitor the system pressure , with a ball valve interfacing the tubing and the cylinder , working pressure 10-15 bar, tested upto 35 bars.Valve shall be CE certified | 13.00 | Set | 54848.00 | 25570.00 | 332410.00 | 38000.00 | 494000.00 | 33450.00 | 434850.00 | 24975.00 | 324675.00 | 35000.00 | 455000.00 | 31500.00 | 409500.00 | 44000.00 | 572000.00 | 19700.00 | 256100.00 | 256100.00 | FOAMTECH ANTIFIRE PRIVATE LIMITED
3.00 | SITC of 4 Kg Automatic Direct Low Pressure Fire Suppression Extinguisher and Valve. Applicable on class A, B, C and electrically started fires. Extinguishing Agent: 4 Kg Clean Agent FK-5-1-12 (UL Listed or FM approved) with zero Ozone Depletion Potential. Fire Suppression Extinguisher Can: EPA & SNAP/PESO approved can, stored Pressure Type, deep drawn and argon welded, MS sheet metal thickness thickness withstanding 100% hydraulic pressure tested to 35 bars, Operating pressure 15 bar. Can as per IS:15683. Cylinder Mounting Bracket. Valve : The valve DLP is nickel plated brass , equipped with a pressure gauge to monitor the system pressure , with a ball valve interfacing the tubing and the cylinder , working pressure 10-15 bar, tested upto 35 bars.Valve shall be CE certified | 4.00 | Set | 65538.77 | 27250.00 | 109000.00 | 48000.00 | 192000.00 | 44250.00 | 177000.00 | 30375.00 | 121500.00 | 40000.00 | 160000.00 | 35600.00 | 142400.00 | 52500.00 | 210000.00 | 22900.00 | 91600.00 | 91600.00 | FOAMTECH ANTIFIRE PRIVATE LIMITED
4.00 | SITC of Heat Sensing Tube for automatic fire detection and suppression system made by special modified Polyamide (PA) color Red RAL 300 , High grade HR quality, , UV Stabilized , inner diameter 4mm , outer diameter 6mm , melting point approx :- 220 degree Celsius when heating up with 10 K/minute, burst pressure 100 bar at 20oC . Temperature grade minus 40oC to + 80oC. Working Pressure 20 Bar at 20oC. Burst Temperature: When pressurized with dry Nitrogen at 15 bar pressure approx 100oC to 110oC, UL approved as per UL521 standard (or equivalent FM approved) for heat detectors for fire protective signaling systems.Loop Clamps shall be used to secure the sensor tube from the walls of the panel/mounting surface.Including pressurizing tube @ 15 Bars using Nitrogen pressurizing agent. Approved Makes: Vivina / Ases / shootfire(Vimal) /Lifeguard (UnitedFire)/ Ceasefire /kalpex(Kalpataru) /Foamtech/supremex /Ansul/LPG/Hygood/Firetrex(SVS)/ Honeywell | 1500.00 | Meter | 1440.92 | 990.00 | 1485000.00 | 800.00 | 1200000.00 | 1075.00 | 1612500.00 | 810.00 | 1215000.00 | 1500.00 | 2250000.00 | 650.00 | 975000.00 | 1199.00 | 1798500.00 | 424.00 | 636000.00 | 636000.00 | FOAMTECH ANTIFIRE PRIVATE LIMITED
5.00 | SITC of T connection , Brass , Nickel plated , for 4 x 6 mm Sensor Tube , quick and easy disassembly using special tool , working pressure 15 bars at 15 Deg temperature , temperature range -40 oC till +80oC, Elastomeric sealings , External diameter tube 6mm. Approved Makes: Vivina / Ases / shootfire(Vimal) /Lifeguard (UnitedFire)/ Ceasefire /kalpex(Kalpataru) /Foamtech/supremex /Ansul/LPG/Hygood/Firetrex(SVS)/ Honeywell | 90.00 | Job | 4500.00 | 1080.00 | 97200.00 | 400.00 | 36000.00 | 910.00 | 81900.00 | 1283.00 | 115470.00 | 2500.00 | 225000.00 | 800.00 | 72000.00 | 2899.00 | 260910.00 | 1079.00 | 97110.00 | 36000.00 | advent electric technologies pvt. ltd.
6.00 | SITC of End of Line Plug for Automatic fire detection and suppression tube used for fitting at the tube end to terminate the point. Fitting made by brass nickel plated material with elastomeric sealings, Temperature range TS -20oC till +60oC, Maximum working pressure 25 Bars , made as per PED pressure equipment directives. Approved Makes: Vivina / Ases / shootfire(Vimal) /Lifeguard (UnitedFire)/ Ceasefire /kalpex(Kalpataru) /Foamtech/supremex /Ansul/LPG/Hygood/Firetrex(SVS)/ Honeywell | 90.00 | Job | 1700.00 | 860.00 | 77400.00 | 200.00 | 18000.00 | 590.00 | 53100.00 | 743.00 | 66870.00 | 1000.00 | 90000.00 | 600.00 | 54000.00 | 2199.00 | 197910.00 | 399.00 | 35910.00 | 18000.00 | advent electric technologies pvt. ltd.
7.00 | SITC of End of Line adaptor with pressure gauge for Automatic fire suppression tube used for fitting at the end of the tube for pressurizing and re pressurizing the tube includes check valve, Pressure gauge and fitting to connect to sensor tubing. Tube connection 6mm, length 2.77"/71mm, gauge scale; 0-20 bar. Fitting made by brass (plated / unplated) , Stainless Steel , elastomeric sealings , copper Nickel plated , Temperature range TS -20oC till +60oC, Maximum working pressure 25 Bars , made as per PED pressure equipment directives. Approved Makes: Vivina / Ases / shootfire(Vimal) /Lifeguard (UnitedFire)/ Ceasefire /kalpex(Kalpataru) /Foamtech/supremex /Ansul/LPG/Hygood/Firetrex(SVS)/ Honeywell | 37.00 | Job | 7500.00 | 3680.00 | 136160.00 | 1200.00 | 44400.00 | 1750.00 | 64750.00 | 1688.00 | 62456.00 | 4500.00 | 166500.00 | 1500.00 | 55500.00 | 4799.00 | 177563.00 | 1099.00 | 40663.00 | 40663.00 | FOAMTECH ANTIFIRE PRIVATE LIMITED
8.00 | SITC of pressure switch to monitor pressure drop in the tube , switch point 5 Bars, switch type SPST, Normally Open/closed , Electric Rating 120/ 240 VAC-375 VA, 24 VAC - 125 VA , Open 160 psi y-7 , Close 185 psi y-5 , Pressure switch + adaptor /5 bar/ M10x1.It should be CE certified Filling Adapter to pressurize the Heat Detection Tube with quick coupling connector and threaded end-of-line connection | 37.00 | Job | 4000.83 | 9200.00 | 340400.00 | 800.00 | 29600.00 | 5100.00 | 188700.00 | 3321.00 | 122877.00 | 10000.00 | 370000.00 | 6298.00 | 233026.00 | 6599.00 | 244163.00 | 2249.00 | 83213.00 | 29600.00 | advent electric technologies pvt. ltd.
9.00 | SITC of Master control unit for the operation of above items Upon receiving notifications from the system pressure switch due to activation, the MCU shall provide outputs for activation of sounders or to third party devices which may be used for Notification. Outputs: Low pressure (Fault), System activation (Fire) Input: Pressure Switch Notification: 12V output for Sounder Main Power: 230V AC With Battery Backup & Sounder Interface system with main control fire alarm system(Inclusive of Wiring) The system should have means to switch off the exhaust fans if installed in the panel at the time of system activation Including control/power cabling with 1.5sqmm Cu cable with cable clamps/ties backed by 6A MCB Approved Makes: Siemens / Eaton / Hochiki / Bosch / Apollo / Ravel /Autronica(UTC)/ Edwards(UTC)/ Honeywell/Kidde (UTC)/ GST (UTC)/ System Sensor/ Morley IAS/ Group4/ Mather & Platt/ Minimax | 37.00 | Nos. | 20000.00 | 20000.00 | 740000.00 | 3200.00 | 118400.00 | 12250.00 | 453250.00 | 16875.00 | 624375.00 | 12000.00 | 444000.00 | 7800.00 | 288600.00 | 22900.00 | 847300.00 | 7400.00 | 273800.00 | 118400.00 | advent electric technologies pvt. ltd.
| Total in Figures |  |  |  |  | 3771170.00 |  | 2692400.00 |  | 3625050.00 |  | 3098723.00 |  | 4820500.00 |  | 2800026.00 |  | 5118346.00 |  | 1872396.00
Lowest Amount Quoted BY: FOAMTECH ANTIFIRE PRIVATE LIMITED(1872396.00)

## BOQ Summary
BOQ Summary Details Tender Title: Fire suppression system for HT/LT panel at NITB VSI Airport, Port Blair Tender ID: 2024_AAI_195811_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | FOAMTECH ANTIFIRE PRIVATE LIMITED | 1872396.00 | L1
| 2 | advent electric technologies pvt. ltd. | 2692400.00 | L2
| 3 | SUPREMEX EQUIPMENTS | 2800026.00 | L3
| 4 | SVS Buildwel Pvt Ltd | 3098723.00 | L4
| 5 | Nexus Fire And Security Systems | 3625050.00 | L5
| 6 | PYROGUARD ENGINEERS PRIVATE LIMITED | 3771170.00 | L6
| 7 | CENTRE TAP ENGINEERING | 4820500.00 | L7
| 8 | Surendra Infrastructure Pvt. Ltd. | 5118346.00 | L8